## Frontsheet
Janssen Biologics BV Leiden
BMS Building QC Kappa - Instrument List
Document Number: J270-06-DVL-001
Version 2.1
BMS Panel : J270-06-1PNL-001
PLC: J270-06-3PLC-001, J270-06-3PLC-002

## Floormanager
IO CPNX/JACE
Version | Nr | Outstation | Device Tag | Point Descriptor | PID Nr | IO Type | Description | Power | Signal Type | Converter | Splitter | Range (Low) | Range (High) | Unit | Accuracy | Mfgr | Model | Cal Cert Req | Tech Datasheet Nr | Signal Type (CPNX/JACE) | Range (Low) (CPNX/JACE) | Range (High) (CPNX/JACE) | Unit (CPNX/JACE) | Remark (CPNX/JACE) | EBI Point Descriptor | EBI Tag | JACE Tag | Remarks | Room Number | JACE | RS485 COM | Module No | Channel No
1.0 | 1 | J270-06-1PNL-001 | J270-06-2XA-001 | J270-06-2XA-001 - J270-06-1PNL-001 - 230VAC Thermal Fault Signal | - | DI | Electrical Panel - 230VAC Thermal Fault | - | PVC | - | - | ALARM | NORMAL | - | - | Schneider Electric | iC60N | - | N/A | PVC | NORMAL | ALARM | - | INVERTED | J270-06-2XA-001 - J270-06-1PNL-001 - 230VAC Thermal Fault Signal | J270-06-2XA-001_230VACThemFlt | J270-06-2XA-001_230VACThemFlt | - |  | 1 | 1 | 1 | 1
1.0 | 2 | J270-06-1PNL-001 | J270-06-2XA-002 | J270-06-2XA-002 - J270-06-1PNL-001 - 24VDC Thermal Fault Signal | - | DI | Electrical Panel - 24VDC Thermal Fault | - | PVC | - | - | ALARM | NORMAL | - | - | Schneider Electric | iC60N | - | N/A | PVC | NORMAL | ALARM | - | INVERTED | J270-06-2XA-002 - J270-06-1PNL-001 - 24VDC Thermal Fault Signal | J270-06-2XA-002_24VDCThemFlt | J270-06-2XA-002_24VDCThemFlt | - |  | 1 | 1 | 1 | 2
1.0 | 3 | J270-06-1PNL-001 | J270-06-2XA-004 | J270-06-2XA-004 - J270-06-1PNL-001 - Surge Voltage Arrester Signal | - | DI | Electrical Panel - Surge Voltage Arrester | - | PVC | - | - | FAULT | NORMAL | - | - | Phoenix Contact | VAL-CP-MCB-1S-350/40/FM | - | N/A | PVC | NORMAL | FAULT | - | INVERTED | J270-06-2XA-004 - J270-06-1PNL-001 - Surge Voltage Arrester Signal | J270-06-2XA-004_SurgeVoltArr | J270-06-2XA-004_SurgeVoltArr | - |  | 1 | 1 | 1 | 3
1.0 | 4 | J270-06-1PNL-001 | J270-06-2XA-005 | J270-06-2XA-005 - J270-06-1PNL-001 - Common Fire Alarm | - | DI | Electrical Panel - Common Fire Alarm from Fire Panel | - | PVC | - | - | ALARM | NORMAL | - | - | - | - | - | N/A | PVC | NORMAL | ALARM | - | INVERTED | J270-06-2XA-005 - J270-06-1PNL-001 - Common Fire Alarm | J270-06-2XA-005_ExtFireCom | J270-06-2XA-005_ExtFireCom | - |  | 1 | 1 | 1 | 4
2.1 | 5 | J270-06-1PNL-001 | J460-01-2TT-612 | J460-01-2TT-612 - Chilled Water - Supply Temperature | J460-01-11-06-001 | AI | Rotronic TF532 Temperature sensor, 4-20mA, -40°C/60°C + 111103 + 102122 | 24VDC | 4-20mA | 500Ω | - | -40 | 60 | °C | 0.2K @ 23°C ±5°C | Rotronic | TF532-WT1XX1XX | NO | HM_Rotronic_TF5 | 2-10V | -40 | 60 | °C |  | J460-01-2TT-612 - Chilled Water - Supply Temperature | J460-01-2TT-612_ChlWtrSupTemp | J460-01-2TT-612_ChlWtrSupTemp |  |  | 1 | 1 | 4 | 1
2.1 | 6 | J270-06-1PNL-001 | J460-01-2TT-613 | J460-01-2TT-613 - Chilled Water - Return Temperature | J460-01-11-06-001 | AI | Rotronic TF532 Temperature sensor, 4-20mA, -40°C/60°C + 111103 + 102122 | 24VDC | 4-20mA | 500Ω | - | -40 | 60 | °C | 0.2K @ 23°C ±5°C | Rotronic | TF532-WT1XX1XX | NO | HM_Rotronic_TF5 | 2-10V | -40 | 60 | °C |  | J460-01-2TT-613 - Chilled Water - Return Temperature | J460-01-2TT-613_ChlWtrRetTemp | J460-01-2TT-613_ChlWtrRetTemp |  |  | 1 | 1 | 4 | 2
1.0 | 7 | J270-06-1PNL-001 | J460-01-2FCV-643 | J460-01-2FCV-643 - Chilled Water Valve - Controller | J460-01-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | -
2.1 | 8 | J270-06-1PNL-001 | J460-01-1PMP-601 | J460-01-1PMP-601 - Chilled water Circulation pump - Controller | J460-01-11-06-001 | BACNET | Grundfos Magna 3 32-100 F; CIM\CIU 300 BACnet MSTP | - | - | - | - | - | - | - | - | Grundfos | Magna 3 40-120 F | NO | TF-W-007 | - | - | - | - | See Profile PMP | - | - | -
2 | 9 | J270-06-1PNL-001 | J460-01-1PMP-601 | J460-01-2XA-601 - Chilled water Circulation pump J460-01-1PMP-601 - Alarm | J460-01-11-06-001 | DI | Grundfos Magna 3 40-120 F | PVC | PVC | - | - | ALARM | NORMAL | - | - | Grundfos | Magna 3 40-120 F | NO | TF-W-007 | PVC | NORMAL | ALARM | - | INVERTED | J460-01-2XA-601 - Chilled water Circulation pump J460-01-1PMP-601 - Alarm | R460-01-2XA-601_ChlWtrCirPmpAlm | R460-01-2XA-601_ChlWtrCirPmpAlm |  |  | 1 | 1 | 1 | 6
1.0 | 10 | J270-06-1PNL-001 | J460-01-1PMP-601 | J460-01-2SS-601 - Chilled water Circulation pump J460-01-1PMP-601 - Status | J460-01-11-06-001 | DI | Grundfos Magna 3 40-120 F | PVC | PVC | - | - | STOP | RUN | - | - | Grundfos | Magna 3 40-120 F | NO | TF-W-007 | PVC | STOP | RUN | - | - | J460-01-2SS-601 - Chilled water Circulation pump J460-01-1PMP-601 - Status | J460-01-2SS-601_ChlWtrCirPmpSts | J460-01-2SS-601_ChlWtrCirPmpSts |  |  | 1 | 1 | 1 | 7
1.0 | 11 | J270-06-1PNL-001 | J460-01-1PMP-601 | J460-01-2SC-601 - Chilled water Circulation pump J460-01-1PMP-601 - Control Signal | J460-01-11-06-001 | AO | Grundfos Magna 3 40-120 F | - | 0-10V | - | - | 0 | 100 | % | - | Grundfos | Magna 3 40-120 F | NO | TF-W-007 | 0-10V | 0 | 100% | - | - | J460-01-2SC-601 - Chilled water Circulation pump J460-01-1PMP-601 - Control Signal | J460-01-2SC-601_ChlWtrCirPmpCntr | J460-01-2SC-601_ChlWtrCirPmpCntr |  |  | 1 | 1 | 9 | 1
1.0 | 12 | J270-06-1PNL-001 | J460-01-1PMP-601 | J460-01-2XS-601 - Chilled water Circulation pump J460-01-1PMP-601 - Enable | J460-01-11-06-001 | DO | Grundfos Magna 3 40-120 F | PVC | PVC | - | - | DISABLE | ENABLE | - | - | Grundfos | Magna 3 40-120 F | NO | TF-W-007 | PVC | DISABLE | ENABLE | - | - | J460-01-2XS-601 - Chilled water Circulation pump J460-01-1PMP-601 - Enable | J460-01-2XS-601_ChlWtrCirPmpEna | J460-01-2XS-601_ChlWtrCirPmpEna |  |  | 1 | 1 | 10 | 2
1.0 | 13 | J270-06-1PNL-001 | J460-01-1PMP-601 | J460-01-2HSI-601 - Chilled water Circulation pump J460-01-1PMP-601 - Maintanance Switch | J460-01-11-06-001 | DI | KRAUS&NAIMER KG10 T203/D-Axxx | PVC | PVC | - | - | OFF | ON | - | - | KRAUS&NAIMER | KG10 T203/D-Axxx | NO |  | PVC | OFF | ON | - | - | J460-01-2HSI-601 - Chilled water Circulation pump J460-01-1PMP-601 - Maintanance Switch | J460-01-2HSI-601_ChlWtrCirPmpMS | J460-01-2HSI-601_ChlWtrCirPmpMS |  |  | 1 | 1 | 1 | 8
1.0 | 14 | J270-06-1PNL-001 | J460-01-2FT-601 | J460-01-2FT-601 - Chilled Water - Energy Meter | J460-01-11-06-001 | BACNET | Kamstrup Multical 403 - 10 (0.6 to 10m³/h) | 24VDC | - | - | - | - | - | - | - | Kamstrup | Multical 403 - 10 | NO | TF-W-013 | - | - | - | - | See Profile 403 | - | - | -
1.0 | 15 | J270-06-1PNL-001 | J460-01-2FT-602 | J460-01-2FT-602 - Hot Water - Energy Meter | J460-01-11-06-001 | BACNET | Kamstrup Multical 403 - 15 (0.6 to 15m³/h) | 24VDC | - | - | - | - | - | - | - | Kamstrup | Multical 403 - 15 | NO | TF-W-013 | - | - | - | - | See Profile 403 | - | - | -
1.0 | 16 | J270-06-1PNL-001 | J460-01-2FT-604 | J460-01-2FT-604 - 61LBK3 - Return Air Flow | J460-01-11-06-001 | AI | CMR232, P-Sensor, LCD, 24VDC, 50Pa, Modbus | 24VDC | 4-20mA | 500Ω | - | 0 | 6507 | m³/h | ±0.25% of Full Scale | CMR Controls | 232A000P0050M12 | NO | HM_CMR_232 | 2-10V | 0 | 6507 | m³/h |  | J460-01-2FT-604 - 61LBK3 - Return Air Flow | J460-01-2FT-604_RetAirFlow | J460-01-2FT-604_RetAirFlow |  |  | 1 | 1 | 4 | 3
1.0 | 17 | J270-06-1PNL-001 | J460-01-2TT-616 | J460-01-2TT-616 - 61LBK3 - Return Air Temperature | J460-01-11-06-001 | AI | Rotronic HF432 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C | 24VDC | 4-20mA | 500Ω | - | 0 | 50 | °C | ±0.2°C @ 23°C | Rotronic | HF432-DB1XX1XX | NO | HM_Rotronic_HF4 | 2-10V | 0 | 50 | °C |  | J460-01-2TT-616 - 61LBK3 - Return Air Temperature | J460-01-2TT-616_RetAirTemp | J460-01-2TT-616_RetAirTemp |  |  | 1 | 1 | 4 | 4
1.0 | 18 | J270-06-1PNL-001 | J460-01-2FT-603 | J460-01-2FT-603 - 61LBK3 - Supply Air Flow | J460-01-11-06-001 | AI | CMR232, P-Sensor, LCD, 24VDC, 25Pa, Modbus | 24VDC | 4-20mA | 500Ω | - | 0 | 5258 | m³/h | ±0.25% of Full Scale | CMR Controls | 232A000P0025M12 | NO | HM_CMR_232 | 2-10V | 0 | 5258 | m³/h |  | J460-01-2FT-603 - 61LBK3 - Supply Air Flow | J460-01-2FT-603_SupAirFlow | J460-01-2FT-603_SupAirFlow |  |  | 1 | 1 | 4 | 5
1.0 | 19 | J270-06-1PNL-001 | J460-01-2TT-614 | J460-01-2TT-614 - 61LBK3 - Supply Air Temperature | J460-01-11-06-001 | AI | Rotronic HF532 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C + HC2A-S | 24VDC | 4-20mA | 500Ω | - | 0 | 50 | °C | ±0.1°C @ 23°C | Rotronic | HF532-DB1XX1XX | NO | HM_Rotronic_HF5 | 2-10V | 0 | 50 | °C |  | J460-01-2TT-614 - 61LBK3 - Supply Air Temperature | J460-01-2TT-614_SupAirTemp | J460-01-2TT-614_SupAirTemp |  |  | 1 | 1 | 4 | 6
1.0 | 20 | J270-06-1PNL-001 | J460-01-2MT-614 | J460-01-2MT-614 - 61LBK3 - Supply Air Humidity | J460-01-11-06-001 | AI | Rotronic HF532 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C + HC2A-S | 24VDC | 4-20mA | 500Ω | - | 0 | 100 | % | ±0.8%RH @ 23°C | Rotronic | HF532-DB1XX1XX | NO | HM_Rotronic_HF5 | 2-10V | 0 | 100 | % |  | J460-01-2MT-614 - 61LBK3 - Supply Air Humidity | J460-01-2MT-614_SupAirHum | J460-01-2MT-614_SupAirHum |  |  | 1 | 1 | 4 | 7
2.1 | 21 | J270-06-1PNL-001 | J100-06-2TT-001 | J100-06-2TT-001 - Potable Water - Temperature | J100-06-11-01 | AI | Rotronic TF532 Temperature sensor, 4-20mA, 0°C/50°C + 111103 + 102122 | 24VDC | 4-20mA | 500Ω | - | 0 | 50 | °C | 0.2K @ 23°C ±5°C | Rotronic | TF532-WT1XX1XX | NO | HM_Rotronic_TF5 | 2-10V | 0 | 50 | °C |  | J100-06-2TT-001 - Potable Water - Temperature | J100-06-2TT-001_PotWtrSupTemp | J100-06-2TT-001_PotWtrSupTemp |  |  | 1 | 1 | 4 | 8
1.0 | 22 | J270-06-1PNL-001 | J100-06-2FT-001 | J100-06-2FT-001 - Potable Water - Flow | J100-06-11-01 | M-BUS | Itron M-Bus Cyble V2.0 | 24VDC | M-Bus | PW03 | - | - | - | - | - | Itron | Cyble M-Bus V2.0 | NO |  | RS-232 | - | - | - |  | - | - | -
2.1 | 23 | J270-06-1PNL-001 | J100-06-2TT-002 | J100-06-2TT-002 - Potable Hot Water - Inlet Temperature Heater | J100-06-11-01 | AI | Rotronic TF532 Temperature sensor, 4-20mA, 0°C/100°C + 111103 + 102122 | 24VDC | 4-20mA | 500Ω | - | 0 | 100 | °C | 0.2K @ 23°C ±5°C | Rotronic | TF532-WT1XX1XX | NO | HM_Rotronic_TF5 | 2-10V | 0 | 100 | °C |  | J100-06-2TT-002 - Potable Hot Water - Inlet Temperature Heater | J100-06-2TT-002_HotWtrInlTmp | J100-06-2TT-002_HotWtrInlTmp |  |  | 1 | 1 | 5 | 1
2 | 24 | J270-06-1PNL-001 | J100-06-2XCV-001 | J100-06-2XCV-001 - Legionella Dump Valve | J100-06-11-01 | DO | Belimo, R240PW-R, NR24A, 24VDC | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Belimo | NR24A | NO |  | 24VDC | CLOSE | OPEN | - |  | J100-06-2XCV-001 - Legionella Dump Valve | J100-06-2TCT-001_LegDmpVlv | J100-06-2TCT-001_LegDmpVlv |  |  | 1 | 1 | 10 | 3
2.1 | 25 | J270-06-1PNL-001 | J130-06-2TT-001 | J130-06-2TT-001 - Non Potable Water - Temperature | J130-06-11-01 | AI | Rotronic TF532 Temperature sensor, 4-20mA, 0°C/50°C + 111103 + 102122 | 24VDC | 4-20mA | 500Ω | - | 0 | 50 | °C | 0.2K @ 23°C ±5°C | Rotronic | TF532-WT1XX1XX | NO | HM_Rotronic_TF5 | 2-10V | 0 | 50 | °C |  | J130-06-2TT-001 - Non Potable Water - Temperature | J130-06-2TT-001_NPotWtrSupTemp | J130-06-2TT-001_NPotWtrSupTemp |  |  | 1 | 1 | 5 | 2
2.1 | 26 | J270-06-1PNL-001 | J130-06-2PT-001 | J130-06-2PT-001 - Non Potable Water - Pressure | J130-06-11-01 | AI | SHD-I 6, 0-6Bar, 4-20mA, 24VDC | 24VDC | 4-20mA | 500Ω | - | 0 | 6 | Bar | ±0.3% | S+S Regeltechnik | SHD-I 6 | NO | HM_Vedotec_SHD | 2-10V | 0 | 6 | Bar |  | J130-06-2PT-001 - Non Potable Water - Pressure | J130-06-2PT-001_NPotWtrSupPress | J130-06-2PT-001_NPotWtrSupPress |  |  | 1 | 1 | 5 | 3
1.0 | 27 | J270-06-1PNL-001 | J130-06-2FT-001 | J130-06-2FT-001 - Non Potable Water - Flow | J130-06-11-01 | M-BUS | Itron M-Bus Cyble V2.0 | 24VDC | M-Bus | PW03 | - | - | - | - | - | Itron | Cyble M-Bus V2.0 | NO |  | RS-232 | - | - | - |  | - | - | -
2.1 | 28 | J270-06-1PNL-001 | J305-06-2FT-001 | J305-06-2FT-001 - Compressed Air - Flow Meter | J305-06-11-01 | MODBUS-IP | Rotarex EL-FLOW, F-111AC, Modbus-TCP, 4-20mA, 24VDC | 24VDC | - | - | - | 4 | 750 | Ln/min | ±0,5% Rd plus ±0,1%FS; | Bronkhorst | F-113AC | NO | TF-W-201
1.0 | 29 | J270-06-1PNL-001 | J305-06-2PT-001 | J305-06-2PT-001 - Compressed Air - Pressure | J305-06-11-01 | AI | Wika MG-1, 24VDC, 0-16Bar, 4-20mA | 24VDC | 4-20mA | 500Ω | - | 0 | 16 | Bar | ≤2% of Span | Wika | MG-1-6-BG416-HAZ2E-AA-M4Z-AA-ZZ | NO | TF-W-206 | 2-10V | 0 | 16 | Bar |  | J305-06-2PT-001 - Compressed Air - Pressure | J305-06-2PT-001_CompAirPress | J305-06-2PT-001_CompAirPress |  |  | 1 | 1 | 5 | 4
1.0 | 30 | J270-06-1PNL-001 | J305-06-2MT-001 | J305-06-2MT-001 - Compressed Air - Dewpoint | J305-06-11-01 | AI | FA515 HTR, 24VDC, 4-20mA, 2 Wire | 24VDC | 4-20mA | 500Ω | - | -20 | 50 | °C | ±1°C@50..-20°C,±2°C@-20..-50°C,±3°C@-50..-80°C | CS Instruments | FA515 | NO | TF-W-204 | 2-10V | -20 | 50 | °C |  | J305-06-2MT-001 - Compressed Air - Dewpoint | J305-06-2MT-001_CompAirDP | J305-06-2MT-001_CompAirDP |  |  | 1 | 1 | 5 | 5
2.1 | 31 | J270-06-1PNL-001 | J320-06-2FT-001 | J320-06-2FT-001 - Carbon Dioxide Gas - Flow Meter | J320-06-11-01 | MODBUS-IP | Rotarex EL-FLOW, F-111AC, Modbus-TCP, 4-20mA, 24VDC | 24VDC | - | - | - | 3 | 390 | Ln/min | ±0,5% Rd plus ±0,1%FS; | Bronkhorst | F-113AC | NO | TF-W-201
1.0 | 32 | J270-06-1PNL-001 | J320-06-2PT-001 | J320-06-2PT-001 - Carbon Dioxide Gas - Pressure | J320-06-11-01 | AI | Wika MG-1, 24VDC, 0-16Bar, 4-20mA | 24VDC | 4-20mA | 500Ω | - | 0 | 16 | Bar | ≤2% of Span | Wika | MG-1-6-BG416-HAZ2E-AA-M4Z-AA-ZZ | NO | TF-W-206 | 2-10V | 0 | 16 | Bar |  | J320-06-2PT-001 - Carbon Dioxide Gas - Pressure | J320-06-2PT-001_CO2Press | J320-06-2PT-001_CO2Press |  |  | 1 | 1 | 5 | 6
2.1 | 33 | J270-06-1PNL-001 | J330-06-2FT-001 | J330-06-2FT-001 - Nitrogen Gas - Flow Meter | J330-06-11-01 | MODBUS-IP | Rotarex EL-FLOW, F-111AC, Modbus-TCP, 4-20mA, 24VDC | 24VDC | - | - | - | 0.6 | 100 | Ln/min | ±0,5% Rd plus ±0,1%FS; | Bronkhorst | F-111AC | NO | TF-W-201
1.0 | 34 | J270-06-1PNL-001 | J330-06-2PT-001 | J330-06-2PT-001 - Nitrogen Gas - Pressure | J330-06-11-01 | AI | Wika MG-1, 24VDC, 0-16Bar, 4-20mA | 24VDC | 4-20mA | 500Ω | - | 0 | 16 | Bar | ≤2% of Span | Wika | MG-1-6-BG416-HAZ2E-AA-M4Z-AA-ZZ | NO | TF-W-206 | 2-10V | 0 | 16 | Bar |  | J330-06-2PT-001 - Nitrogen Gas - Pressure | J330-06-2PT-001_NitroPress | J330-06-2PT-001_NitroPress |  |  | 1 | 1 | 5 | 7
1.0 | 35 | J270-06-1PNL-001 | J229-06-1QIT-001 | J229-06-1QIT-001 - SVK-6H - Energy Meter | J229-06-29-01 | MODBUS-IP | Shnieder Electric PM8240
1.0 | 36 | J270-06-1PNL-001 | J229-06-1QIT-002 | J229-06-1QIT-002 - VK-6H-1 - Energy Meter | J229-06-29-02 | MODBUS-IP | Shnieder Electric PM8240
1.0 | 37 | J270-06-1PNL-001 | J229-06-1QIT-003 | J229-06-1QIT-003 - VK-6H-2 - Energy Meter | J229-06-29-03 | MODBUS-IP | Shnieder Electric PM8240
1.0 | 38 | J270-06-1PNL-001 | J229-06-1QIT-004 | J229-06-1QIT-004 - VK-6H-3 - Energy Meter | J229-06-29-04 | MODBUS-IP | Shnieder Electric PM8240
1.0 | 39 | J270-06-1PNL-001 | J229-06-1QIT-005 | J229-06-1QIT-005 - VK-6H-4 - Energy Meter | J229-06-29-05 | MODBUS-IP | Shnieder Electric PM8240
1.0 | 40 | J270-06-1PNL-001 | J232-06-1UPS-001 | J232-06-1UPS-001 - Parameters UPS MDF room 6th floor | J232-06-11-01 | MODBUS-IP | Parameters UPS MDF room 6th floor
1.0 | 41 | J270-06-1PNL-001 | J229-06-2XA-101 | J229-06-2XA-101 - SVK-6H - Circuit Breaker Tripped | J229-06-29-01 | DI | J229-06-2XA-101 - SVK-6H - Circuit Breaker Tripped | - | PVC | - | - | ALARM | NORMAL | - | - | - | - | - | - | PVC | NORMAL | ALARM | - | INVERTED | J229-06-2XA-101 - SVK-6H - Circuit Breaker Tripped | J229-06-2XA-101_CirBrkTrip | J229-06-2XA-101_CirBrkTrip |  |  | 1 | 1 | 1 | 9
1.0 | 42 | J270-06-1PNL-001 | J229-06-2XA-102 | J229-06-2XA-102 - SVK-6H - Voltage Surge Arrestor | J229-06-29-01 | DI | J229-06-2XA-102 - SVK-6H - Voltage Surge Arrestor | - | PVC | - | - | FAULT | NORMAL | - | - | - | - | - | - | PVC | NORMAL | FAULT | - | INVERTED | J229-06-2XA-102 - SVK-6H - Voltage Surge Arrestor | J229-06-2XA-102_SurgeVoltArr | J229-06-2XA-102_SurgeVoltArr |  |  | 1 | 1 | 1 | 10
1.0 | 43 | J270-06-1PNL-001 | J229-06-2XA-103 | J229-06-2XA-103 - VK-6H-1 - Circuit Breaker Tripped | J229-06-29-02 | DI | J229-06-2XA-103 - VK-6H-1 - Circuit Breaker Tripped | - | PVC | - | - | ALARM | NORMAL | - | - | - | - | - | - | PVC | NORMAL | ALARM | - | INVERTED | J229-06-2XA-103 - VK-6H-1 - Circuit Breaker Tripped | J229-06-2XA-103_CirBrkTrip | J229-06-2XA-103_CirBrkTrip |  |  | 1 | 1 | 1 | 11
1.0 | 44 | J270-06-1PNL-001 | J229-06-2XA-104 | J229-06-2XA-104 - VK-6H-1 - Voltage Surge Arrestor | J229-06-29-02 | DI | J229-06-2XA-104 - VK-6H-1 - Voltage Surge Arrestor | - | PVC | - | - | FAULT | NORMAL | - | - | - | - | - | - | PVC | NORMAL | FAULT | - | INVERTED | J229-06-2XA-104 - VK-6H-1 - Voltage Surge Arrestor | J229-06-2XA-104_SurgeVoltArr | J229-06-2XA-104_SurgeVoltArr |  |  | 1 | 1 | 1 | 12
1.0 | 45 | J270-06-1PNL-001 | J229-06-2XA-105 | J229-06-2XA-105 - VK-6H-2 - Circuit Breaker Tripped | J229-06-29-03 | DI | J229-06-2XA-105 - VK-6H-2 - Circuit Breaker Tripped | - | PVC | - | - | ALARM | NORMAL | - | - | - | - | - | - | PVC | NORMAL | ALARM | - | INVERTED | J229-06-2XA-105 - VK-6H-2 - Circuit Breaker Tripped | J229-06-2XA-105_CirBrkTrip | J229-06-2XA-105_CirBrkTrip |  |  | 1 | 1 | 2 | 1
1.0 | 46 | J270-06-1PNL-001 | J229-06-2XA-106 | J229-06-2XA-106 - VK-6H-2 - Voltage Surge Arrestor | J229-06-29-03 | DI | J229-06-2XA-106 - VK-6H-2 - Voltage Surge Arrestor | - | PVC | - | - | FAULT | NORMAL | - | - | - | - | - | - | PVC | NORMAL | FAULT | - | INVERTED | J229-06-2XA-106 - VK-6H-2 - Voltage Surge Arrestor | J229-06-2XA-106_SurgeVoltArr | J229-06-2XA-106_SurgeVoltArr |  |  | 1 | 1 | 2 | 2
1.0 | 47 | J270-06-1PNL-001 | J229-06-2XA-107 | J229-06-2XA-107 - VK-6H-3 - Circuit Breaker Tripped | J229-06-29-04 | DI | J229-06-2XA-107 - VK-6H-3 - Circuit Breaker Tripped | - | PVC | - | - | ALARM | NORMAL | - | - | - | - | - | - | PVC | NORMAL | ALARM | - | INVERTED | J229-06-2XA-107 - VK-6H-3 - Circuit Breaker Tripped | J229-06-2XA-107_CirBrkTrip | J229-06-2XA-107_CirBrkTrip |  |  | 1 | 1 | 2 | 3
1.0 | 48 | J270-06-1PNL-001 | J229-06-2XA-108 | J229-06-2XA-108 - VK-6H-3 - Voltage Surge Arrestor | J229-06-29-04 | DI | J229-06-2XA-108 - VK-6H-3 - Voltage Surge Arrestor | - | PVC | - | - | FAULT | NORMAL | - | - | - | - | - | - | PVC | NORMAL | FAULT | - | INVERTED | J229-06-2XA-108 - VK-6H-3 - Voltage Surge Arrestor | J229-06-2XA-108_SurgeVoltArr | J229-06-2XA-108_SurgeVoltArr |  |  | 1 | 1 | 2 | 4
1.0 | 49 | J270-06-1PNL-001 | J229-06-2XA-109 | J229-06-2XA-109 - VK-6H-4 - Circuit Breaker Tripped | J229-06-29-05 | DI | J229-06-2XA-109 - VK-6H-4 - Circuit Breaker Tripped | - | PVC | - | - | ALARM | NORMAL | - | - | - | - | - | - | PVC | NORMAL | ALARM | - | INVERTED | J229-06-2XA-109 - VK-6H-4 - Circuit Breaker Tripped | J229-06-2XA-109_CirBrkTrip | J229-06-2XA-109_CirBrkTrip |  |  | 1 | 1 | 2 | 5
1.0 | 50 | J270-06-1PNL-001 | J229-06-2XA-110 | J229-06-2XA-110 - VK-6H-4 - Voltage Surge Arrestor | J229-06-29-05 | DI | J229-06-2XA-110 - VK-6H-4 - Voltage Surge Arrestor | - | PVC | - | - | FAULT | NORMAL | - | - | - | - | - | - | PVC | NORMAL | FAULT | - | INVERTED | J229-06-2XA-110 - VK-6H-4 - Voltage Surge Arrestor | J229-06-2XA-110_SurgeVoltArr | J229-06-2XA-110_SurgeVoltArr |  |  | 1 | 1 | 2 | 6
1.0 | 51 | J270-06-1PNL-001 | J229-06-2XA-111 | J229-06-2XA-111 - VK-UPS-6H-5 - Circuit Breaker Tripped | J229-06-29-06 | DI | J229-06-2XA-111 - VK-UPS-6H-5 - Circuit Breaker Tripped | - | PVC | - | - | ALARM | NORMAL | - | - | - | - | - | - | PVC | NORMAL | ALARM | - | INVERTED | J229-06-2XA-111 - VK-UPS-6H-5 - Circuit Breaker Tripped | J229-06-2XA-111_CirBrkTrip | J229-06-2XA-111_CirBrkTrip |  |  | 1 | 1 | 2 | 7
1.0 | 52 | J270-06-1PNL-001 | J229-06-2XA-112 | J229-06-2XA-112 - VK-UPS-6H-5 - Voltage Surge Arrestor | J229-06-29-06 | DI | J229-06-2XA-112 - VK-UPS-6H-5 - Voltage Surge Arrestor | - | PVC | - | - | FAULT | NORMAL | - | - | - | - | - | - | PVC | NORMAL | FAULT | - | INVERTED | J229-06-2XA-112 - VK-UPS-6H-5 - Voltage Surge Arrestor | J229-06-2XA-112_SurgeVoltArr | J229-06-2XA-112_SurgeVoltArr |  |  | 1 | 1 | 2 | 8
1.0 | 53 | J270-06-1PNL-001 | J460-02-2FT-602 | J460-02-2FT-602 - 61LBK2 - Return Air Flow | J460-02-11-06-001 | AI | CMR232, P-Sensor, LCD, 24VDC, 100Pa, Modbus | 24VDC | 4-20mA | 500Ω | - | 0 | 21690 | m³/h | ±0.25% of Full Scale | CMR Controls | 232A000P0100M12 | NO | HM_CMR_232 | 2-10V | 0 | 21690 | m³/h |  | J460-02-2FT-602 - 61LBK2 - Return Air Flow | J460-02-2FT-602_RetAirFlow | J460-02-2FT-602_RetAirFlow |  |  | 1 | 1 | 5 | 8
1.0 | 54 | J270-06-1PNL-001 | J460-02-2TT-608 | J460-02-2TT-608 - 61LBK2 - Return Air Temperature | J460-02-11-06-001 | AI | Rotronic HF432 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C | 24VDC | 4-20mA | 500Ω | - | 0 | 50 | °C | ±0.2°C @ 23°C | Rotronic | HF432-DB1XX1XX | NO | HM_Rotronic_HF4 | 2-10V | 0 | 50 | °C |  | J460-02-2TT-608 - 61LBK2 - Return Air Temperature | J460-02-2TT-608_RetAirTemp | J460-02-2TT-608_RetAirTemp |  |  | 1 | 1 | 6 | 1
1.0 | 55 | J270-06-1PNL-001 | J460-02-2FT-601 | J460-02-2FT-601 - 61LBK2 - Supply Air Flow | J460-02-11-06-001 | AI | CMR232, P-Sensor, LCD, 24VDC, 100Pa, Modbus | 24VDC | 4-20mA | 500Ω | - | 0 | 21690 | m³/h | ±0.25% of Full Scale | CMR Controls | 232A000P0100M12 | NO | HM_CMR_232 | 2-10V | 0 | 21690 | m³/h |  | J460-02-2FT-601 - 61LBK2 - Supply Air Flow | J460-02-2FT-601_SupAirFlow | J460-02-2FT-601_SupAirFlow |  |  | 1 | 1 | 6 | 2
1.0 | 56 | J270-06-1PNL-001 | J460-02-2TT-607 | J460-02-2TT-607 - 61LBK2 - Supply Air Temperature | J460-02-11-06-001 | AI | Rotronic HF532 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C + HC2A-S | 24VDC | 4-20mA | 500Ω | - | 0 | 50 | °C | ±0.1°C @ 23°C | Rotronic | HF532-DB1XX1XX | NO | HM_Rotronic_HF5 | 2-10V | 0 | 50 | °C |  | J460-02-2TT-607 - 61LBK2 - Supply Air Temperature | J460-02-2TT-607_SupAirTemp | J460-02-2TT-607_SupAirTemp |  |  | 1 | 1 | 6 | 3
1.0 | 57 | J270-06-1PNL-001 | J460-02-2MT-607 | J460-02-2MT-607 - 61LBK2 - Supply Air Humidity | J460-02-11-06-001 | AI | Rotronic HF532 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C + HC2A-S | 24VDC | 4-20mA | 500Ω | - | 0 | 100 | % | ±0.8%RH @ 23°C | Rotronic | HF532-DB1XX1XX | NO | HM_Rotronic_HF5 | 2-10V | 0 | 100 | % |  | J460-02-2MT-607 - 61LBK2 - Supply Air Humidity | J460-02-2MT-607_SupAirHum | J460-02-2MT-607_SupAirHum |  |  | 1 | 1 | 6 | 4
1.0 | 58 | J270-06-1PNL-001 | J460-02-2KS-603 | J460-02-2KS-603 - Labs Day Extention Timer - Timer | J460-02-11-06-001 | DI | Vedotec DOT-U/1, 24VDC | 24VDC | PVC | - | - | OFF | ON | - | - | Royal | DOT-U/1 | NO |  | PVC | OFF | ON | - |  | J460-02-2KS-603 - Labs Day Extention Timer - Timer | J460-02-2KS-603_DET | J460-02-2KS-603_DET |  |  | 1 | 1 | 2 | 9
1.0 | 59 | J270-06-1PNL-001 | J460-02-2XI-603 | J460-02-2XI-603 - Labs Day Extention Timer - Indicator | J460-02-11-06-001 | DO | Jung, LEDKO6TX24, DC 24 V | 24VDC | 24VDC | - | - | OFF | ON | - | - | Jung | LEDKO6TX24 | NO |  | 24VDC | OFF | ON | - |  | J460-02-2XI-603 - Labs Day Extention Timer - Indicator | J460-02-2XI-603_DETLamp | J460-02-2XI-603_DETLamp |  |  | 1 | 1 | 10 | 4
1.0 | 60 | J270-06-1PNL-001 | J460-02-2XS-603 | J460-02-2XS-603 - Labs Day Extention Timer - Enable | J460-02-11-06-001 | DO | Vedotec DOT-U/1, 24VDC | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | Royal | DOT-U/1 | NO |  | 24DC | DISABLE | ENABLE | - |  | J460-02-2XS-603 - Labs Day Extention Timer - Enable | J460-02-2XS-603_DETEna | J460-02-2XS-603_DETEna |  |  | 1 | 1 | 10 | 5
2.1 | 61 | J270-06-1PNL-001 | J460-01-2TT-003 | J460-01-2TT-003 - Chilled Water - Return Temperature | J460-01-11-01-001 | AI | Rotronic TF532 Temperature sensor, 4-20mA, -40°C/60°C + 111103 + 102122 | 24VDC | 4-20mA | 500Ω | - | -40 | 60 | °C | 0.2K @ 23°C ±5°C | Rotronic | TF532-WT1XX1XX | NO | HM_Rotronic_TF5 | 2-10V | -40 | 60 | °C |  | J460-01-2TT-003 - Chilled Water - Return Temperature | J460-01-2TT-003_ChlWtrRetTemp | J460-01-2TT-003_ChlWtrRetTemp |  |  | 1 | 1 | 6 | 5
2.1 | 62 | J270-06-1PNL-001 | J460-01-2TT-002 | J460-01-2TT-002 - Chilled Water - Supply Temperature | J460-01-11-01-001 | AI | Rotronic TF532 Temperature sensor, 4-20mA, -40°C/60°C + 111103 + 102122 | 24VDC | 4-20mA | 500Ω | - | -40 | 60 | °C | 0.2K @ 23°C ±5°C | Rotronic | TF532-WT1XX1XX | NO | HM_Rotronic_TF5 | 2-10V | -40 | 60 | °C |  | J460-01-2TT-002 - Chilled Water - Supply Temperature | J460-01-2TT-002_ChlWtrSupTemp | J460-01-2TT-002_ChlWtrSupTemp |  |  | 1 | 1 | 6 | 6
1.0 | 63 | J270-06-1PNL-001 | J460-01-2FCV-001 | J460-01-2FCV-001 - Chilled Water Valve - Controller | J460-01-11-01-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | -
2.1 | 64 | J270-06-1PNL-001 | J460-01-1PMP-001 | J460-01-1PMP-001 - Chilled water Circulation pump - Controller | J460-01-11-01-001 | BACNET | Grundfos Magna 3 32-100 F; CIM\CIU 300 BACnet MSTP | [8 empty] | Grundfos | Magna 3 32-100 F | NO | TF-W-007 | - | - | - | - | See Profile PMP | - | - | - | bar: PVC to -
2 | 65 | J270-06-1PNL-001 | J460-01-1PMP-001 | J460-01-2XA-001 - Chilled water Circulation pump J460-01-1PMP-001 - Alarm | J460-01-11-06-001 | DI | Grundfos Magna 3 32-100 F | PVC | PVC | - | - | ALARM | NORMAL | - | - | Grundfos | Magna 3 32-100 F | NO | TF-W-007 | PVC | NORMAL | ALARM | - | INVERTED | J460-01-2XA-001 - Chilled water Circulation pump J460-01-1PMP-001 - Alarm | J460-01-2XA-001_ChlWtrCirPmpAlm | J460-01-2XA-001_ChlWtrCirPmpAlm |  |  | 1 | 1 | 2 | 10
2 | 66 | J270-06-1PNL-001 | J460-01-1PMP-001 | J460-01-2SS-001 - Chilled water Circulation pump J460-01-1PMP-001 - Status | J460-01-11-06-001 | DI | Grundfos Magna 3 32-100 F | PVC | PVC | - | - | STOP | RUN | - | - | Grundfos | Magna 3 32-100 F | NO | TF-W-007 | PVC | STOP | RUN | - | - | J460-01-2SS-001 - Chilled water Circulation pump J460-01-1PMP-001 - Status | J460-01-2SS-001_ChlWtrCirPmpSts | J460-01-2SS-001_ChlWtrCirPmpSts |  |  | 1 | 1 | 2 | 11
2 | 67 | J270-06-1PNL-001 | J460-01-1PMP-001 | J460-01-2SC-001 - Chilled water Circulation pump J460-01-1PMP-001 - Control Signal | J460-01-11-06-001 | AO | Grundfos Magna 3 32-100 F | - | 0-10V | - | - | 0 | 100 | % | - | Grundfos | Magna 3 32-100 F | NO | TF-W-007 | 0-10V | 0 | 100% | - | - | J460-01-2SC-001 - Chilled water Circulation pump J460-01-1PMP-001 - Control Signal | J460-01-2SC-001_ChlWtrCirPmpCntr | J460-01-2SC-001_ChlWtrCirPmpCntr |  |  | 1 | 1 | 9 | 2
2 | 68 | J270-06-1PNL-001 | J460-01-1PMP-001 | J460-01-2XS-001 - Chilled water Circulation pump J460-01-1PMP-001 - Enable | J460-01-11-06-001 | DO | Grundfos Magna 3 32-100 F | PVC | PVC | - | - | DISABLE | ENABLE | - | - | Grundfos | Magna 3 32-100 F | NO | TF-W-007 | PVC | DISABLE | ENABLE | - | - | J460-01-2XS-001 - Chilled water Circulation pump J460-01-1PMP-001 - Enable | J460-01-2XS-001_ChlWtrCirPmpEna | J460-01-2XS-001_ChlWtrCirPmpEna |  |  | 1 | 1 | 10 | 6
2 | 69 | J270-06-1PNL-001 | J460-01-1PMP-001 | J460-01-2HSI-001 - Chilled water Circulation pump J460-01-1PMP-001 - Maintanance Switch | J460-01-11-06-001 | DI | KRAUS&NAIMER KG10 T203/D-Axxx | PVC | PVC | - | - | OFF | ON | - | - | KRAUS&NAIMER | KG10 T203/D-Axxx | NO |  | PVC | OFF | ON | - | - | J460-01-2HSI-001 - Chilled water Circulation pump J460-01-1PMP-001 - Maintanance Switch | J460-01-2HSI-001_ChlWtrCirPmpMS | J460-01-2HSI-001_ChlWtrCirPmpMS |  |  | 1 | 1 | 2 | 12
1.0 | 70 | J270-06-1PNL-001 | J140-06-2FT-002 | J140-06-2FT-002 - Demi Water - Return Flow | J140-06-11-01 | AI | LIQUI-VIEW Base LVB-10-AD | 24VDC | 4-20mA | 500Ω | - | 2 | 40 | L/min | ≤1% @ FS | LIQUI-VIEW Base | LVB-10 | NO | TF-W-210 | 2-10V | 2 | 40 | L/min |  | J140-06-2FT-002 - Demi Water - Return Flow | J140-06-2FT-002_DmiWtrRetFlow | J140-06-2FT-002_DmiWtrRetFlow |  |  | 1 | 1 | 6 | 7
1.0 | 71 | J270-06-1PNL-001 | J140-06-2FT-001 | J140-06-2FT-001 - Demi Water - Supply Flow | J140-06-11-01 | AI | LIQUI-VIEW Base LVB-10-AD | 24VDC | 4-20mA | 500Ω | - | 2 | 40 | L/min | ≤1% @ FS | LIQUI-VIEW Base | LVB-10 | NO | TF-W-210 | 2-10V | 2 | 40 | L/min |  | J140-06-2FT-001 - Demi Water - Supply Flow | J140-06-2FT-001_DmiWtrSupFlow | J140-06-2FT-001_DmiWtrSupFlow |  |  | 1 | 1 | 6 | 8
1.0 | 72 | J270-06-1PNL-001 | J140-06-2PT-001 | J140-06-2PT-001 - Demi Water - Inlet Pressure | J140-06-11-01 | AI | Wika MG-1, 24VDC, 0-16Bar, 4-20mA | 24VDC | 4-20mA | 500Ω | - | 0 | 16 | Bar | ≤2% of Span | Wika | MG-1-6-BG416-HAZ2E-AA-M4Z-AA-ZZ | NO | TF-W-212 | 2-10V | 0 | 16 | Bar |  | J140-06-2PT-001 - Demi Water - Inlet Pressure | J140-06-2PT-001_DmiWtrInPress | J140-06-2PT-001_DmiWtrInPress |  |  | 1 | 1 | 7 | 1
1.0 | 73 | J270-06-1PNL-001 | J140-06-2PT-002 | J140-06-2PT-002 - Demi Water - Outlet Pressure | J140-06-11-01 | AI | Wika MG-1, 24VDC, 0-16Bar, 4-20mA | 24VDC | 4-20mA | 500Ω | - | 0 | 16 | Bar | ≤2% of Span | Wika | MG-1-6-BG416-HAZ2E-AA-M4Z-AA-ZZ | NO | TF-W-212 | 2-10V | 0 | 16 | Bar |  | J140-06-2PT-002 - Demi Water - Outlet Pressure | J140-06-2PT-002_DmiWtrOutPress | J140-06-2PT-002_DmiWtrOutPress |  |  | 1 | 1 | 7 | 2
1.0 | 74 | J270-06-1PNL-001 | J140-06-2PT-003 | J140-06-2PT-003 - Demi Water - Return Pressure | J140-06-11-01 | AI | Wika MG-1, 24VDC, 0-16Bar, 4-20mA | 24VDC | 4-20mA | 500Ω | - | 0 | 16 | Bar | ≤2% of Span | Wika | MG-1-6-BG416-HAZ2E-AA-M4Z-AA-ZZ | NO | TF-W-212 | 2-10V | 0 | 16 | Bar |  | J140-06-2PT-003 - Demi Water - Return Pressure | J140-06-2PT-003_DmiWtrRetPress | J140-06-2PT-003_DmiWtrRetPress |  |  | 1 | 1 | 7 | 3
2.1 | 75 | J270-06-1PNL-001 | J460-02-2TT-617 | J460-02-2TT-617 - Chilled Water - Return Temperature | J460-02-11-06-001 | AI | Rotronic TF532 Temperature sensor, 4-20mA, -40°C/60°C + 111103 + 102122 | 24VDC | 4-20mA | 500Ω | - | -40 | 60 | °C | 0.2K @ 23°C ±5°C | Rotronic | TF532-WT1XX1XX | NO | HM_Rotronic_TF5 | 2-10V | -40 | 60 | °C |  | J460-02-2TT-617 - Chilled Water - Return Temperature | J460-02-2TT-617_ChlWtrRetTemp | J460-02-2TT-617_ChlWtrRetTemp |  |  | 1 | 1 | 7 | 4
2.1 | 76 | J270-06-1PNL-001 | J460-02-2TT-616 | J460-02-2TT-616 - Chilled Water - Supply Temperature | J460-02-11-06-001 | AI | Rotronic TF532 Temperature sensor, 4-20mA, -40°C/60°C + 111103 + 102122 | 24VDC | 4-20mA | 500Ω | - | -40 | 60 | °C | 0.2K @ 23°C ±5°C | Rotronic | TF532-WT1XX1XX | NO | HM_Rotronic_TF5 | 2-10V | -40 | 60 | °C |  | J460-02-2TT-616 - Chilled Water - Supply Temperature | J460-02-2TT-616_ChlWtrSupTemp | J460-02-2TT-616_ChlWtrSupTemp |  |  | 1 | 1 | 7 | 5
1.0 | 77 | J270-06-1PNL-001 | J460-02-2FCV-624 | J460-02-2FCV-624 - Chilled Water Valve - Controller | J460-02-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | -
2.1 | 78 | J270-06-1PNL-001 | J460-02-1PMP-601 | J460-02-1PMP-601 - Chilled water Circulation pump - Controller | J460-02-11-06-001 | BACNET | Grundfos Magna 3 32-100 F; CIM\CIU 300 BACnet MSTP | [8 empty] | Grundfos | Magna 3 25-100 | NO | TF-W-007 | - | - | - | - | See Profile PMP | - | - | - | bar: PVC to -
2 | 79 | J270-06-1PNL-001 | J460-02-1PMP-601 | J460-02-2XA-601 - Chilled water Circulation pump J460-02-1PMP-601 - Alarm | J460-02-11-06-001 | DI | Grundfos Magna 3 25-100 | PVC | PVC | - | - | ALARM | NORMAL | - | - | Grundfos | Magna 3 25-100 | NO | TF-W-007 | PVC | NORMAL | ALARM | - | INVERTED | J460-02-2XA-601 - Chilled water Circulation pump J460-02-1PMP-601 - Alarm | J460-02-2XA-601_ChlWtrCirPmpAlm | J460-02-2XA-601_ChlWtrCirPmpAlm |  |  | 1 | 1 | 3 | 1
1.0 | 80 | J270-06-1PNL-001 | J460-02-1PMP-601 | J460-02-2SS-601 - Chilled water Circulation pump J460-02-1PMP-601 - Status | J460-02-11-06-001 | DI | Grundfos Magna 3 25-100 | PVC | PVC | - | - | STOP | RUN | - | - | Grundfos | Magna 3 25-100 | NO | TF-W-007 | PVC | STOP | RUN | - | - | J460-02-2SS-601 - Chilled water Circulation pump J460-02-1PMP-601 - Status | J460-02-2SS-601_ChlWtrCirPmpSts | J460-02-2SS-601_ChlWtrCirPmpSts |  |  | 1 | 1 | 3 | 2
2 | 81 | J270-06-1PNL-001 | J460-02-1PMP-601 | J460-02-2SC-601 - Chilled water Circulation pump J460-02-1PMP-601 - Control Signal | J460-02-11-06-001 | AO | Grundfos Magna 3 25-100 | - | 0-10V | - | - | 0 | 100 | % | - | Grundfos | Magna 3 25-100 | NO | TF-W-007 | 0-10V | 0 | 100% | - | - | J460-02-2SC-601 - Chilled water Circulation pump J460-02-1PMP-601 - Control Signal | J460-02-2SC-601_ChlWtrCirPmpCntr | J460-02-2SC-601_ChlWtrCirPmpCntr |  |  | 1 | 1 | 9 | 3
1.0 | 82 | J270-06-1PNL-001 | J460-02-1PMP-601 | J460-02-2XS-601 - Chilled water Circulation pump J460-02-1PMP-601 - Enable | J460-02-11-06-001 | DO | Grundfos Magna 3 25-100 | PVC | PVC | - | - | DISABLE | ENABLE | - | - | Grundfos | Magna 3 25-100 | NO | TF-W-007 | PVC | DISABLE | ENABLE | - | - | J460-02-2XS-601 - Chilled water Circulation pump J460-02-1PMP-601 - Enable | J460-02-2XS-601_ChlWtrCirPmpEna | J460-02-2XS-601_ChlWtrCirPmpEna |  |  | 1 | 1 | 11 | 1
2 | 83 | J270-06-1PNL-001 | J460-02-1PMP-601 | J460-02-2HSI-601 - Chilled water Circulation pump J460-02-1PMP-601 - Maintanance Switch | J460-02-11-06-001 | DI | KRAUS&NAIMER KG10 T203/D-Axxx | PVC | PVC | - | - | OFF | ON | - | - | KRAUS&NAIMER | KG10 T203/D-Axxx | NO |  | PVC | OFF | ON | - | - | J460-02-2HSI-601 - Chilled water Circulation pump J460-02-1PMP-601 - Maintanance Switch | J460-02-2HSI-601_ChlWtrCirPmpMS | J460-02-2HSI-601_ChlWtrCirPmpMS |  |  | 1 | 1 | 3 | 3
1.0 | 84 | J270-06-1PNL-001 | J460-02-2PT-902 | J460-02-2PT-902 - Exhaust Duct J460-02-2B-902- Pressure | J460-02-11-06-001 | AI | Huba 698, 24VDC, 4-20mA, 0-1000Pa | 24VDC | 4-20mA | 500Ω | - | 0 | 1000 | Pa | ±0.7% FS @25°C | Huba | 698.0081020101 | NO | HM_Huba_698 | 2-10V | 0 | 1000 | Pa | - | J460-02-2PT-902 - Exhaust Duct J460-02-2B-902- Pressure | J460-02-2PT-902_ExhFanPress | J460-02-2PT-902_ExhFanPress |  |  | 1 | 1 | 7 | 6
1.0 | 85 | J270-06-1PNL-001 | J460-02-2B-902 | J460-02-2XC-902 - Exhaust Fan J460-02-2B-902 - Control Signal | J460-02-11-06-001 | AO | Rood Fan, VRE-250-731W-1900EC-DR-090R-PPs | - | 0-10V | - | - | 0 | 100 | % | - | Mietzsch GmbH | VRE-250-731W-1900EC-DR-090R-PPs | NO | TF-W-105 | 0-10V | 0 | 100% | - | - | J460-02-2XC-902 - Exhaust Fan J460-02-2B-902 - Control Signal | J460-02-2XC-902_ExhFanCntr | J460-02-2XC-902_ExhFanCntr |  |  | 1 | 1 | 9 | 4
1.0 | 86 | J270-06-1PNL-001 | J460-02-2B-902 | J460-02-2XA-902 - Exhaust Fan J460-02-2B-902 - Alarm | J460-02-11-06-001 | DI | Rood Fan, VRE-250-731W-1900EC-DR-090R-PPs | - | PVC | - | - | ALARM | NORMAL | - | - | Mietzsch GmbH | VRE-250-731W-1900EC-DR-090R-PPs | NO | TF-W-105 | PVC | NORMAL | ALARM | - | INVERTED | J460-02-2XA-902 - Exhaust Fan J460-02-2B-902 - Alarm | J460-02-2XA-902_ExhFanAlm | J460-02-2XA-902_ExhFanAlm |  |  | 1 | 1 | 3 | 4
1.0 | 87 | J270-06-1PNL-001 | J460-02-2B-902 | J460-02-2HSI-902 - Exhaust Fan J460-02-2B-902- Maintanace Switch | J460-02-11-06-001 | DI | KRAUS&NAIMER KG10 T203/D-Axxx | PVC | PVC | - | - | OFF | ON | - | - | KRAUS&NAIMER | KG10 T203/D-Axxx | NO |  | PVC | OFF | ON | - | - | J460-02-2HSI-902 - Exhaust Fan J460-02-2B-902- Maintanace Switch | J460-01-2HSI-902_ExhFanMS | J460-01-2HSI-902_ExhFanMS |  |  | 1 | 1 | 3 | 5
2 | 88 | J270-06-1PNL-001 | J460-01-2TC-601 | J460-01-2TC-601 - Room J6.02 - Room Controller | J460-01-11-06-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | Office - Solo Room | J6.02
1.0 | 89 | J270-06-1PNL-001 | J460-01-2FCV-601 | J460-01-2FCV-601 - Room J6.02 - Reheater Valve Control | J460-01-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.02
2 | 90 | J270-06-1PNL-001 | J460-01-2TC-602 | J460-01-2TC-602 - Room J6.03 - Room Controller | J460-01-11-06-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | Office - Solo Room | J6.03
1.0 | 91 | J270-06-1PNL-001 | J460-01-2FCV-602 | J460-01-2FCV-602 - Room J6.03 - Reheater Valve Control | J460-01-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.03
2 | 92 | J270-06-1PNL-001 | J460-01-2TC-603 | J460-01-2TC-603 - Room J6.06 - Room Controller | J460-01-11-06-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | Office - Open Workspace | J6.06
1.0 | 93 | J270-06-1PNL-001 | J460-01-2FCV-603 | J460-01-2FCV-603 - Room J6.06 - J460-01-1ACU-601 Heating Valve Control | J460-01-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.06
2.1 | 94 | J270-06-1PNL-001 | J460-01-2FCV-604 | J460-01-2FCV-604 - Room J6.06 - J460-01-1ACU-602 Heating Valve Control | J460-01-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.06
1.0 | 95 | J270-06-1PNL-001 | J460-01-2FCV-605 | J460-01-2FCV-605 - Room J6.06 - J460-01-1ACU-603 Heating Valve Control | J460-01-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.06
1.0 | 96 | J270-06-1PNL-001 | J460-01-2FCV-606 | J460-01-2FCV-606 - Room J6.06 - J460-01-1ACU-604 Heating Valve Control | J460-01-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.06
1.0 | 97 | J270-06-1PNL-001 | J460-01-2FCV-607 | J460-01-2FCV-607 - Room J6.06 - J460-01-1ACU-601 Cooling Valve Control | J460-01-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.06
1.0 | 98 | J270-06-1PNL-001 | J460-01-2FCV-608 | J460-01-2FCV-608 - Room J6.06 - J460-01-1ACU-602 Cooling Valve Control | J460-01-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.06
1.0 | 99 | J270-06-1PNL-001 | J460-01-2FCV-609 | J460-01-2FCV-609 - Room J6.06 - J460-01-1ACU-603 Cooling Valve Control | J460-01-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.06
1.0 | 100 | J270-06-1PNL-001 | J460-01-2FCV-610 | J460-01-2FCV-610 - Room J6.06 - J460-01-1ACU-604 Cooling Valve Control | J460-01-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.06
1.0 | 101 | J270-06-1PNL-001 | J460-01-1VAV-601 | J460-01-2FC-601 - Room J6.06 - Return Air Flow Control. | J460-01-11-06-001 | BACNET | TROX VAV controller BM0 | 24VDC | BACNET | - | - | 0 | 300 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET | 0 | 300 | m³/h |  | - | - | - |  | J6.06
1.0 | 102 | J270-06-1PNL-001 | J460-01-1VAV-602 | J460-01-2FC-602 - Room J6.06 - Return Air Flow Control. | J460-01-11-06-001 | BACNET | TROX VAV controller BM0 | 24VDC | BACNET | - | - | 0 | 300 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET | 0 | 300 | m³/h |  | - | - | - |  | J6.06
1.0 | 103 | J270-06-1PNL-001 | J460-01-1VAV-603 | J460-01-2FC-603 - Room J6.06 - Supply Air Flow Control. | J460-01-11-06-001 | BACNET | TROX VAV controller BM0 | 24VDC | BACNET | - | - | 0 | 400 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET | 0 | 400 | m³/h |  | - | - | - |  | J6.06
1.0 | 104 | J270-06-1PNL-001 | J460-01-1VAV-604 | J460-01-2FC-604 - Room J6.06 - Return Air Flow Control. | J460-01-11-06-001 | BACNET | TROX VAV controller BM0 | 24VDC | BACNET | - | - | 0 | 200 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET | 0 | 200 | m³/h |  | - | - | - |  | J6.06
2 | 105 | J270-06-1PNL-001 | J460-01-2TC-612 | J460-01-2TC-612 - Room J6.04 - MDF Room Controller | J460-01-11-06-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | Office - MDF & Security Room | J6.04
1.0 | 106 | J270-06-1PNL-001 | J460-01-1ACU-618 | J460-01-1ACU-618 - Room J6.04 - Fan Coil unit Control | J460-01-11-06-001 | BACNET | Mitsubishi Electric, Bacnet-MSTP | - | Bacnet | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | J6.04
1.0 | 107 | J270-06-1PNL-001 | J460-01-1ACU-619 | J460-01-1ACU-619 - Room J6.04 - Fan Coil unit Control | J460-01-11-06-001 | BACNET | Mitsubishi Electric, Bacnet-MSTP | - | Bacnet | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | J6.04
2 | 108 | J270-06-1PNL-001 | J460-01-2TC-604 | J460-01-2TC-604 - Room J6.07 - Room Controller | J460-01-11-06-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | Office - Small meeting Room | J6.07
1.0 | 109 | J270-06-1PNL-001 | J460-01-2FCV-611 | J460-01-2FCV-611 - Room J6.07 - Reheater Valve Control | J460-01-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.07
1.0 | 110 | J270-06-1PNL-001 | J460-01-1VAV-605 | J460-01-2FC-605 - Room J6.07 - Supply Air Fow Control | J460-01-11-06-001 | BACNET | TROX VAV controller BM0 | 24VDC | BACNET | - | - | 0 | 350 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET | 0 | 350 | m³/h |  | - | - | - |  | J6.07
1.0 | 111 | J270-06-1PNL-001 | J460-01-1VAV-606 | J460-01-2FC-606 - Room J6.07 - Return Air Flow Control | J460-01-11-06-001 | BACNET | TROX VAV controller BM0 | 24VDC | BACNET | - | - | 0 | 350 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET | 0 | 350 | m³/h |  | - | - | - |  | J6.07
1.0 | 112 | J270-06-1PNL-001 | J460-01-2FCV-612 | J460-01-2FCV-612 - Room J6.06 - J460-01-1ACU-605 Heating Valve Control | J460-01-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.06
1.0 | 113 | J270-06-1PNL-001 | J460-01-2FCV-613 | J460-01-2FCV-613 - Room J6.06 - J460-01-1ACU-606 Heating Valve Control | J460-01-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.06
1.0 | 114 | J270-06-1PNL-001 | J460-01-2FCV-614 | J460-01-2FCV-614 - Room J6.06 - J460-01-1ACU-607 Heating Valve Control | J460-01-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.06
1.0 | 115 | J270-06-1PNL-001 | J460-01-2FCV-615 | J460-01-2FCV-615 - Room J6.06 - J460-01-1ACU-608 Heating Valve Control | J460-01-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.06
1.0 | 116 | J270-06-1PNL-001 | J460-01-2FCV-616 | J460-01-2FCV-616 - Room J6.06 - J460-01-1ACU-605 Cooling Valve Control | J460-01-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.06
1.0 | 117 | J270-06-1PNL-001 | J460-01-2FCV-617 | J460-01-2FCV-617 - Room J6.06 - J460-01-1ACU-606 Cooling Valve Control | J460-01-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.06
1.0 | 118 | J270-06-1PNL-001 | J460-01-2FCV-618 | J460-01-2FCV-618 - Room J6.06 - J460-01-1ACU-607 Cooling Valve Control | J460-01-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.06
1.0 | 119 | J270-06-1PNL-001 | J460-01-2FCV-619 | J460-01-2FCV-619 - Room J6.06 - J460-01-1ACU-608 Cooling Valve Control | J460-01-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.06
1.0 | 120 | J270-06-1PNL-001 | J460-01-1VAV-607 | J460-01-2FC-607 - Room J6.06 - Return Air Flow Control | J460-01-11-06-001 | BACNET | TROX VAV controller BM0 | 24VDC | BACNET | - | - | 0 | 200 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET | 0 | 200 | m³/h |  | - | - | - |  | J6.06
1.0 | 121 | J270-06-1PNL-001 | J460-01-1VAV-608 | J460-01-2FC-608 - Room J6.06 - Supply Air Fow Control | J460-01-11-06-001 | BACNET | TROX VAV controller BM0 | 24VDC | BACNET | - | - | 0 | 400 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET | 0 | 400 | m³/h |  | - | - | - |  | J6.06
2 | 122 | J270-06-1PNL-001 | J460-01-2TC-605 | J460-01-2TC-605 - Room J6.05 - Room Controller | J460-01-11-06-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | Office - Focus Room | J6.05
1.0 | 123 | J270-06-1PNL-001 | J460-01-2FCV-620 | J460-01-2FCV-620 - Room J6.05 - Reheater Valve Control | J460-01-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.05
1.0 | 124 | J270-06-1PNL-001 | J460-01-1VAV-610 | J460-01-2FC-610 - Room J6.05 - Return Air Flow Control | J460-01-11-06-001 | BACNET | TROX VAV controller BM0 | 24VDC | BACNET | - | - | 0 | 250 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET | 0 | 250 | m³/h |  | - | - | - |  | J6.05
2.1 | 125 | J270-06-1PNL-001 | J460-01-1VAV-609 | J460-01-2FC-609 - Room J6.05 - Supply Air Fow Control | J460-01-11-06-001 | BACNET | TROX VAV controller BM0 | 24VDC | BACNET | - | - | 0 | 250 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET | 0 | 250 | m³/h |  | - | - | - |  | J6.05
1.0 | 126 | J270-06-1PNL-001 | J460-01-2FCV-621 | J460-01-2FCV-621 - Room J6.06 - J460-01-1ACU-609 Heating Valve Control | J460-01-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.06
1.0 | 127 | J270-06-1PNL-001 | J460-01-2FCV-622 | J460-01-2FCV-622 - Room J6.06 - J460-01-1ACU-609 Cooling Valve Control | J460-01-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.06
1.0 | 128 | J270-06-1PNL-001 | J460-01-1VAV-611 | J460-01-2FC-611 - Room J6.06 - Supply Air Fow Control | J460-01-11-06-001 | BACNET | TROX VAV controller BM0 | 24VDC | BACNET | - | - | 0 | 200 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET | 0 | 200 | m³/h |  | - | - | - |  | J6.06
2 | 129 | J270-06-1PNL-001 | J460-01-2TC-606 | J460-01-2TC-606 - Room J6.08 - Room Controller | J460-01-11-06-002 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | Office - Solo Room | J6.08
1.0 | 130 | J270-06-1PNL-001 | J460-01-2FCV-623 | J460-01-2FCV-623 - Room J6.08 - Reheater Valve Control | J460-01-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.08
2 | 131 | J270-06-1PNL-001 | J460-01-2TC-607 | J460-01-2TC-607 - Room J6.09 - Room Controller | J460-01-11-06-002 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | Office - Team Den/ Scrum Area | J6.09
1.0 | 132 | J270-06-1PNL-001 | J460-01-2FCV-624 | J460-01-2FCV-624 - Room J6.09 - J460-01-1ACU-610 Heating Valve Control | J460-01-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.09
1.0 | 133 | J270-06-1PNL-001 | J460-01-2FCV-625 | J460-01-2FCV-625 - Room J6.09 - J460-01-1ACU-611 Heating Valve Control | J460-01-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.09
1.0 | 134 | J270-06-1PNL-001 | J460-01-2FCV-626 | J460-01-2FCV-626 - Room J6.09 - J460-01-1ACU-612 Heating Valve Control | J460-01-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.09
1.0 | 135 | J270-06-1PNL-001 | J460-01-2FCV-627 | J460-01-2FCV-627 - Room J6.09 - J460-01-1ACU-613 Heating Valve Control | J460-01-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.09
1.0 | 136 | J270-06-1PNL-001 | J460-01-2FCV-628 | J460-01-2FCV-628 - Room J6.09 - J460-01-1ACU-610 Cooling Valve Control | J460-01-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.09
1.0 | 137 | J270-06-1PNL-001 | J460-01-2FCV-629 | J460-01-2FCV-629 - Room J6.09 - J460-01-1ACU-611 Cooling Valve Control | J460-01-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.09
1.0 | 138 | J270-06-1PNL-001 | J460-01-2FCV-630 | J460-01-2FCV-630 - Room J6.09 - J460-01-1ACU-612 Cooling Valve Control | J460-01-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.09
1.0 | 139 | J270-06-1PNL-001 | J460-01-2FCV-631 | J460-01-2FCV-631 - Room J6.09 - J460-01-1ACU-613 Cooling Valve Control | J460-01-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.09
1.0 | 140 | J270-06-1PNL-001 | J460-01-1VAV-612 | J460-01-2FC-612 - Room J6.09 - Return Air Flow Control | J460-01-11-06-002 | BACNET | TROX VAV controller BM0 | 24VDC | BACNET | - | - | 0 | 400 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET | 0 | 400 | m³/h |  | - | - | - |  | J6.09
1.0 | 141 | J270-06-1PNL-001 | J460-01-1VAV-613 | J460-01-2FC-613 - Room J6.09 - Supply Air Fow Control | J460-01-11-06-002 | BACNET | TROX VAV controller BM0 | 24VDC | BACNET | - | - | 0 | 400 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET | 0 | 400 | m³/h |  | - | - | - |  | J6.09
2 | 142 | J270-06-1PNL-001 | J460-01-2TC-608 | J460-01-2TC-608 - Room J6.10 - Room Controller | J460-01-11-06-002 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | Office - Solo Room | J6.10
1.0 | 143 | J270-06-1PNL-001 | J460-01-2FCV-632 | J460-01-2FCV-632 - Room J6.10 - Reheater Valve Control | J460-01-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.10
2 | 144 | J270-06-1PNL-001 | J460-01-2TC-609 | J460-01-2TC-609 - Room J6.11 - Room Controller | J460-01-11-06-002 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | Office - Open Workspace | J6.11
1.0 | 145 | J270-06-1PNL-001 | J460-01-2FCV-633 | J460-01-2FCV-633 - Room J6.11 - J460-01-1ACU-614 Heating Valve Control | J460-01-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.11
1.0 | 146 | J270-06-1PNL-001 | J460-01-2FCV-634 | J460-01-2FCV-634 - Room J6.11 - J460-01-1ACU-615 Heating Valve Control | J460-01-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.11
1.0 | 147 | J270-06-1PNL-001 | J460-01-2FCV-635 | J460-01-2FCV-635 - Room J6.11 - J460-01-1ACU-616 Heating Valve Control | J460-01-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.11
1.0 | 148 | J270-06-1PNL-001 | J460-01-2FCV-636 | J460-01-2FCV-636 - Room J6.11 - J460-01-1ACU-617 Heating Valve Control | J460-01-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.11
1.0 | 149 | J270-06-1PNL-001 | J460-01-2FCV-637 | J460-01-2FCV-637 - Room J6.11 - J460-01-1ACU-614 Cooling Valve Control | J460-01-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.11
1.0 | 150 | J270-06-1PNL-001 | J460-01-2FCV-638 | J460-01-2FCV-638 - Room J6.11 - J460-01-1ACU-615 Cooling Valve Control | J460-01-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.11
1.0 | 151 | J270-06-1PNL-001 | J460-01-2FCV-639 | J460-01-2FCV-639 - Room J6.11 - J460-01-1ACU-616 Cooling Valve Control | J460-01-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.11
1.0 | 152 | J270-06-1PNL-001 | J460-01-2FCV-640 | J460-01-2FCV-640 - Room J6.11 - J460-01-1ACU-617 Cooling Valve Control | J460-01-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.11
1.0 | 153 | J270-06-1PNL-001 | J460-01-1VAV-614 | J460-01-2FC-614 - Room J6.11 - Return Air Flow Control | J460-01-11-06-002 | BACNET | TROX VAV controller BM0 | 24VDC | BACNET | - | - | 0 | 500 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET | 0 | 500 | m³/h |  | - | - | - |  | J6.11
1.0 | 154 | J270-06-1PNL-001 | J460-01-1VAV-615 | J460-01-2FC-615 - Room J6.11 - Supply Air Fow Control | J460-01-11-06-002 | BACNET | TROX VAV controller BM0 | 24VDC | BACNET | - | - | 0 | 500 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET | 0 | 500 | m³/h |  | - | - | - |  | J6.11
2 | 155 | J270-06-1PNL-001 | J460-01-2TC-610 | J460-01-2TC-610 - Room J6.13 - Room Controller | J460-01-11-06-002 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | Office - Solo Room | J6.13
1.0 | 156 | J270-06-1PNL-001 | J460-01-2FCV-641 | J460-01-2FCV-641 - Room J6.13 - Reheater Valve Control | J460-01-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.13
1.0 | 157 | J270-06-1PNL-001 | J460-01-1VAV-616 | J460-01-2FC-616 - Room J6.13 - Supply Air Fow Control | J460-01-11-06-002 | BACNET | TROX VAV controller BM0 | 24VDC | BACNET | - | - | 0 | 150 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET | 0 | 150 | m³/h |  | - | - | - |  | J6.13
1.0 | 158 | J270-06-1PNL-001 | J460-01-1VAV-617 | J460-01-2FC-617 - Room J6.13 - Return Air Flow Control | J460-01-11-06-002 | BACNET | TROX VAV controller BM0 | 24VDC | BACNET | - | - | 0 | 125 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET | 0 | 125 | m³/h |  | - | - | - |  | J6.13
2 | 159 | J270-06-1PNL-001 | J460-01-2TC-611 | J460-01-2TC-611 - Room J6.12 - Room Controller | J460-01-11-06-002 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | Office - Solo Room | J6.12
1.0 | 160 | J270-06-1PNL-001 | J460-01-2FCV-642 | J460-01-2FCV-642 - Room J6.12 - Reheater Valve Control | J460-01-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.12
2 | 161 | J270-06-1PNL-001 | J460-02-2TC-601 | J460-02-2TC-601 - Room J6.20 - Lab Controller | J460-02-11-06-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - MOI | J6.20
1.0 | 162 | J270-06-1PNL-001 | J460-02-2FCV-601 | J460-02-2FCV-601 - Room J6.20 - Reheater Valve Control | J460-02-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.20
1.0 | 163 | J270-06-1PNL-001 | J460-02-2FCV-602 | J460-02-2FCV-602 - Room J6.20 - J460-02-1ACU-602 Cooling Valve Control | J460-02-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.20
1.0 | 164 | J270-06-1PNL-001 | J460-02-1VAV-601 | J460-02-2FC-601 - Room J6.20 - Air Fow Control (Slave VAV-602, VAV-603, VAV-604) | J460-02-11-06-001 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J6.20
2 | 165 | J270-06-1PNL-001 | J460-02-2TC-602 | J460-02-2TC-602 - Room J6.22 - Lab Controller | J460-02-11-06-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - Cleaning & Storage | J6.22
1.0 | 166 | J270-06-1PNL-001 | J460-02-2FCV-603 | J460-02-2FCV-603 - Room J6.22 - J460-02-1ACU-601 Cooling Valve Control | J460-02-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.22
1.0 | 167 | J270-06-1PNL-001 | J460-02-2FCV-604 | J460-02-2FCV-604 - Room J6.22 - J460-02-1ACU-601 Heating Valve Control | J460-02-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.22
1.0 | 168 | J270-06-1PNL-001 | J460-02-1VAV-605 | J460-02-2FC-605 - Room J6.22 - Air Fow Control (Slave VAV-644, VAV-606) | J460-02-11-06-001 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J6.22
1.0 | 169 | J270-06-1PNL-001 | J460-02-1VAV-606 | J460-02-2XU-606 - Room J6.22 - Fume hood. | J460-02-11-06-001 | BACNET | Shneider FC700 | - | Bacnet | - | - | - | - | - | - | Shneider | FC700 | NO |  | Bacnet | - | - | - | See Profile FC700 | - | - | - |  | J6.22
2 | 170 | J270-06-1PNL-001 | J460-02-2TC-603 | J460-02-2TC-603 - Room J6.23 - Lab Controller | J460-02-11-06-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - ELISA | J6.23
1.0 | 171 | J270-06-1PNL-001 | J460-02-2FCV-605 | J460-02-2FCV-605 - Room J6.23 - Reheater Valve Control | J460-02-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.23
1.0 | 172 | J270-06-1PNL-001 | J460-02-1VAV-607 | J460-02-2FC-607 - Room J6.23 - Air Fow Control (Slave VAV-608) | J460-02-11-06-001 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J6.23
1.0 | 173 | J270-06-1PNL-001 | J460-02-2FCV-606 | J460-02-2FCV-606 - Room J6.23 - Reheater Valve Control | J460-02-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.23
1.0 | 174 | J270-06-1PNL-001 | J460-02-2FCV-607 | J460-02-2FCV-607 - Room J6.23 - J460-02-1ACU-603 Cooling Valve Control | J460-02-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.23
1.0 | 175 | J270-06-1PNL-001 | J460-02-1VAV-609 | J460-02-2FC-609 - Room J6.23 - Air Fow Control (Slave VAV-610, VAV-611) | J460-02-11-06-001 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J6.23
2 | 176 | J270-06-1PNL-001 | J460-02-2TC-609 | J460-02-2TC-609 - Room J6.23 - Lab Controller | J460-02-11-06-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - ELISA | J6.23
1.0 | 177 | J270-06-1PNL-001 | J460-02-2FCV-608 | J460-02-2FCV-608 - Room J6.23 - Reheater Valve Control | J460-02-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.23
1.0 | 178 | J270-06-1PNL-001 | J460-02-2FCV-609 | J460-02-2FCV-609 - Room J6.23 - J460-02-1ACU-604 Cooling Valve Control | J460-02-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.23
1.0 | 179 | J270-06-1PNL-001 | J460-02-1VAV-612 | J460-02-2FC-612 - Room J6.23 - Air Fow Control (Slave VAV-613, VAV-614) | J460-02-11-06-001 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J6.23
2 | 180 | J270-06-1PNL-001 | J460-02-2TC-610 | J460-02-2TC-610 - Room J6.23 - Lab Controller | J460-02-11-06-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - ELISA | J6.23
1.0 | 181 | J270-06-1PNL-001 | J460-02-2FCV-610 | J460-02-2FCV-610 - Room J6.23 - Reheater Valve Control | J460-02-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.23
1.0 | 182 | J270-06-1PNL-001 | J460-02-2FCV-611 | J460-02-2FCV-611 - Room J6.23 - J460-02-1ACU-605 Cooling Valve Control | J460-02-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.23
1.0 | 183 | J270-06-1PNL-001 | J460-02-1VAV-615 | J460-02-2FC-615 - Room J6.23 - Air Fow Control (Slave VAV-616, VAV-617, VAV-618) | J460-02-11-06-001 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J6.23
2 | 184 | J270-06-1PNL-001 | J460-02-2TC-604 | J460-02-2TC-604 - Room J6.24 - Lab Controller | J460-02-11-06-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - Sample Management | J6.24
1.0 | 185 | J270-06-1PNL-001 | J460-02-2FCV-612 | J460-02-2FCV-612 - Room J6.24 - Reheater Valve Control | J460-02-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.24
1.0 | 186 | J270-06-1PNL-001 | J460-02-2FCV-613 | J460-02-2FCV-613 - Room J6.24 - J460-02-1ACU-606 Cooling Valve Control | J460-02-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.24
1.0 | 187 | J270-06-1PNL-001 | J460-02-1VAV-619 | J460-02-2FC-619 - Room J6.24 - Air Fow Control (Slave VAV-620) | J460-02-11-06-001 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J6.24
2 | 188 | J270-06-1PNL-001 | J460-02-2TC-611 | J460-02-2TC-611 - Room J6.24 - Lab Controller | J460-02-11-06-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - Sample Management | J6.24
1.0 | 189 | J270-06-1PNL-001 | J460-02-2FCV-614 | J460-02-2FCV-614 - Room J6.24 - Reheater Valve Control | J460-02-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.24
1.0 | 190 | J270-06-1PNL-001 | J460-02-2FCV-615 | J460-02-2FCV-615 - Room J6.24 - J460-02-1ACU-607 Cooling Valve Control | J460-02-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.24
1.0 | 191 | J270-06-1PNL-001 | J460-02-1VAV-621 | J460-02-2FC-621 - Room J6.24 - Air Fow Control (Slave VAV-622) | J460-02-11-06-001 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J6.24
1.0 | 192 | J270-06-1PNL-001 | J460-02-2FCV-616 | J460-02-2FCV-616 - Room J6.20 - Reheater Valve Control | J460-02-11-06-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.20
1.0 | 193 | J270-06-1PNL-001 | J460-02-1VAV-623 | J460-02-2FC-623 - Room J6.20 - Air Fow Control (Slave VAV-624, VAV-625) | J460-02-11-06-001 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J6.20
2 | 194 | J270-06-1PNL-001 | J460-02-2TC-612 | J460-02-2TC-612 - Room J6.20 - Lab Controller | J460-02-11-06-002 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - MOI | J6.20
1.0 | 195 | J270-06-1PNL-001 | J460-02-2FCV-617 | J460-02-2FCV-617 - Room J6.20 - Reheater Valve Control | J460-02-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.20
1.0 | 196 | J270-06-1PNL-001 | J460-02-2FCV-618 | J460-02-2FCV-618 - Room J6.20 - J460-02-1ACU-609 Cooling Valve Control | J460-02-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.20
1.0 | 197 | J270-06-1PNL-001 | J460-02-1VAV-626 | J460-02-2FC-626 - Room J6.20 - Air Fow Control (Slave VAV-627, VAV-628, VAV-629) | J460-02-11-06-002 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J6.20
2 | 198 | J270-06-1PNL-001 | J460-02-2TC-605 | J460-02-2TC-605 - Room J6.17 - Lab Controller | J460-02-11-06-002 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - Clean & Unch. Cell culture | J6.17
1.0 | 199 | J270-06-1PNL-001 | J460-02-2FCV-619 | J460-02-2FCV-619 - Room J6.17 - Reheater Valve Control | J460-02-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.17
1.0 | 200 | J270-06-1PNL-001 | J460-02-1VAV-630 | J460-02-2FC-630 - Room J6.17 - Air Fow Control (Slave VAV-631, VAV-632) | J460-02-11-06-002 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J6.17
2 | 201 | J270-06-1PNL-001 | J460-02-2TC-613 | J460-02-2TC-613 - Room J6.17 - Lab Controller | J460-02-11-06-002 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - Clean & Unch. Cell culture | J6.17
1.0 | 202 | J270-06-1PNL-001 | J460-02-2FCV-620 | J460-02-2FCV-620 - Room J6.17 - Reheater Valve Control | J460-02-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.17
1.0 | 203 | J270-06-1PNL-001 | J460-02-1VAV-633 | J460-02-2FC-633 - Room J6.17 - Air Fow Control (Slave VAV-634, VAV-635) | J460-02-11-06-002 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J6.17
2 | 204 | J270-06-1PNL-001 | J460-02-2TC-614 | J460-02-2TC-614 - Room J6.17 - Lab Controller | J460-02-11-06-002 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - Clean & Unch. Cell culture | J6.17
1.0 | 205 | J270-06-1PNL-001 | J460-02-2FCV-621 | J460-02-2FCV-621 - Room J6.17 - Reheater Valve Control | J460-02-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.17
1.0 | 206 | J270-06-1PNL-001 | J460-02-1VAV-636 | J460-02-2FC-636 - Room J6.17 - Air Fow Control (Slave VAV-637, VAV-638) | J460-02-11-06-002 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J6.17
2 | 207 | J270-06-1PNL-001 | J460-02-2TC-606 | J460-02-2TC-606 - Room J6.14 - Lab Controller | J460-02-11-06-002 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - Clean cell based methods | J6.14
1.0 | 208 | J270-06-1PNL-001 | J460-02-2FCV-622 | J460-02-2FCV-622 - Room J6.14 - Reheater Valve Control | J460-02-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.14
1.0 | 209 | J270-06-1PNL-001 | J460-02-1VAV-639 | J460-02-2FC-639 - Room J6.14 - Air Fow Control (Slave VAV-640, VAV-641) | J460-02-11-06-002 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J6.14
2 | 210 | J270-06-1PNL-001 | J460-02-2TC-615 | J460-02-2TC-615 - Room J6.14 - Lab Controller | J460-02-11-06-002 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - Clean cell based methods | J6.14
1.0 | 211 | J270-06-1PNL-001 | J460-02-2FCV-623 | J460-02-2FCV-623 - Room J6.14 - Reheater Valve Control | J460-02-11-06-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J6.14
1.0 | 212 | J270-06-1PNL-001 | J460-02-1VAV-642 | J460-02-2FC-642 - Room J6.14 - Air Fow Control (Slave VAV-643, VAV-664) | J460-02-11-06-002 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J6.14
2 | 213 | J270-06-1PNL-001 | J460-01-2TC-001 | J460-01-2TC-001 - Room J0.07 - Room Controller | J460-01-11-01-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RL1644MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | Office - Energy Room / Team Den | J0.07
1.0 | 214 | J270-06-1PNL-001 | J460-01-2FCV-002 | J460-01-2FCV-002 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control | J460-01-11-01-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J0.07
1.0 | 215 | J270-06-1PNL-001 | J460-01-2FCV-003 | J460-01-2FCV-003 - Room J0.07 - J460-01-1ACU-002 Heating Valve Control | J460-01-11-01-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J0.07
1.0 | 216 | J270-06-1PNL-001 | J460-01-2FCV-004 | J460-01-2FCV-004 - Room J0.07 - J460-01-1ACU-003 Heating Valve Control | J460-01-11-01-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J0.07
1.0 | 217 | J270-06-1PNL-001 | J460-01-2FCV-005 | J460-01-2FCV-005 - Room J0.07 - J460-01-1ACU-004 Heating Valve Control | J460-01-11-01-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J0.07
1.0 | 218 | J270-06-1PNL-001 | J460-01-2FCV-006 | J460-01-2FCV-006 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control | J460-01-11-01-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J0.07
1.0 | 219 | J270-06-1PNL-001 | J460-01-2FCV-007 | J460-01-2FCV-007 - Room J0.07 - J460-01-1ACU-002 Cooling Valve Control | J460-01-11-01-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J0.07
1.0 | 220 | J270-06-1PNL-001 | J460-01-2FCV-008 | J460-01-2FCV-008 - Room J0.07 - J460-01-1ACU-003 Cooling Valve Control | J460-01-11-01-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J0.07
1.0 | 221 | J270-06-1PNL-001 | J460-01-2FCV-009 | J460-01-2FCV-009 - Room J0.07 - J460-01-1ACU-004 Cooling Valve Control | J460-01-11-01-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J0.07
1.0 | 222 | J270-06-1PNL-001 | J460-01-1VAV-001 | J460-01-2FC-001 - Room J0.07 - Return Air Flow Control | J460-01-11-01-001 | BACNET | TROX VAV controller BM0 | 24VDC | Bacnet | - | - | 0 | 650 | m³/h | - | TROX | BM0 | NO | TF-W-111 | Bacnet | 0 | 650 | m³/h | See Profile BM0 | - | - | - | - | J0.07
1.0 | 223 | J270-06-1PNL-001 | J460-01-1VAV-002 | J460-01-2FC-002 - Room J0.07 - Supply Air Flow Control | J460-01-11-01-001 | BACNET | TROX VAV controller BM0 | 24VDC | Bacnet | - | - | 0 | 650 | m³/h | - | TROX | BM0 | NO | TF-W-111 | Bacnet | 0 | 650 | m³/h | See Profile BM0 | - | - | - | - | J0.07
Note on E96: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ACU-601 replaced with 602
Note on E100: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ACU-601 replaced with 602
Note on D127: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Replaced 610 to 609

## RackPositioning (hidden)
7448-15-1PNL-001 |  | 7448-15-1PNL-001 Expansion
Description | Module Quantity | Description | Module Quantity
Analog Input (8 channel) | 0 | Analog Input (8 channel) | 0
Analog Input hi level (16 ch) | 5 | Analog Input hi level (16 ch) | 0
Analog Outputs 0 to 20mA (8 channel, 5 modules/rack) | 0 | Analog Outputs 0 to 20mA (8 channel, 5 modules/rack) | 0
Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 2 | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 2
Digital Input, 24VDC (32 channel) | 3 | Digital Input, 24VDC (32 channel) | 0
Digital Output, Relays ( 8 channel) | 2 | Digital Output, Relays ( 8 channel) | 1
| 12 |  | 3
Module assignement for this panel |  | Module assignement for this panel
Discription | Rack slot | Discription | Rack slot
Controller C70 CPU | 0 | I/O Scanner | 0
Power Supply 120/240VAC, 60W | 0 | Power Supply 120/240VAC, 60W | 0
Digital Input, 24VDC (32 channel) | 1 | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 1
Digital Input, 24VDC (32 channel) | 2 | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 2
Digital Input, 24VDC (32 channel) | 3 | Digital Output, Relays ( 8 channel) | 3
Analog Input hi level (16 ch) | 4 | SPARE | 4
Analog Input hi level (16 ch) | 5
Analog Input hi level (16 ch) | 6
Analog Input hi level (16 ch) | 7
Analog Input hi level (16 ch) | 8
Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 9
Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 10
Digital Output, Relays ( 8 channel) | 11
Digital Output, Relays ( 8 channel) | 12

## RoomControllers
IO CPNX/JACE
Version | Nr | Outstation | Device Tag | Point Descriptor | PID Nr | IO Type | Description | Power | Signal Type | Converter | Splitter | Range (Low) | Range (High) | Unit | Accuracy | Mfgr | Model | Cal Cert Req | Tech Datasheet Nr | Signal Type (CPNX/JACE) | Range (Low) (CPNX/JACE) | Range (High) (CPNX/JACE) | Unit (CPNX/JACE) | Remark (CPNX/JACE) | EBI Point Descriptor | EBI Tag | JACE Tag | Remarks | Room Number | JACE | RS485 COM | Module No | Channel No
1.0 | 1 | J460-01-1CP-601 | J460-01-2TT-601 | J460-01-2TT-601 - Room J6.02 - Temperature | J460-01-11-06-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR42-H | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-01-2TT-601 - Room J6.02 - Temperature | J460-01-2TT-601_RmTemp | J460-01-2TT-601_RmTemp |  | J6.02
1.0 | 2 | J460-01-1CP-601 | J460-01-2MT-601 | J460-01-2MT-601 - Room J6.02 - Humidity | J460-01-11-06-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR42-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-01-2MT-601 - Room J6.02 - Humidity | J460-02-2MT-601_RmHum | J460-02-2MT-601_RmHum |  | J6.02
2.1 | 3 | J460-01-1CP-601 | J460-01-2XT-612 | J460-01-2XT-612 - Room J6.02 - Occupied | J460-01-11-06-001 | (UIO) DI | PIR 360°, 24VDC, ON/OFF Delay | 24VDC | PVC | - | - | UNOCC | OCC | - | - | Calectro | PIR-TF-25-360 | NO | HM_Betec_PIR-TF-25-360 | PVC | UNOCC | OCC | - |  | J460-01-2XT-612 - Room J6.02 - Occupied | J460-01-2XT-612_RmOcc | J460-01-2XT-612_RmOcc |  | J6.02 |  |  |  | (UIO) DI1
1.0 | 4 | J460-01-1CP-602 | J460-01-2TT-602 | J460-01-2TT-602 - Room J6.03 - Temperature | J460-01-11-06-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR42-H | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-01-2TT-602 - Room J6.03 - Temperature | J460-02-2TT-602_RmTemp | J460-02-2TT-602_RmTemp |  | J6.03
1.0 | 5 | J460-01-1CP-602 | J460-01-2MT-602 | J460-01-2MT-602 - Room J6.03 - Humidity | J460-01-11-06-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR42-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-01-2MT-602 - Room J6.03 - Humidity | J460-02-2MT-602_RmHum | J460-02-2MT-602_RmHum |  | J6.03
2.1 | 6 | J460-01-1CP-602 | J460-01-2XT-613 | J460-01-2XT-613 - Room J6.03 - Occupied | J460-01-11-06-001 | (UIO) DI | PIR 360°, 24VDC, ON/OFF Delay | 24VDC | PVC | - | - | UNOCC | OCC | - | - | Calectro | PIR-TF-25-360 | NO | HM_Betec_PIR-TF-25-360 | PVC | UNOCC | OCC | - |  | J460-01-2XT-613 - Room J6.03 - Occupied | J460-01-2XT-613_RmOcc | J460-01-2XT-613_RmOcc |  | J6.03 |  |  |  | (UIO) DI1
1.0 | 7 | J460-01-1CP-603 | J460-01-2TT-603 | J460-01-2TT-603 - Room J6.06 - Temperature | J460-01-11-06-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-01-2TT-603 - Room J6.06 - Temperature | J460-02-2TT-603_RmTemp | J460-02-2TT-603_RmTemp |  | J6.06
1.0 | 8 | J460-01-1CP-603 | J460-01-2MT-603 | J460-01-2MT-603 - Room J6.06 - Humidity | J460-01-11-06-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-01-2MT-603 - Room J6.06 - Humidity | J460-02-2MT-603_RmHum | J460-02-2MT-603_RmHum |  | J6.06
2.1 | 10 | J460-01-1CP-603 | J460-01-2XT-614 | J460-01-2XT-614 - Room J6.06 - Occupied | J460-01-11-06-001 | (UIO) DI | PIR 360°, 24VDC, ON/OFF Delay | 24VDC | PVC | - | - | UNOCC | OCC | - | - | Calectro | PIR-TF-25-360 | NO | HM_Betec_PIR-TF-25-360 | PVC | UNOCC | OCC | - |  | J460-01-2XT-614 - Room J6.06 - Occupied | J460-01-2XT-614_RmOcc | J460-01-2XT-614_RmOcc |  | J6.06 |  |  |  | (UIO) DI1
2.1 | 17 | J460-01-1CP-604 | J460-01-2XT-615 | J460-01-2XT-615 - Room J6.07 - Occupied | J460-01-11-06-001 | (UIO) DI | PIR 360°, 24VDC, ON/OFF Delay | 24VDC | PVC | - | - | UNOCC | OCC | - | - | Calectro | PIR-TF-25-360 | NO | HM_Betec_PIR-TF-25-360 | PVC | UNOCC | OCC | - |  | J460-01-2XT-615 - Room J6.07 - Occupied | J460-01-2XT-615_RmOcc | J460-01-2XT-615_RmOcc |  | J6.07 |  |  |  | (UIO) DI1
1.0 | 11 | J460-01-1CP-612 | J460-01-2TT-615 | J460-01-2TT-615 - Room J6.04 - Temperature | J460-01-11-06-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR42-H | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-01-2TT-615 - Room J6.04 - Temperature | J460-02-2TT-615_RmTemp | J460-02-2TT-615_RmTemp |  | J6.04
1.0 | 12 | J460-01-1CP-612 | J460-01-2MT-615 | J460-01-2MT-615 - Room J6.04 - Humidity | J460-01-11-06-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR42-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-01-2MT-615 - Room J6.04 - Humidity | J460-02-2MT-615_RmHum | J460-02-2MT-615_RmHum |  | J6.04
2.1 | 13 | J460-01-1CP-612 | J460-01-2LA-601 | J460-01-2LA-601 - Room J6.04 - Water Leakage Detection | J460-01-11-06-001 | (UIO) DI | VEDOTEC Leakage detection PEK-SPS4 | 24VDC | PVC | - | - | ALARM | NORMAL | - | - | Jola | PEK-LS4 | NO | HM_Vedotec_PEK-LS4 | PVC | NORMAL | ALARM | - | INVERTED | J460-01-2LA-601 - Room J6.04 - Water Leakage Detection | J460-01-2LA-601_RmWtrLeakAlm | J460-01-2LA-601_RmWtrLeakAlm |  | J6.04 |  |  |  | (UIO) DI1
1.0 | 14 | J460-01-1CP-604 | J460-01-2TT-604 | J460-01-2TT-604 - Room J6.07 - Temperature | J460-01-11-06-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-01-2TT-604 - Room J6.07 - Temperature | J460-02-2TT-604_RmTemp | J460-02-2TT-604_RmTemp |  | J6.07
1.0 | 15 | J460-01-1CP-604 | J460-01-2MT-604 | J460-01-2MT-604 - Room J6.07 - Humidity | J460-01-11-06-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-01-2MT-604 - Room J6.07 - Humidity | J460-02-2MT-604_RmHum | J460-02-2MT-604_RmHum |  | J6.07
2.1 | 21 | J460-01-1CP-605 | J460-01-2XT-616 | J460-01-2XT-616 - Room J6.05 - Occupied | J460-01-11-06-001 | (UIO) DI | PIR 360°, 24VDC, ON/OFF Delay | 24VDC | PVC | - | - | UNOCC | OCC | - | - | Calectro | PIR-TF-25-360 | NO | HM_Betec_PIR-TF-25-360 | PVC | UNOCC | OCC | - |  | J460-01-2XT-616 - Room J6.05 - Occupied | J460-01-2XT-616_RmOcc | J460-01-2XT-616_RmOcc |  | J6.05 |  |  |  | (UIO) DI1
2.1 | 24 | J460-01-1CP-606 | J460-01-2XT-617 | J460-01-2XT-617 - Room J6.08 - Occupied | J460-01-11-06-002 | (UIO) DI | PIR 360°, 24VDC, ON/OFF Delay | 24VDC | PVC | - | - | UNOCC | OCC | - | - | Calectro | PIR-TF-25-360 | NO | HM_Betec_PIR-TF-25-360 | PVC | UNOCC | OCC | - |  | J460-01-2XT-617 - Room J6.08 - Occupied | J460-01-2XT-617_RmOcc | J460-01-2XT-617_RmOcc |  | J6.08 |  |  |  | (UIO) DI1
1.0 | 18 | J460-01-1CP-605 | J460-01-2TT-605 | J460-01-2TT-605 - Room J6.05 - Temperature | J460-01-11-06-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-01-2TT-605 - Room J6.05 - Temperature | J460-02-2TT-605_RmTemp | J460-02-2TT-605_RmTemp |  | J6.05
1.0 | 19 | J460-01-1CP-605 | J460-01-2MT-605 | J460-01-2MT-605 - Room J6.05 - Humidity | J460-01-11-06-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-01-2MT-605 - Room J6.05 - Humidity | J460-02-2MT-605_RmHum | J460-02-2MT-605_RmHum |  | J6.05
2.1 | 28 | J460-01-1CP-607 | J460-01-2XT-618 | J460-01-2XT-618 - Room J6.09 - Occupied | J460-01-11-06-002 | (UIO) DI | PIR 360°, 24VDC, ON/OFF Delay | 24VDC | PVC | - | - | UNOCC | OCC | - | - | Calectro | PIR-TF-25-360 | NO | HM_Betec_PIR-TF-25-360 | PVC | UNOCC | OCC | - |  | J460-01-2XT-618 - Room J6.09 - Occupied | J460-01-2XT-618_RmOcc | J460-01-2XT-618_RmOcc |  | J6.09 |  |  |  | (UIO) DI1
2.1 | 32 | J460-01-1CP-608 | J460-01-2XT-619 | J460-01-2XT-619 - Room J6.10 - Occupied | J460-01-11-06-002 | (UIO) DI | PIR 360°, 24VDC, ON/OFF Delay | 24VDC | PVC | - | - | UNOCC | OCC | - | - | Calectro | PIR-TF-25-360 | NO | HM_Betec_PIR-TF-25-360 | PVC | UNOCC | OCC | - |  | J460-01-2XT-619 - Room J6.10 - Occupied | J460-01-2XT-619_RmOcc | J460-01-2XT-619_RmOcc |  | J6.10 |  |  |  | (UIO) DI1
1 | 22 | J460-01-1CP-606 | J460-01-2TT-606 | J460-01-2TT-606 - Room J6.08 - Temperature | J460-01-11-06-002 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR42-H | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-01-2TT-606 - Room J6.08 - Temperature | J460-01-2TT-606_RmTemp | J460-01-2TT-606_RmTemp |  | J6.08
1.0 | 23 | J460-01-1CP-606 | J460-01-2MT-606 | J460-01-2MT-606 - Room J6.08 - Humidity | J460-01-11-06-002 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR42-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-01-2MT-606 - Room J6.08 - Humidity | J460-01-2MT-606_RmHum | J460-01-2MT-606_RmHum |  | J6.08
2.1 | 36 | J460-01-1CP-609 | J460-01-2XT-620 | J460-01-2XT-620 - Room J6.11 - Occupied | J460-01-11-06-002 | (UIO) DI | PIR 360°, 24VDC, ON/OFF Delay | 24VDC | PVC | - | - | UNOCC | OCC | - | - | Calectro | PIR-TF-25-360 | NO | HM_Betec_PIR-TF-25-360 | PVC | UNOCC | OCC | - |  | J460-01-2XT-620 - Room J6.11 - Occupied | J460-01-2XT-620_RmOcc | J460-01-2XT-620_RmOcc |  | J6.11 |  |  |  | (UIO) DI1
1.0 | 25 | J460-01-1CP-607 | J460-01-2TT-607 | J460-01-2TT-607 - Room J6.09 - Temperature | J460-01-11-06-002 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-01-2TT-607 - Room J6.09 - Temperature | J460-01-2TT-607_RmTemp | J460-01-2TT-607_RmTemp |  | J6.09
1.0 | 26 | J460-01-1CP-607 | J460-01-2MT-607 | J460-01-2MT-607 - Room J6.09 - Humidity | J460-01-11-06-002 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-01-2MT-607 - Room J6.09 - Humidity | J460-01-2MT-607_RmHum | J460-01-2MT-607_RmHum |  | J6.09
2.1 | 40 | J460-01-1CP-610 | J460-01-2XT-621 | J460-01-2XT-621 - Room J6.13 - Occupied | J460-01-11-06-002 | (UIO) DI | PIR 360°, 24VDC, ON/OFF Delay | 24VDC | PVC | - | - | UNOCC | OCC | - | - | Calectro | PIR-TF-25-360 | NO | HM_Betec_PIR-TF-25-360 | PVC | UNOCC | OCC | - |  | J460-01-2XT-621 - Room J6.13 - Occupied | J460-01-2XT-621_RmOcc | J460-01-2XT-621_RmOcc |  | J6.13 |  |  |  | (UIO) DI1
2.1 | 43 | J460-01-1CP-611 | J460-01-2XT-622 | J460-01-2XT-622 - Room J6.12 - Occupied | J460-01-11-06-002 | (UIO) DI | PIR 360°, 24VDC, ON/OFF Delay | 24VDC | PVC | - | - | UNOCC | OCC | - | - | Calectro | PIR-TF-25-360 | NO | HM_Betec_PIR-TF-25-360 | PVC | UNOCC | OCC | - |  | J460-01-2XT-622 - Room J6.12 - Occupied | J460-01-2XT-622_RmOcc | J460-01-2XT-622_RmOcc |  | J6.12 |  |  |  | (UIO) DI1
1.0 | 29 | J460-01-1CP-608 | J460-01-2TT-608 | J460-01-2TT-608 - Room J6.10 - Temperature | J460-01-11-06-002 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-01-2TT-608 - Room J6.10 - Temperature | J460-01-2TT-608_RmTemp | J460-01-2TT-608_RmTemp |  | J6.10
1.0 | 30 | J460-01-1CP-608 | J460-01-2MT-608 | J460-01-2MT-608 - Room J6.10 - Humidity | J460-01-11-06-002 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-01-2MT-608 - Room J6.10 - Humidity | J460-01-2MT-608_RmHum | J460-01-2MT-608_RmHum |  | J6.10
2.1 | 95 | J460-01-1CP-001 | J460-01-2XT-002 | J460-01-2XT-002 - Room J0.07 - Occupied | J460-01-11-01-001 | (UIO) DI | PIR 360°, 24VDC, ON/OFF Delay | 24VDC | PVC | - | - | UNOCC | OCC | - | - | Calectro | PIR-TF-25-360 | NO | HM_Betec_PIR-TF-25-360 | PVC | UNOCC | OCC | - |  | J460-01-2XT-002 - Room J0.07 - Occupied | J460-01-2XT-002_RmOcc | J460-01-2XT-002_RmOcc |  | J0.07 |  |  |  | (UIO) DI1
2.1 | 9 | J460-01-1CP-603 | J460-01-2XT-603 | J460-01-2XT-603 - Room J6.06 - CO2 Concentration | J460-01-11-06-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 2000 | ppm | ±30ppm + 3% Measured value | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 2000 | ppm |  | J460-01-2XT-603 - Room J6.06 - CO2 Concentration | J460-01-2XT-603_RmCO2 | J460-01-2XT-603_RmCO2 |  | J6.06
1.0 | 33 | J460-01-1CP-609 | J460-01-2TT-609 | J460-01-2TT-609 - Room J6.11 - Temperature | J460-01-11-06-002 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-01-2TT-609 - Room J6.11 - Temperature | J460-01-2TT-609_RmTemp | J460-01-2TT-609_RmTemp |  | J6.11
1.0 | 34 | J460-01-1CP-609 | J460-01-2MT-609 | J460-01-2MT-609 - Room J6.11 - Humidity | J460-01-11-06-002 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-01-2MT-609 - Room J6.11 - Humidity | J460-01-2MT-609_RmHum | J460-01-2MT-609_RmHum |  | J6.11
2.1 | 16 | J460-01-1CP-604 | J460-01-2XT-604 | J460-01-2XT-604 - Room J6.07 - CO2 Concentration | J460-01-11-06-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 2000 | ppm | ±30ppm + 3% Measured value | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 2000 | ppm |  | J460-01-2XT-604 - Room J6.07 - CO2 Concentration | J460-01-2XT-604_RmCO2 | J460-01-2XT-604_RmCO2 |  | J6.07
2.1 | 20 | J460-01-1CP-605 | J460-01-2XT-605 | J460-01-2XT-605 - Room J6.05 - CO2 Concentration | J460-01-11-06-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 2000 | ppm | ±30ppm + 3% Measured value | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 2000 | ppm |  | J460-01-2XT-605 - Room J6.05 - CO2 Concentration | J460-01-2XT-605_RmCO2 | J460-01-2XT-605_RmCO2 |  | J6.05
1.0 | 37 | J460-01-1CP-610 | J460-01-2TT-610 | J460-01-2TT-610 - Room J6.13 - Temperature | J460-01-11-06-002 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-01-2TT-610 - Room J6.13 - Temperature | J460-01-2TT-610_RmTemp | J460-01-2TT-610_RmTemp |  | J6.13
1.0 | 38 | J460-01-1CP-610 | J460-01-2MT-610 | J460-01-2MT-610 - Room J6.13 - Humidity | J460-01-11-06-002 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-01-2MT-610 - Room J6.13 - Humidity | J460-01-2MT-610_RmHum | J460-01-2MT-610_RmHum |  | J6.13
2.1 | 27 | J460-01-1CP-607 | J460-01-2XT-607 | J460-01-2XT-607 - Room J6.09 - CO2 Concentration | J460-01-11-06-002 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 2000 | ppm | ±30ppm + 3% Measured value | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 2000 | ppm |  | J460-01-2XT-607 - Room J6.09 - CO2 Concentration | J460-01-2XT-607_RmCO2 | J460-01-2XT-607_RmCO2 |  | J6.09
2.1 | 31 | J460-01-1CP-608 | J460-01-2XT-608 | J460-01-2XT-608 - Room J6.10 - CO2 Concentration | J460-01-11-06-002 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 2000 | ppm | ±30ppm + 3% Measured value | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 2000 | ppm |  | J460-01-2XT-608 - Room J6.10 - CO2 Concentration | J460-01-2XT-608_RmCO2 | J460-01-2XT-608_RmCO2 |  | J6.10
1.0 | 41 | J460-01-1CP-611 | J460-01-2TT-611 | J460-01-2TT-611 - Room J6.12 - Temperature | J460-01-11-06-002 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR42-H | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-01-2TT-611 - Room J6.12 - Temperature | J460-01-2TT-611_RmTemp | J460-01-2TT-611_RmTemp |  | J6.12
1.0 | 42 | J460-01-1CP-611 | J460-01-2MT-611 | J460-01-2MT-611 - Room J6.12 - Humidity | J460-01-11-06-002 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR42-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-01-2MT-611 - Room J6.12 - Humidity | J460-01-2MT-611_RmHum | J460-01-2MT-611_RmHum |  | J6.12
2.1 | 35 | J460-01-1CP-609 | J460-01-2XT-609 | J460-01-2XT-609 - Room J6.11 - CO2 Concentration | J460-01-11-06-002 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 2000 | ppm | ±30ppm + 3% Measured value | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 2000 | ppm |  | J460-01-2XT-609 - Room J6.11 - CO2 Concentration | J460-01-2XT-609_RmCO2 | J460-01-2XT-609_RmCO2 |  | J6.11
1.0 | 44 | J460-02-1CP-601 | J460-02-2TT-601 | J460-02-2TT-601 - Room J6.20 - Temperature | J460-02-11-06-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-02-2TT-601 - Room J6.20 - Temperature | J460-02-2TT-601_RmTemp | J460-02-2TT-601_RmTemp |  | J6.20
1.0 | 45 | J460-02-1CP-601 | J460-02-2MT-601 | J460-02-2MT-601 - Room J6.20 - Humidity | J460-02-11-06-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-601 - Room J6.20 - Humidity | J460-02-2MT-601_RmHum | J460-02-2MT-601_RmHum |  | J6.20
1.0 | 46 | J460-02-1CP-601 | J460-02-2TT-618 | J460-02-2TT-618 - Room J6.20 - J460-02-1ACU-601 - Supply Temperature | J460-02-11-06-001 | (UIO) AI | Rotronic HF432 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0.2°C @ 23°C | Rotronic | HF432-DB1XX1XX | NO | HM_Rotronic_HF4 | 4-20mA | 0 | 50 | °C |  | J460-02-2TT-618 - Room J6.20 - J460-02-1ACU-601 - Supply Temperature | J460-02-2TT-618_SupAirTemp | J460-02-2TT-618_SupAirTemp |  | J6.20 |  |  |  | (UIO) AI1
1.0 | 47 | J460-02-1CP-601 | J460-02-1ACU-601 | J460-02-2XA-618 - J460-02-1ACU-601 - Alarm | J460-02-11-06-001 | (UIO) DI | HYPOPOWER GEKO, GH12.UW04.SE0C2 | - | PVC | - | - | NORMAL | ALARM | - | - | Flaktgroup | HYPOPOWER GEKO, GH12.UW04.SE0C2 | NO |  | PVC | NORMAL | ALARM | - |  | J460-02-2XA-618 - J460-02-1ACU-601 - Alarm | J460-02-2XA-618_FCUAlm | J460-02-2XA-618_FCUAlm |  | J6.20 |  |  |  | (UIO) DI2
1.0 | 48 | J460-02-1CP-601 | J460-02-1ACU-601 | J460-02-2SC-618 - J460-02-1ACU-601 - Fan Speed | J460-02-11-06-001 | (UIO) AO | HYPOPOWER GEKO, GH12.UW04.SE0C2 | - | 0-10V | - | - | 0 | 100 | % | - | Flaktgroup | HYPOPOWER GEKO, GH12.UW04.SE0C2 | NO |  | 0-10V | 0 | 100 | % |  | J460-02-2SC-618 - J460-02-1ACU-601 - Fan Speed | J460-02-2SC-618_FCUSpd | J460-02-2SC-618_FCUSpd |  | J6.20 |  |  |  | (UIO) AO3
1.0 | 49 | J460-02-1CP-602 | J460-02-2TT-602 | J460-02-2TT-602 - Room J6.22 - Temperature | J460-02-11-06-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-02-2TT-602 - Room J6.22 - Temperature | J460-02-2TT-602_RmTemp | J460-02-2TT-602_RmTemp |  | J6.22
1.0 | 50 | J460-02-1CP-602 | J460-02-2MT-602 | J460-02-2MT-602 - Room J6.22 - Humidity | J460-02-11-06-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-602 - Room J6.22 - Humidity | J460-02-2MT-602_RmHum | J460-02-2MT-602_RmHum |  | J6.22
1.0 | 51 | J460-02-1CP-602 | J460-02-1ACU-602 | J460-02-2SC-625 - J460-02-1ACU-602 - Fan Speed | J460-02-11-06-001 | (UIO) AO | CASETTE GEKO DOUBLE, GCD1.UWW.SE5 | - | 0-10V | - | - | 0 | 100 | % | - | Flaktgroup | CASETTE GEKO DOUBLE, GCD1.UWW.SE5 | NO |  | 0-10V | 0 | 100 | % |  | J460-02-2SC-625 - J460-02-1ACU-602 - Fan Speed | J460-02-2SC-625_FCUSpd | J460-02-2SC-625_FCUSpd |  | J6.22 |  |  |  | (UIO) AO3
2 | 52 | J460-02-1CP-603 | J460-02-2TT-603 | J460-02-2TT-603 - Room J6.23 - Temperature | J460-02-11-06-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-02-2TT-603 - Room J6.23 - Temperature | J460-02-2TT-603_RmTemp | J460-02-2TT-603_RmTemp |  | J6.23
2 | 53 | J460-02-1CP-603 | J460-02-2MT-603 | J460-02-2MT-603 - Room J6.23 - Humidity | J460-02-11-06-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-603 - Room J6.23 - Humidity | J460-02-2MT-603_RmHum | J460-02-2MT-603_RmHum |  | J6.23
2.1 | 54 | J460-02-1CP-603 | J460-02-2TT-619 | J460-02-2TT-619 - Room J6.23 - J460-02-1ACU-603 Supply - Temperature | J460-02-11-06-001 | (UIO) AI | Rotronic HF432 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0.2°C @ 23°C | Rotronic | HF432-DB1XX1XX | NO | HM_Rotronic_HF4 | 4-20mA | 0 | 50 | °C |  | J460-02-2TT-619 - J460-02-1ACU-603 Supply - Temperature | J460-02-2TT-619_SupAirTemp | J460-02-2TT-619_SupAirTemp |  | J6.23 |  |  |  | (UIO) AI1
2 | 55 | J460-02-1CP-603 | J460-02-1ACU-603 | J460-02-2XA-619 - J460-02-1ACU-603 - Alarm | J460-02-11-06-001 | (UIO) DI | HYPOPOWER GEKO, GH22.UW03.SE0C2 | - | PVC | - | - | NORMAL | ALARM | - | - | Flaktgroup | HYPOPOWER GEKO, GH22.UW03.SE0C2 | NO |  | PVC | NORMAL | ALARM | - |  | J460-02-2XA-619 - J460-02-1ACU-603 - Alarm | J460-02-2XA-619_FCUAlm | J460-02-2XA-619_FCUAlm |  | J6.23 |  |  |  | (UIO) DI2
2 | 56 | J460-02-1CP-603 | J460-02-1ACU-603 | J460-02-2SC-619 - 460-02-1ACU-603 - Fan Speed | J460-02-11-06-001 | (UIO) AO | HYPOPOWER GEKO, GH22.UW03.SE0C2 | - | 0-10V | - | - | 0 | 100 | % | - | Flaktgroup | HYPOPOWER GEKO, GH22.UW03.SE0C2 | NO |  | 0-10V | 0 | 100 | % |  | J460-02-2SC-619 - 460-02-1ACU-603 - Fan Speed | J460-02-2SC-619_FCUSpd | J460-02-2SC-619_FCUSpd |  | J6.23 |  |  |  | (UIO) AO3
1.0 | 57 | J460-02-1CP-609 | J460-02-2TT-609 | J460-02-2TT-609 - Room J6.23 - Temperature | J460-02-11-06-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-02-2TT-609 - Room J6.23 - Temperature | J460-02-2TT-609_RmTemp | J460-02-2TT-609_RmTemp |  | J6.23
1.0 | 58 | J460-02-1CP-609 | J460-02-2MT-609 | J460-02-2MT-609 - Room J6.23 - Humidity | J460-02-11-06-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-609 - Room J6.23 - Humidity | J460-02-2MT-609_RmHum | J460-02-2MT-609_RmHum |  | J6.23
2.1 | 59 | J460-02-1CP-609 | J460-02-2TT-620 | J460-02-2TT-620 - Room J6.23 - J460-02-1ACU-604 - Supply Temperature | J460-02-11-06-001 | (UIO) AI | Rotronic HF432 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0.2°C @ 23°C | Rotronic | HF432-DB1XX1XX | NO | HM_Rotronic_HF4 | 4-20mA | 0 | 50 | °C |  | J460-02-2TT-620 - J460-02-1ACU-604 - Supply Temperature | J460-02-2TT-620_SupAirTemp | J460-02-2TT-620_SupAirTemp |  | J6.23 |  |  |  | (UIO) AI1
1.0 | 60 | J460-02-1CP-609 | J460-02-1ACU-604 | J460-02-2XA-620 - J460-02-1ACU-604 - Alarm | J460-02-11-06-001 | (UIO) DI | HYPOPOWER GEKO, GH22.UW04.SE0C2 | - | PVC | - | - | NORMAL | ALARM | - | - | Flaktgroup | HYPOPOWER GEKO, GH22.UW04.SE0C2 | NO |  | PVC | NORMAL | ALARM | - |  | J460-02-2XA-620 - J460-02-1ACU-604 - Alarm | J460-02-2XA-620_FCUAlm | J460-02-2XA-620_FCUAlm |  | J6.23 |  |  |  | (UIO) DI2
1.0 | 61 | J460-02-1CP-609 | J460-02-1ACU-604 | J460-02-2SC-620 - J460-02-1ACU-604 - Fan Speed | J460-02-11-06-001 | (UIO) AO | HYPOPOWER GEKO, GH22.UW04.SE0C2 | - | 0-10V | - | - | 0 | 100 | % | - | Flaktgroup | HYPOPOWER GEKO, GH22.UW04.SE0C2 | NO |  | 0-10V | 0 | 100 | % |  | J460-02-2SC-620 - J460-02-1ACU-604 - Fan Speed | J460-02-2SC-620_FCUSpd | J460-02-2SC-620_FCUSpd |  | J6.23 |  |  |  | (UIO) AO3
1.0 | 62 | J460-02-1CP-610 | J460-02-2TT-610 | J460-02-2TT-610 - Room J6.23 - Temperature | J460-02-11-06-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-02-2TT-610 - Room J6.23 - Temperature | J460-02-2TT-610_RmTemp | J460-02-2TT-610_RmTemp |  | J6.23
1.0 | 63 | J460-02-1CP-610 | J460-02-2MT-610 | J460-02-2MT-610 - Room J6.23 - Humidity | J460-02-11-06-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-610 - Room J6.23 - Humidity | J460-02-2MT-610_RmHum | J460-02-2MT-610_RmHum |  | J6.23
2.1 | 64 | J460-02-1CP-610 | J460-02-2TT-621 | J460-02-2TT-621 - Room J6.23 - J460-02-1ACU-605 - Supply Temperature | J460-02-11-06-001 | (UIO) AI | Rotronic HF432 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0.2°C @ 23°C | Rotronic | HF432-DB1XX1XX | NO | HM_Rotronic_HF4 | 4-20mA | 0 | 50 | °C |  | J460-02-2TT-621 - J460-02-1ACU-605 - Supply Temperature | J460-02-2TT-621_SupAirTemp | J460-02-2TT-621_SupAirTemp |  | J6.23 |  |  |  | (UIO) AI1
1.0 | 65 | J460-02-1CP-610 | J460-02-1ACU-605 | J460-02-2XA-621 - J460-02-1ACU-605 - Alarm | J460-02-11-06-001 | (UIO) DI | HYPOPOWER GEKO, GH12.UW03.SE0C2 | - | PVC | - | - | NORMAL | ALARM | - | - | Flaktgroup | HYPOPOWER GEKO, GH12.UW03.SE0C2 | NO |  | PVC | NORMAL | ALARM | - |  | J460-02-2XA-621 - J460-02-1ACU-605 - Alarm | J460-02-2XA-621_FCUAlm | J460-02-2XA-621_FCUAlm |  | J6.23 |  |  |  | (UIO) DI2
1.0 | 66 | J460-02-1CP-610 | J460-02-1ACU-605 | J460-02-2SC-621 - J460-02-1ACU-605 - Fan Speed | J460-02-11-06-001 | (UIO) AO | HYPOPOWER GEKO, GH12.UW03.SE0C2 | - | 0-10V | - | - | 0 | 100 | % | - | Flaktgroup | HYPOPOWER GEKO, GH12.UW03.SE0C2 | NO |  | 0-10V | 0 | 100 | % |  | J460-02-2SC-621 - J460-02-1ACU-605 - Fan Speed | J460-02-2SC-621_FCUSpd | J460-02-2SC-621_FCUSpd |  | J6.23 |  |  |  | (UIO) AO3
1.0 | 67 | J460-02-1CP-604 | J460-02-2TT-604 | J460-02-2TT-604 - Room J6.24 - Temperature | J460-02-11-06-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-02-2TT-604 - Room J6.24 - Temperature | J460-02-2TT-604_RmTemp | J460-02-2TT-604_RmTemp |  | J6.24
1.0 | 68 | J460-02-1CP-604 | J460-02-2MT-604 | J460-02-2MT-604 - Room J6.24 - Humidity | J460-02-11-06-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-604 - Room J6.24 - Humidity | J460-02-2MT-604_RmHum | J460-02-2MT-604_RmHum |  | J6.24
2.1 | 69 | J460-02-1CP-604 | J460-02-2TT-622 | J460-02-2TT-622 - Room J6.24 - J460-02-1ACU-606 - Supply Temperature | J460-02-11-06-001 | (UIO) AI | Rotronic HF432 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0.2°C @ 23°C | Rotronic | HF432-DB1XX1XX | NO | HM_Rotronic_HF4 | 4-20mA | 0 | 50 | °C |  | J460-02-2TT-622 - J460-02-1ACU-606 - Supply Temperature | J460-02-2TT-622_SupAirTemp | J460-02-2TT-622_SupAirTemp |  | J6.24 |  |  |  | (UIO) AI1
1.0 | 70 | J460-02-1CP-604 | J460-02-1ACU-606 | J460-02-2XA-622 - J460-02-1ACU-606 - Alarm | J460-02-11-06-001 | (UIO) DI | HYPOPOWER GEKO, GH22.UW04.SE0C2 | - | PVC | - | - | NORMAL | ALARM | - | - | Flaktgroup | HYPOPOWER GEKO, GH22.UW04.SE0C2 | NO |  | PVC | NORMAL | ALARM | - |  | J460-02-2XA-622 - J460-02-1ACU-606 - Alarm | J460-02-2XA-622_FCUAlm | J460-02-2XA-622_FCUAlm |  | J6.24 |  |  |  | (UIO) DI2
1.0 | 71 | J460-02-1CP-604 | J460-02-1ACU-606 | J460-02-2SC-622 - J460-02-1ACU-606 - Fan Speed | J460-02-11-06-001 | (UIO) AO | HYPOPOWER GEKO, GH22.UW04.SE0C2 | - | 0-10V | - | - | 0 | 100 | % | - | Flaktgroup | HYPOPOWER GEKO, GH22.UW04.SE0C2 | NO |  | 0-10V | 0 | 100 | % |  | J460-02-2SC-622 - J460-02-1ACU-606 - Fan Speed | J460-02-2SC-622_FCUSpd | J460-02-2SC-622_FCUSpd |  | J6.24 |  |  |  | (UIO) AO3
2 | 72 | J460-02-1CP-611 | J460-02-2TT-611 | J460-02-2TT-611 - Room J6.24 - Temperature | J460-02-11-06-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-02-2TT-611 - Room J6.24 - Temperature | J460-02-2TT-611_RmTemp | J460-02-2TT-611_RmTemp |  | J6.24
2 | 73 | J460-02-1CP-611 | J460-02-2MT-611 | J460-02-2MT-611 - Room J6.24 - Humidity | J460-02-11-06-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-611 - Room J6.24 - Humidity | J460-02-2MT-611_RmHum | J460-02-2MT-611_RmHum |  | J6.24
2.1 | 74 | J460-02-1CP-611 | J460-02-2TT-623 | J460-02-2TT-623 - Room J6.24 - J460-02-1ACU-607 - Supply Temperature | J460-02-11-06-001 | (UIO) AI | Rotronic HF432 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0.2°C @ 23°C | Rotronic | HF432-DB1XX1XX | NO | HM_Rotronic_HF4 | 4-20mA | 0 | 50 | °C |  | J460-02-2TT-623 - J460-02-1ACU-607 - Supply Temperature | J460-02-2TT-623_SupAirTemp | J460-02-2TT-623_SupAirTemp |  | J6.24 |  |  |  | (UIO) AI1
2 | 75 | J460-02-1CP-611 | J460-02-1ACU-607 | J460-02-2XA-623 - J460-02-1ACU-607 - Alarm | J460-02-11-06-001 | (UIO) DI | HYPOPOWER GEKO, GH22.UW03.SE0C2 | - | PVC | - | - | NORMAL | ALARM | - | - | Flaktgroup | HYPOPOWER GEKO, GH22.UW03.SE0C2 | NO |  | PVC | NORMAL | ALARM | - |  | J460-02-2XA-623 - J460-02-1ACU-607 - Alarm | J460-02-2XA-623_FCUAlm | J460-02-2XA-623_FCUAlm |  | J6.24 |  |  |  | (UIO) DI2
2 | 76 | J460-02-1CP-611 | J460-02-1ACU-607 | J460-02-2SC-623 - J460-02-1ACU-607 - Fan Speed | J460-02-11-06-001 | (UIO) AO | HYPOPOWER GEKO, GH22.UW03.SE0C2 | - | 0-10V | - | - | 0 | 100 | % | - | Flaktgroup | HYPOPOWER GEKO, GH22.UW03.SE0C2 | NO |  | 0-10V | 0 | 100 | % |  | J460-02-2SC-623 - J460-02-1ACU-607 - Fan Speed | J460-02-2SC-623_FCUSpd | J460-02-2SC-623_FCUSpd |  | J6.24 |  |  |  | (UIO) AO3
1.0 | 77 | J460-02-1CP-612 | J460-02-2TT-612 | J460-02-2TT-612 - Room J6.20 - Temperature | J460-02-11-06-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-02-2TT-612 - Room J6.20 - Temperature | J460-02-2TT-612_RmTemp | J460-02-2TT-612_RmTemp |  | J6.20
1.0 | 78 | J460-02-1CP-612 | J460-02-2MT-612 | J460-02-2MT-612 - Room J6.20 - Humidity | J460-02-11-06-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-612 - Room J6.20 - Humidity | J460-02-2MT-612_RmHum | J460-02-2MT-612_RmHum |  | J6.20
2.1 | 79 | J460-02-1CP-612 | J460-02-2TT-624 | J460-02-2TT-624 - Room J6.20 - J460-02-1ACU-609 - Supply Temperature | J460-02-11-06-002 | (UIO) AI | Rotronic HF432 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0.2°C @ 23°C | Rotronic | HF432-DB1XX1XX | NO | HM_Rotronic_HF4 | 4-20mA | 0 | 50 | °C |  | J460-02-2TT-624 - J460-02-1ACU-609 - Supply Temperature | J460-02-2TT-624_SupAirTemp | J460-02-2TT-624_SupAirTemp |  | J6.20 |  |  |  | (UIO) AI1
1.0 | 80 | J460-02-1CP-612 | J460-02-1ACU-609 | J460-02-2XA-624 - J460-02-1ACU-609 - Alarm | J460-02-11-06-002 | (UIO) DI | HYPOPOWER GEKO, GH12.UW04.SE0C2 | - | PVC | - | - | NORMAL | ALARM | - | - | Flaktgroup | HYPOPOWER GEKO, GH12.UW04.SE0C2 | NO |  | PVC | NORMAL | ALARM | - |  | J460-02-2XA-624 - J460-02-1ACU-609 - Alarm | J460-02-2XA-624_FCUAlm | J460-02-2XA-624_FCUAlm |  | J6.20 |  |  |  | (UIO) DI2
1.0 | 81 | J460-02-1CP-612 | J460-02-1ACU-609 | J460-02-2SC-624 - J460-02-1ACU-609 - Fan Speed | J460-02-11-06-002 | (UIO) AO | HYPOPOWER GEKO, GH12.UW04.SE0C2 | - | 0-10V | - | - | 0 | 100 | % | - | Flaktgroup | HYPOPOWER GEKO, GH12.UW04.SE0C2 | NO |  | 0-10V | 0 | 100 | % |  | J460-02-2SC-624 - J460-02-1ACU-609 - Fan Speed | J460-02-2SC-624_FCUSpd | J460-02-2SC-624_FCUSpd |  | J6.20 |  |  |  | (UIO) AO3
1.0 | 82 | J460-02-1CP-605 | J460-02-2TT-605 | J460-02-2TT-605 - Room J6.17 - Temperature | J460-02-11-06-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-02-2TT-605 - Room J6.17 - Temperature | J460-02-2TT-605_RmTemp | J460-02-2TT-605_RmTemp |  | J6.17
1.0 | 83 | J460-02-1CP-605 | J460-02-2MT-605 | J460-02-2MT-605 - Room J6.17 - Humidity | J460-02-11-06-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-605 - Room J6.17 - Humidity | J460-02-2MT-605_RmHum | J460-02-2MT-605_RmHum |  | J6.17
1.0 | 84 | J460-02-1CP-613 | J460-02-2TT-613 | J460-02-2TT-613 - Room J6.17 - Temperature | J460-02-11-06-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-02-2TT-613 - Room J6.17 - Temperature | J460-02-2TT-613_RmTemp | J460-02-2TT-613_RmTemp |  | J6.17
1.0 | 85 | J460-02-1CP-613 | J460-02-2MT-613 | J460-02-2MT-613 - Room J6.17 - Humidity | J460-02-11-06-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-613 - Room J6.17 - Humidity | J460-02-2MT-613_RmHum | J460-02-2MT-613_RmHum |  | J6.17
1.0 | 86 | J460-02-1CP-614 | J460-02-2TT-614 | J460-02-2TT-614 - Room J6.17 - Temperature | J460-02-11-06-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-02-2TT-614 - Room J6.17 - Temperature | J460-02-2TT-614_RmTemp | J460-02-2TT-614_RmTemp |  | J6.17
1.0 | 87 | J460-02-1CP-614 | J460-02-2MT-614 | J460-02-2MT-614 - Room J6.17 - Humidity | J460-02-11-06-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-614 - Room J6.17 - Humidity | J460-02-2MT-614_RmHum | J460-02-2MT-614_RmHum |  | J6.17
1.0 | 88 | J460-02-1CP-606 | J460-02-2TT-606 | J460-02-2TT-606 - Room J6.14 - Temperature | J460-02-11-06-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-02-2TT-606 - Room J6.14 - Temperature | J460-02-2TT-606_RmTemp | J460-02-2TT-606_RmTemp |  | J6.14
1.0 | 89 | J460-02-1CP-606 | J460-02-2MT-606 | J460-02-2MT-606 - Room J6.14 - Humidity | J460-02-11-06-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-606 - Room J6.14 - Humidity | J460-02-2MT-606_RmHum | J460-02-2MT-606_RmHum |  | J6.14
1.0 | 90 | J460-02-1CP-615 | J460-02-2TT-615 | J460-02-2TT-615 - Room J6.14 - Temperature | J460-02-11-06-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 50 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 50 | °C |  | J460-02-2TT-615 - Room J6.14 - Temperature | J460-02-2TT-615_RmTemp | J460-02-2TT-615_RmTemp |  | J6.14
1.0 | 91 | J460-02-1CP-615 | J460-02-2MT-615 | J460-02-2MT-615 - Room J6.14 - Humidity | J460-02-11-06-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, No Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-615 - Room J6.14 - Humidity | J460-02-2MT-615_RmHum | J460-02-2MT-615_RmHum |  | J6.14
1.0 | 92 | J460-01-1CP-001 | J460-01-2TT-001 | J460-01-2TT-001 - Room J0.07 - Temperature | J460-01-11-01-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 52 | °C | ±0.2°C @25°C | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 52 | °C |  | J460-01-2TT-001 - Room J0.07 - Temperature | J460-01-2TT-001_RmTemp | J460-01-2TT-001_RmTemp | - | J0.07
1.0 | 93 | J460-01-1CP-001 | J460-01-2MT-001 | J460-01-2MT-001 - Room J0.07 - Humidity | J460-01-11-01-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-01-2MT-001 - Room J0.07 - Humidity | J460-01-2MT-001_RmHum | J460-01-2MT-001_RmHum | - | J0.07
2.1 | 39 | J460-01-1CP-610 | J460-01-2XT-610 | J460-01-2XT-610 - Room J6.13 - CO2 Concentration | J460-01-11-06-002 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 2000 | ppm | ±30ppm + 3% Measured value | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 2000 | ppm |  | J460-01-2XT-610 - Room J6.13 - CO2 Concentration | J460-01-2XT-610_RmCO2 | J460-01-2XT-610_RmCO2 |  | J6.13
2.1 | 94 | J460-01-1CP-001 | J460-01-2XT-001 | J460-01-2XT-001 - Room J0.07 - CO2 Concentration | J460-01-11-01-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 2000 | ppm | ±30ppm + 3% Measured value | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 2000 | ppm |  | J460-01-2XT-001 - Room J0.07 - CO2 Concentration | J460-01-2XT-001_RmCO2 | J460-01-2XT-001_RmCO2 | - | J0.07
Note on E56: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Added room reference Room J6.23
Note on E61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Added room reference Room J6.23
Note on E66: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Added room reference Room J6.23
Note on E71: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Added room reference Room J6.24
Note on E76: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Added room reference Room J6.24
Note on E81: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Added room reference Room J6.20

## Doc Revision History
*** END OF DOCUMENT ***
Document Revision History
Version Number | Section | Description of Change | Justification of Change
1.0 | NA | New document | CC#2249686
2 | NA | Corrected CP numbers | CC#2249686
2.1 | NA | Corrected ACU's and Added Room references | CC#2249686

## Vault Data (hidden)
Vault Data |  | Vault Data
Cell Tokens | Value | (Default/Odd) Frontsheet Header | (Default/Odd) Frontsheet Header Configure Token
${vault:major} | 1 | Left Header
${vault:minor} | 4 | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
${vault:subtype__v} | Design | Right Header
${vault:document_owning_facility__vr.name__v} | Leiden JBV | (Default/Odd) Frontsheet Footer | (Default/Odd) Frontsheet Footer Configure Token
${vault:document_owning_facility__vr.id} | 00F000000003361 | Left Footer
${vault:owning_facility__v} | Leiden JBV | Central Footer
${vault:title__v} | J270-06 BMS 6th Floor Room control Instrument List J-Building | Right Footer
${vault:type__v} | Technical Document | (Even) Frontsheet Header | (Even) Frontsheet Header Configure Token
${vault:document_facility__vr.name__v} | Leiden JBV | Left Header
${vault:document_facility__vr.id} | 00F000000003361 | Central Header
${vault:version} | 2 | Right Header
${vault:document_impacted_facilities__vr.name__v} | Leiden JBV | (Even) Frontsheet Footer | (Even) Frontsheet Footer Configure Token
${vault:document_impacted_facilities__vr.id} | 00F000000003361 | Left Footer
Central Footer
Right Footer
|  | (First Page) Frontsheet Header | (First Page) Frontsheet Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) Frontsheet Footer | (First Page) Frontsheet Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) Floormanager Header | (Default/Odd) Floormanager Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) Floormanager Footer | (Default/Odd) Floormanager Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) Floormanager Header | (Even) Floormanager Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) Floormanager Footer | (Even) Floormanager Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) Floormanager Header | (First Page) Floormanager Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) Floormanager Footer | (First Page) Floormanager Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) RackPositioning Header | (Default/Odd) RackPositioning Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) RackPositioning Footer | (Default/Odd) RackPositioning Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) RackPositioning Header | (Even) RackPositioning Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) RackPositioning Footer | (Even) RackPositioning Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) RackPositioning Header | (First Page) RackPositioning Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) RackPositioning Footer | (First Page) RackPositioning Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) RoomControllers Header | (Default/Odd) RoomControllers Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) RoomControllers Footer | (Default/Odd) RoomControllers Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) RoomControllers Header | (Even) RoomControllers Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) RoomControllers Footer | (Even) RoomControllers Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) RoomControllers Header | (First Page) RoomControllers Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) RoomControllers Footer | (First Page) RoomControllers Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) Doc Revision History Header | (Default/Odd) Doc Revision History Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) Doc Revision History Footer | (Default/Odd) Doc Revision History Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) Doc Revision History Header | (Even) Doc Revision History Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) Doc Revision History Footer | (Even) Doc Revision History Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) Doc Revision History Header | (First Page) Doc Revision History Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) Doc Revision History Footer | (First Page) Doc Revision History Footer Configure Token
Left Footer
Central Footer
Right Footer