## Frontsheet
Janssen Kappa Pollux QC
BMS 6th Floor Office And Lab Room Control Alarm & Parameter List
Document Number: J270-06-APL-001
BMS Alarm & Parameter List
Version: 2.1
BMS Panel : J270-06-1PNL-001 Controller:J270-06-3PLC-001, J270-06-3PLC-002

## J270-06
Rev Nr | Nr | Outstation | Device Tag | Function | Point Description | EBI Tag | JACE Tag | Range (Low) / State 0 | Range (High) / State 1 | State 2 | State 3 | State 4 | State 5 | State 6 | State 7 | State 8 | State 9 | State 16 | State 32 | State 64 | State 128 | State 8192 | State 16384 | State 32768 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
1.0 | 1 | J270-06-1PNL-001 | J270-06-2XA-001 | Measurement | J270-06-2XA-001 - J270-06-1PNL-001 - 230VAC Thermal Fault Signal | J270-06-2XA-001_230VACThemFlt | J270-06-2XA-001_230VACThemFlt | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2 | J270-06-1PNL-001 | J270-06-2XA-001 | Alarm | J270-06-2XA-001 - J270-06-1PNL-001 - 230VAC Thermal Fault Signal Alarm | J270-06-2XA-001_230VACThemFlt_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J270-06-2XA-001_230VACThemFlt_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 3 | J270-06-1PNL-001 | J270-06-2XA-002 | Measurement | J270-06-2XA-002 - J270-06-1PNL-001 - 24VDC Thermal Fault Signal | J270-06-2XA-002_24VDCThemFlt | J270-06-2XA-002_24VDCThemFlt | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 4 | J270-06-1PNL-001 | J270-06-2XA-002 | Alarm | J270-06-2XA-002 - J270-06-1PNL-001 - 24VDC Thermal Fault Signal Alarm | J270-06-2XA-002_24VDCThemFlt_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J270-06-2XA-002_24VDCThemFlt_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 5 | J270-06-1PNL-001 | J270-06-2XA-004 | Measurement | J270-06-2XA-004 - J270-06-1PNL-001 - Surge Voltage Arrester Signal | J270-06-2XA-004_SurgeVoltArr | J270-06-2XA-004_SurgeVoltArr | NORMAL | FAULT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 6 | J270-06-1PNL-001 | J270-06-2XA-004 | Alarm | J270-06-2XA-004 - J270-06-1PNL-001 - Surge Voltage Arrester Signal Alarm | J270-06-2XA-004_SurgeVoltArr_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J270-06-2XA-004_SurgeVoltArr_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 7 | J270-06-1PNL-001 | J270-06-2XA-005 | Measurement | J270-06-2XA-005 - J270-06-1PNL-001 - Common Fire Alarm | J270-06-2XA-005_ExtFireCom | J270-06-2XA-005_ExtFireCom | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 8 | J270-06-1PNL-001 | J270-06-2XA-005 | Alarm | J270-06-2XA-005 - J270-06-1PNL-001 - Common Fire Alarm | J270-06-2XA-005_ExtFireCom_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J270-06-2XA-005_ExtFireCom_Alm | 1 | M | - | bar: State 2 to State 64
1.0 | 9 | J270-06-1PNL-001 | J460-01-2TT-612 | Measurement | J460-01-2TT-612 - Chilled Water - Supply Temperature | J460-01-2TT-612_ChlWtrSupTemp | J460-01-2TT-612_ChlWtrSupTemp | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 10 | J270-06-1PNL-001 | J460-01-2TT-612 | Measurement | J460-01-2TT-612 - Chilled Water - Supply Temperature Field | J460-01-2TT-612_ChlWtrSupTemp_Field | J460-01-2TT-612_ChlWtrSupTemp_Field | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 11 | J270-06-1PNL-001 | J460-01-2TT-612 | Alarm | J460-01-2TT-612 - Chilled Water - Supply Temperature High Alarm | J460-01-2TT-612_ChlWtrSupTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-612_ChlWtrSupTempHiAlm | 2 | Y | - | bar: State 2 to State 64
2.1 | 12 | J270-06-1PNL-001 | J460-01-2TT-612 | Setting | J460-01-2TT-612 - Chilled Water - Supply Temperature | J460-01-2TT-612_ChlWtrSupTemp_HASP | J460-01-2TT-612_ChlWtrSupTemp_HASP | - | 16 | [11 empty] | - | - | - | - | - | 0.5 | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 13 | J270-06-1PNL-001 | J460-01-2TT-612 | Alarm | J460-01-2TT-612 - Chilled Water - Supply Temperature Low Alarm | J460-01-2TT-612_ChlWtrSupTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-612_ChlWtrSupTempLoAlm | 2 | Y | - | bar: State 2 to State 64
2.1 | 14 | J270-06-1PNL-001 | J460-01-2TT-612 | Setting | J460-01-2TT-612 - Chilled Water - Supply Temperature | J460-01-2TT-612_ChlWtrSupTemp_LASP | J460-01-2TT-612_ChlWtrSupTemp_LASP | 6 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 15 | J270-06-1PNL-001 | J460-01-2TT-612 | Setting | J460-01-2TT-612 - Chilled Water - Supply Temperature Calibration Mode Selection | J460-01-2TT-612_ChlWtrSupTempCalModeSel | J460-01-2TT-612_ChlWtrSupTempCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 16 | J270-06-1PNL-001 | J460-01-2TT-612 | Alarm | J460-01-2TT-612 - Chilled Water - Supply Temperature Calibration Still Active Alarm | J460-01-2TT-612_ChlWtrSupTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-612_ChlWtrSupTempCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 17 | J270-06-1PNL-001 | J460-01-2TT-612 | Setting | J460-01-2TT-612 - Chilled Water - Supply Temperature Setpoint | J460-01-2TT-612_ChlWtrSupTempSetpoint | J460-01-2TT-612_ChlWtrSupTempSetpoint | 16 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 18 | J270-06-1PNL-001 | N/A | Calculated | BMS Sixth Floor Office Room Dew Point Temperature Setpoint | J460-01-2TT-612_OffcDewPtTempSetpoint | J460-01-2TT-612_OffcDewPtTempSetpoint | Calculated | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 19 | J270-06-1PNL-001 | N/A | Setting | BMS Sixth Floor Office Room Dew Point Temperature Setpoint Offset | J460-01-2TT-612_OffcDewPtTempSPOffset | J460-01-2TT-612_OffcDewPtTempSPOffset | 1 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 20 | J270-06-1PNL-001 | J460-01-2TT-612 | Setting | J460-01-2TT-612 - Chilled Water - Supply Temperature Proportional Band | J460-01-2TT-612_ChlWtrSupTemp_Set_P | J460-01-2TT-612_ChlWtrSupTemp_Set_P | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 21 | J270-06-1PNL-001 | J460-01-2TT-612 | Setting | J460-01-2TT-612 - Chilled Water - Supply Temperature Integral Time | J460-01-2TT-612_ChlWtrSupTemp_Set_I | J460-01-2TT-612_ChlWtrSupTemp_Set_I | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 22 | J270-06-1PNL-001 | J460-01-2TT-612 | Setting | J460-01-2TT-612 - Chilled Water - Supply Temperature Derivative Time | J460-01-2TT-612_ChlWtrSupTemp_Set_D | J460-01-2TT-612_ChlWtrSupTemp_Set_D | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 23 | J270-06-1PNL-001 | J460-01-2TT-613 | Measurement | J460-01-2TT-613 - Chilled Water - Return Temperature | J460-01-2TT-613_ChlWtrRetTemp | J460-01-2TT-613_ChlWtrRetTemp | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 24 | J270-06-1PNL-001 | J460-01-2TT-613 | Measurement | J460-01-2TT-613 - Chilled Water - Return Temperature Field | J460-01-2TT-613_ChlWtrRetTemp_Field | J460-01-2TT-613_ChlWtrRetTemp_Field | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 25 | J270-06-1PNL-001 | J460-01-2TT-613 | Alarm | J460-01-2TT-613 - Chilled Water - Return Temperature High Alarm | J460-01-2TT-613_ChlWtrRetTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-613_ChlWtrRetTempHiAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 26 | J270-06-1PNL-001 | J460-01-2TT-613 | Setting | J460-01-2TT-613 - Chilled Water - Return Temperature | J460-01-2TT-613_ChlWtrRetTemp_HASP | J460-01-2TT-613_ChlWtrRetTemp_HASP | - | 18.5 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 3 to State 64
1.0 | 27 | J270-06-1PNL-001 | J460-01-2TT-613 | Alarm | J460-01-2TT-613 - Chilled Water - Return Temperature Low Alarm | J460-01-2TT-613_ChlWtrRetTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-613_ChlWtrRetTempLoAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 28 | J270-06-1PNL-001 | J460-01-2TT-613 | Setting | J460-01-2TT-613 - Chilled Water - Return Temperature | J460-01-2TT-613_ChlWtrRetTemp_LASP | J460-01-2TT-613_ChlWtrRetTemp_LASP | 12 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 29 | J270-06-1PNL-001 | J460-01-2TT-613 | Setting | J460-01-2TT-613 - Chilled Water - Return Temperature Calibration Mode Selection | J460-01-2TT-613_ChlWtrRetTempCalModeSel | J460-01-2TT-613_ChlWtrRetTempCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 30 | J270-06-1PNL-001 | J460-01-2TT-613 | Alarm | J460-01-2TT-613 - Chilled Water - Return Temperature Calibration Still Active Alarm | J460-01-2TT-613_ChlWtrRetTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-613_ChlWtrRetTempCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 31 | J270-06-1PNL-001 | J460-01-2FCV-643 | Alarm | J460-01-2FCV-643 - Chilled Water Valve - Controller Communication Failure Alarm | J460-01-2FCV-643_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-643_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 32 | J270-06-1PNL-001 | J460-01-2FCV-643 | Measurement | J460-01-2FCV-643 - Chilled Water Valve - Forced Position | J460-01-2FCV-643_ForcePos | J460-01-2FCV-643_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 33 | J270-06-1PNL-001 | J460-01-2FCV-643 | Setting | J460-01-2FCV-643 - Chilled Water Valve - Forced Calibration | J460-01-2FCV-643_ForceCal | J460-01-2FCV-643_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 34 | J270-06-1PNL-001 | J460-01-2FCV-643 | Measurement | J460-01-2FCV-643 - Chilled Water Valve - Status | J460-01-2FCV-643_MotState | J460-01-2FCV-643_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 35 | J270-06-1PNL-001 | J460-01-2FCV-643 | Measurement | J460-01-2FCV-643 - Chilled Water Valve - Actual SP | J460-01-2FCV-643_ActSP | J460-01-2FCV-643_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 36 | J270-06-1PNL-001 | J460-01-2FCV-643 | Setting | J460-01-2FCV-643 - Chilled Water Valve - SP | J460-01-2FCV-643_SP | J460-01-2FCV-643_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 37 | J270-06-1PNL-001 | J460-01-2FCV-643 | Alarm | J460-01-2FCV-643 - Chilled Water Valve - Controller Fail to Open Alarm | J460-01-2FCV-643_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-643_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 38 | J270-06-1PNL-001 | J460-01-2FCV-643 | Alarm | J460-01-2FCV-643 - Chilled Water Valve - Controller Fail to Close Alarm | J460-01-2FCV-643_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-643_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 39 | J270-06-1PNL-001 | J460-01-2FCV-643 | Measurement | J460-01-2FCV-643 - Chilled Water Valve - Error Code | J460-01-2FCV-643_Err | J460-01-2FCV-643_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 40 | J270-06-1PNL-001 | J460-01-1PMP-601 | Alarm | J460-01-1PMP-601 - Chilled Water Circulation Pump - Controller Communication Failure Alarm | J460-01-1PMP-601_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1PMP-601_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 41 | J270-06-1PNL-001 | J460-01-1PMP-601 | Measurement | J460-01-1PMP-601 - Chilled Water Circulation Pump - Error Code | J460-01-1PMP-601_ErrCode | J460-01-1PMP-601_ErrCode | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 42 | J270-06-1PNL-001 | J460-01-1PMP-601 | Measurement | J460-01-1PMP-601 - Chilled Water Circulation Pump - Speed | J460-01-1PMP-601_Spd | J460-01-1PMP-601_Spd | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | rpm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 43 | J270-06-1PNL-001 | J460-01-1PMP-601 | Measurement | J460-01-1PMP-601 - Chilled Water Circulation Pump - Frequency | J460-01-1PMP-601_Frq | J460-01-1PMP-601_Frq | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 44 | J270-06-1PNL-001 | J460-01-1PMP-601 | Measurement | J460-01-1PMP-601 - Chilled Water Circulation Pump - Motor Current | J460-01-1PMP-601_MtrCur | J460-01-1PMP-601_MtrCur | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 45 | J270-06-1PNL-001 | J460-01-1PMP-601 | Measurement | J460-01-1PMP-601 - Chilled Water Circulation Pump - DC Link Voltage | J460-01-1PMP-601_DCVolt | J460-01-1PMP-601_DCVolt | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 46 | J270-06-1PNL-001 | J460-01-1PMP-601 | Measurement | J460-01-1PMP-601 - Chilled Water Circulation Pump - Power | J460-01-1PMP-601_Pwr | J460-01-1PMP-601_Pwr | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | W | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 47 | J270-06-1PNL-001 | J460-01-1PMP-601 | Measurement | J460-01-1PMP-601 - Chilled Water Circulation Pump - Run Time | J460-01-1PMP-601_RunTime | J460-01-1PMP-601_RunTime | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 48 | J270-06-1PNL-001 | J460-01-1PMP-601 | Measurement | J460-01-1PMP-601 - Chilled Water Circulation Pump - Load Percentage | J460-01-1PMP-601_LdPerc | J460-01-1PMP-601_LdPerc | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 49 | J270-06-1PNL-001 | J460-01-1PMP-601 | Measurement | J460-01-1PMP-601 - Chilled Water Circulation Pump - Control Source | J460-01-1PMP-601_CntSrc | J460-01-1PMP-601_CntSrc | LOCCNT | BUSCNT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 50 | J270-06-1PNL-001 | J460-01-1PMP-601 | Measurement | J460-01-1PMP-601 - Chilled Water Circulation Pump - Rotation Status | J460-01-1PMP-601_Rot | J460-01-1PMP-601_Rot | NOROT | ROT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 51 | J270-06-1PNL-001 | J460-01-1PMP-601 | Measurement | J460-01-1PMP-601 - Chilled Water Circulation Pump - Actual Operation Mode | J460-01-1PMP-601_ActOpMode | J460-01-1PMP-601_ActOpMode | - | START | STOP | MINIMUM | MAXIMUM | USERDEF | LOCMODE | EMGMODE | HANDMODE | UNKNOWN | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 52 | J270-06-1PNL-001 | J460-01-1PMP-601 | Measurement | J460-01-1PMP-601 - Chilled Water Circulation Pump - Operation Mode | J460-01-1PMP-601_OpMode | J460-01-1PMP-601_OpMode | - | START | STOP | MINIMUM | MAXIMUM | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1.0 | 53 | J270-06-1PNL-001 | J460-01-1PMP-601 | Measurement | J460-01-2XS-601 - Chilled Water Circulation Pump J460-01-1PMP-601 - Enable | J460-01-2XS-601_ChlWtrCirPmpEna | J460-01-2XS-601_ChlWtrCirPmpEna | DISABLE | ENABLE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 54 | J270-06-1PNL-001 | J460-01-1PMP-601 | Measurement | J460-01-2SC-601 - Chilled Water Circulation Pump J460-01-1PMP-601 - Control Signal | J460-01-2SC-601_ChlWtrCirPmpCntr | J460-01-2SC-601_ChlWtrCirPmpCntr | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 55 | J270-06-1PNL-001 | J460-01-1PMP-601 | Measurement | J460-01-2XA-601 - Chilled Water Circulation Pump J460-01-1PMP-601 - Alarm | J460-01-2XA-601_ChlWtrCirPmpAlm | R420-01-2XA-601_ChlWtrCirPmpAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 56 | J270-06-1PNL-001 | J460-01-1PMP-601 | Alarm | J460-01-2XA-601 - Chilled Water Circulation Pump J460-01-1PMP-601 - Alarm | J460-01-2XA-601_ChlWtrCirPmpAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2XA-601_ChlWtrCirPmpAlm_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 57 | J270-06-1PNL-001 | J460-01-1PMP-601 | Measurement | J460-01-2SS-601 - Chilled Water Circulation Pump J460-01-1PMP-601 - Status | J460-01-2SS-601_ChlWtrCirPmpSts | J460-01-2SS-601_ChlWtrCirPmpSts | STOP | RUN | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 58 | J270-06-1PNL-001 | J460-01-1PMP-601 | Alarm | J460-01-1PMP-601 - Chilled Water Circulation Pump - Fail to Start Alarm | J460-01-1PMP-601_FailToStartAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1PMP-601_FailToStartAlm | 1 | M | - | bar: State 2 to State 64
1.0 | 59 | J270-06-1PNL-001 | J460-01-1PMP-601 | Alarm | J460-01-1PMP-601 - Chilled Water Circulation Pump - Fail to Stop Alarm | J460-01-1PMP-601_FailToStopAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1PMP-601_FailToStopAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 60 | J270-06-1PNL-001 | J460-01-1PMP-601 | Measurement | J460-01-2HSI-601 - Chilled Water Circulation Pump J460-01-1PMP-601 - Maintenance Switch | J460-01-2HSI-601_ChlWtrCirPmpMS | J460-01-2HSI-601_ChlWtrCirPmpMS | OFF | ON | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 61 | J270-06-1PNL-001 | J460-01-2FT-601 | Alarm | J460-01-2FT-601 - Chilled Water - Energy Meter Communication Failure Alarm | J460-01-2FT-601_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FT-601_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 62 | J270-06-1PNL-001 | J460-01-2FT-601 | Measurement | J460-01-2FT-601 - Chilled Water - Energy Meter Flow | J460-01-2FT-601_Flow | J460-01-2FT-601_Flow | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 63 | J270-06-1PNL-001 | J460-01-2FT-601 | Measurement | J460-01-2FT-601 - Chilled Water - Energy Meter Actual Power | J460-01-2FT-601_ActPwr | J460-01-2FT-601_ActPwr | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | GJ | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 64 | J270-06-1PNL-001 | J460-01-2FT-601 | Measurement | J460-01-2FT-601 - Chilled Water - Energy Meter Inlet Temperature | J460-01-2FT-601_InlTemp | J460-01-2FT-601_InlTemp | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 65 | J270-06-1PNL-001 | J460-01-2FT-601 | Measurement | J460-01-2FT-601 - Chilled Water - Energy Meter Outlet Temperature | J460-01-2FT-601_OutlTemp | J460-01-2FT-601_OutlTemp | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 66 | J270-06-1PNL-001 | J460-01-2FT-601 | Measurement | J460-01-2FT-601 - Chilled Water - Energy Meter Differential Temperature | J460-01-2FT-601_DiffTemp | J460-01-2FT-601_DiffTemp | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °K | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 67 | J270-06-1PNL-001 | J460-01-2FT-601 | Measurement | J460-01-2FT-601 - Chilled Water - Energy Meter Pressure | J460-01-2FT-601_Press | J460-01-2FT-601_Press | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 68 | J270-06-1PNL-001 | J460-01-2FT-601 | Measurement | J460-01-2FT-601 - Chilled Water - Energy Meter Heating Energy | J460-01-2FT-601_HtgEnergy | J460-01-2FT-601_HtgEnergy | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kWh | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 69 | J270-06-1PNL-001 | J460-01-2FT-601 | Measurement | J460-01-2FT-601 - Chilled Water - Energy Meter Cooling Energy | J460-01-2FT-601_ClgEnergy | J460-01-2FT-601_ClgEnergy | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kWh | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 70 | J270-06-1PNL-001 | J460-01-2FT-601 | Measurement | J460-01-2FT-601 - Chilled Water - Energy Meter Volume | J460-01-2FT-601_Volume | J460-01-2FT-601_Volume | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³ | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 71 | J270-06-1PNL-001 | J460-01-2FT-601 | Measurement | J460-01-2FT-601 - Chilled Water - Energy Meter Runtime | J460-01-2FT-601_RunTime | J460-01-2FT-601_RunTime | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 72 | J270-06-1PNL-001 | J460-01-2FT-602 | Alarm | J460-01-2FT-602 - Hot Water - Energy Meter Communication Failure Alarm | J460-01-2FT-602_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FT-602_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 73 | J270-06-1PNL-001 | J460-01-2FT-602 | Measurement | J460-01-2FT-602 - Hot Water - Energy Meter Flow | J460-01-2FT-602_Flow | J460-01-2FT-602_Flow | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 74 | J270-06-1PNL-001 | J460-01-2FT-602 | Measurement | J460-01-2FT-602 - Hot Water - Energy Meter Actual Power | J460-01-2FT-602_ActPwr | J460-01-2FT-602_ActPwr | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | GJ | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 75 | J270-06-1PNL-001 | J460-01-2FT-602 | Measurement | J460-01-2FT-602 - Hot Water - Energy Meter Inlet Temperature | J460-01-2FT-602_InlTemp | J460-01-2FT-602_InlTemp | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 76 | J270-06-1PNL-001 | J460-01-2FT-602 | Measurement | J460-01-2FT-602 - Hot Water - Energy Meter Outlet Temperature | J460-01-2FT-602_OutlTemp | J460-01-2FT-602_OutlTemp | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 77 | J270-06-1PNL-001 | J460-01-2FT-602 | Measurement | J460-01-2FT-602 - Hot Water - Energy Meter Differential Temperature | J460-01-2FT-602_DiffTemp | J460-01-2FT-602_DiffTemp | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °K | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 78 | J270-06-1PNL-001 | J460-01-2FT-602 | Measurement | J460-01-2FT-602 - Hot Water - Energy Meter Pressure | J460-01-2FT-602_Press | J460-01-2FT-602_Press | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 79 | J270-06-1PNL-001 | J460-01-2FT-602 | Measurement | J460-01-2FT-602 - Hot Water - Energy Meter Heating Energy | J460-01-2FT-602_HtgEnergy | J460-01-2FT-602_HtgEnergy | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kWh | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 80 | J270-06-1PNL-001 | J460-01-2FT-602 | Measurement | J460-01-2FT-602 - Hot Water - Energy Meter Cooling Energy | J460-01-2FT-602_ClgEnergy | J460-01-2FT-602_ClgEnergy | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kWh | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 81 | J270-06-1PNL-001 | J460-01-2FT-602 | Measurement | J460-01-2FT-602 - Hot Water - Energy Meter Volume | J460-01-2FT-602_Volume | J460-01-2FT-602_Volume | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³ | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 82 | J270-06-1PNL-001 | J460-01-2FT-602 | Measurement | J460-01-2FT-602 - Hot Water - Energy Meter Runtime | J460-01-2FT-602_RunTime | J460-01-2FT-602_RunTime | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 83 | J270-06-1PNL-001 | J460-01-2FT-603 | Measurement | J460-01-2FT-603 - 61LBK3 - Supply Air Flow | J460-01-2FT-603_SupAirFlow | J460-01-2FT-603_SupAirFlow | 0 | 5258 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 84 | J270-06-1PNL-001 | J460-01-2FT-603 | Measurement | J460-01-2FT-603 - 61LBK3 - Supply Air Flow Field | J460-01-2FT-603_SupAirFlow_Field | J460-01-2FT-603_SupAirFlow_Field | 0 | 5258 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 85 | J270-06-1PNL-001 | J460-01-2FT-603 | Alarm | J460-01-2FT-603 - 61LBK3 - Supply Air Flow High Alarm | J460-01-2FT-603_SupAirFlowHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FT-603_SupAirFlowHiAlm | 1 | Y | - | bar: State 2 to State 64
2.1 | 86 | J270-06-1PNL-001 | J460-01-2FT-603 | Setting | J460-01-2FT-603 - 61LBK3 - Supply Air Flow | J460-01-2FT-603_SupAirFlow_HASP | J460-01-2FT-603_SupAirFlow_HASP | - | 4200 | 3800 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | -
1.0 | 87 | J270-06-1PNL-001 | J460-01-2FT-603 | Alarm | J460-01-2FT-603 - 61LBK3 - Supply Air Flow Low Alarm | J460-01-2FT-603_SupAirFlowLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FT-603_SupAirFlowLoAlm | 1 | Y | - | bar: State 2 to State 64
2.1 | 88 | J270-06-1PNL-001 | J460-01-2FT-603 | Setting | J460-01-2FT-603 - 61LBK3 - Supply Air Flow | J460-01-2FT-603_SupAirFlow_LASP | J460-01-2FT-603_SupAirFlow_LASP | 3800 | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 89 | J270-06-1PNL-001 | J460-01-2FT-603 | Setting | J460-01-2FT-603 - 61LBK3 - Supply Air Flow Calibration Mode Selection | J460-01-2FT-603_SupAirFlowCalModeSel | J460-01-2FT-603_SupAirFlowCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 90 | J270-06-1PNL-001 | J460-01-2FT-603 | Alarm | J460-01-2FT-603 - 61LBK3 - Supply Air Flow Calibration Still Active Alarm | J460-01-2FT-603_SupAirFlowCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FT-603_SupAirFlowCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 91 | J270-06-1PNL-001 | J460-01-2FT-604 | Measurement | J460-01-2FT-604 - 61LBK3 - Return Air Flow | J460-01-2FT-604_RetAirFlow | J460-01-2FT-604_RetAirFlow | 0 | 6507 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 92 | J270-06-1PNL-001 | J460-01-2FT-604 | Measurement | J460-01-2FT-604 - 61LBK3 - Return Air Flow Field | J460-01-2FT-604_RetAirFlow_Field | J460-01-2FT-604_RetAirFlow_Field | 0 | 6507 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 93 | J270-06-1PNL-001 | J460-01-2FT-604 | Alarm | J460-01-2FT-604 - 61LBK3 - Return Air Flow High Alarm | J460-01-2FT-604_RetAirFlowHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FT-604_RetAirFlowHiAlm | 1 | Y | - | bar: State 2 to State 64
2.1 | 94 | J270-06-1PNL-001 | J460-01-2FT-604 | Setting | J460-01-2FT-604 - 61LBK3 - Return Air Flow | J460-01-2FT-604_RetAirFlow_HASP | J460-01-2FT-604_RetAirFlow_HASP | - | 4200 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 95 | J270-06-1PNL-001 | J460-01-2FT-604 | Alarm | J460-01-2FT-604 - 61LBK3 - Return Air Flow Low Alarm | J460-01-2FT-604_RetAirFlowLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FT-604_RetAirFlowLoAlm | 1 | Y | - | bar: State 2 to State 64
2.1 | 96 | J270-06-1PNL-001 | J460-01-2FT-604 | Setting | J460-01-2FT-604 - 61LBK3 - Return Air Flow | J460-01-2FT-604_RetAirFlow_LASP | J460-01-2FT-604_RetAirFlow_LASP | 3800 | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 97 | J270-06-1PNL-001 | J460-01-2FT-604 | Setting | J460-01-2FT-604 - 61LBK3 - Return Air Flow Calibration Mode Selection | J460-01-2FT-604_RetAirFlowCalModeSel | J460-01-2FT-604_RetAirFlowCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 98 | J270-06-1PNL-001 | J460-01-2FT-604 | Alarm | J460-01-2FT-604 - 61LBK3 - Return Air Flow Calibration Still Active Alarm | J460-01-2FT-604_RetAirFlowCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FT-604_RetAirFlowCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 99 | J270-06-1PNL-001 | J460-01-2TT-614 | Measurement | J460-01-2TT-614 - 61LBK3 - Supply Air Temperature | J460-01-2TT-614_SupAirTemp | J460-01-2TT-614_SupAirTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 100 | J270-06-1PNL-001 | J460-01-2TT-614 | Measurement | J460-01-2TT-614 - 61LBK3 - Supply Air Temperature Field | J460-01-2TT-614_SupAirTemp_Field | J460-01-2TT-614_SupAirTemp_Field | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 101 | J270-06-1PNL-001 | J460-01-2TT-614 | Alarm | J460-01-2TT-614 - 61LBK3 - Supply Air Temperature High Alarm | J460-01-2TT-614_SupAirTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-614_SupAirTempHiAlm | 1 | Y | - | bar: State 2 to State 64
2.1 | 102 | J270-06-1PNL-001 | J460-01-2TT-614 | Setting | J460-01-2TT-614 - 61LBK3 - Supply Air Temperature | J460-01-2TT-614_SupAirTemp_HASP | J460-01-2TT-614_SupAirTemp_HASP | - | 21 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 103 | J270-06-1PNL-001 | J460-01-2TT-614 | Alarm | J460-01-2TT-614 - 61LBK3 - Supply Air Temperature Low Alarm | J460-01-2TT-614_SupAirTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-614_SupAirTempLoAlm | 1 | Y | - | bar: State 2 to State 64
2.1 | 104 | J270-06-1PNL-001 | J460-01-2TT-614 | Setting | J460-01-2TT-614 - 61LBK3 - Supply Air Temperature | J460-01-2TT-614_SupAirTemp_LASP | J460-01-2TT-614_SupAirTemp_LASP | 15 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 105 | J270-06-1PNL-001 | J460-01-2TT-614 | Setting | J460-01-2TT-614 - 61LBK3 - Supply Air Temperature Calibration Mode Selection | J460-01-2TT-614_SupAirTempCalModeSel | J460-01-2TT-614_SupAirTempCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 106 | J270-06-1PNL-001 | J460-01-2TT-614 | Alarm | J460-01-2TT-614 - 61LBK3 - Supply Air Temperature Calibration Still Active Alarm | J460-01-2TT-614_SupAirTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-614_SupAirTempCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 107 | J270-06-1PNL-001 | J460-01-2TT-616 | Measurement | J460-01-2TT-616 - 61LBK3 - Return Air Temperature | J460-01-2TT-616_RetAirTemp | J460-01-2TT-616_RetAirTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 108 | J270-06-1PNL-001 | J460-01-2TT-616 | Measurement | J460-01-2TT-616 - 61LBK3 - Return Air Temperature Field | J460-01-2TT-616_RetAirTemp_Field | J460-01-2TT-616_RetAirTemp_Field | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 109 | J270-06-1PNL-001 | J460-01-2TT-616 | Alarm | J460-01-2TT-616 - 61LBK3 - Return Air Temperature High Alarm | J460-01-2TT-616_RetAirTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-616_RetAirTempHiAlm | 1 | Y | - | bar: State 2 to State 64
2.1 | 110 | J270-06-1PNL-001 | J460-01-2TT-616 | Setting | J460-01-2TT-616 - 61LBK3 - Return Air Temperature | J460-01-2TT-616_RetAirTemp_HASP | J460-01-2TT-616_RetAirTemp_HASP | - | 26 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 111 | J270-06-1PNL-001 | J460-01-2TT-616 | Alarm | J460-01-2TT-616 - 61LBK3 - Return Air Temperature Low Alarm | J460-01-2TT-616_RetAirTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-616_RetAirTempLoAlm | 1 | Y | - | bar: State 2 to State 64
2.1 | 112 | J270-06-1PNL-001 | J460-01-2TT-616 | Setting | J460-01-2TT-616 - 61LBK3 - Return Air Temperature | J460-01-2TT-616_RetAirTemp_LASP | J460-01-2TT-616_RetAirTemp_LASP | 16 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 113 | J270-06-1PNL-001 | J460-01-2TT-616 | Setting | J460-01-2TT-616 - 61LBK3 - Return Air Temperature Calibration Mode Selection | J460-01-2TT-616_RetAirTempCalModeSel | J460-01-2TT-616_RetAirTempCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 114 | J270-06-1PNL-001 | J460-01-2TT-616 | Alarm | J460-01-2TT-616 - 61LBK3 - Return Air Temperature Calibration Still Active Alarm | J460-01-2TT-616_RetAirTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-616_RetAirTempCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 115 | J270-06-1PNL-001 | J460-01-2MT-614 | Measurement | J460-01-2MT-614 - 61LBK3 - Supply Air Humidity | J460-01-2MT-614_SupAirHum | J460-01-2MT-614_SupAirHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 116 | J270-06-1PNL-001 | J460-01-2MT-614 | Measurement | J460-01-2MT-614 - 61LBK3 - Supply Air Humidity Field | J460-01-2MT-614_SupAirHum_Field | J460-01-2MT-614_SupAirHum_Field | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 117 | J270-06-1PNL-001 | J460-01-2MT-614 | Alarm | J460-01-2MT-614 - 61LBK3 - Supply Air Humidity High Alarm | J460-01-2MT-614_SupAirHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-614_SupAirHumHiAlm | 1 | Y | - | bar: State 2 to State 64
2.1 | 118 | J270-06-1PNL-001 | J460-01-2MT-614 | Setting | J460-01-2MT-614 - 61LBK3 - Supply Air Humidity | J460-01-2MT-614_SupAirHum_HASP | J460-01-2MT-614_SupAirHum_HASP | - | 80 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 119 | J270-06-1PNL-001 | J460-01-2MT-614 | Alarm | J460-01-2MT-614 - 61LBK3 - Supply Air Humidity Low Alarm | J460-01-2MT-614_SupAirHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-614_SupAirHumLoAlm | 1 | Y | - | bar: State 2 to State 64
2.1 | 120 | J270-06-1PNL-001 | J460-01-2MT-614 | Setting | J460-01-2MT-614 - 61LBK3 - Supply Air Humidity | J460-01-2MT-614_SupAirHum_LASP | J460-01-2MT-614_SupAirHum_LASP | 30 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 121 | J270-06-1PNL-001 | J460-01-2MT-614 | Setting | J460-01-2MT-614 - 61LBK3 - Supply Air Humidity Calibration Mode Selection | J460-01-2MT-614_SupAirHumCalModeSel | J460-01-2MT-614_SupAirHumCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 122 | J270-06-1PNL-001 | J460-01-2MT-614 | Alarm | J460-01-2MT-614 - 61LBK3 - Supply Air Humidity Calibration Still Active Alarm | J460-01-2MT-614_SupAirHumCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-614_SupAirHumCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 123 | J270-06-1PNL-001 | J100-06-2TT-001 | Measurement | J100-06-2TT-001 - Potable Water - Temperature | J100-06-2TT-001_PotWtrSupTemp | J100-06-2TT-001_PotWtrSupTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 124 | J270-06-1PNL-001 | J100-06-2TT-001 | Measurement | J100-06-2TT-001 - Potable Water - Temperature Field | J100-06-2TT-001_PotWtrSupTemp_Field | J100-06-2TT-001_PotWtrSupTemp_Field | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 125 | J270-06-1PNL-001 | J100-06-2TT-001 | Alarm | J100-06-2TT-001 - Potable Water - Temperature High Alarm | J100-06-2TT-001_PotWtrSupTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J100-06-2TT-001_PotWtrSupTempHiAlm | 2 | Y | - | bar: State 2 to State 64
2.1 | 126 | J270-06-1PNL-001 | J100-06-2TT-001 | Setting | J100-06-2TT-001 - Potable Water - Temperature | J100-06-2TT-001_PotWtrSupTemp_HASP | J100-06-2TT-001_PotWtrSupTemp_HASP | - | 30 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 127 | J270-06-1PNL-001 | J100-06-2TT-001 | Alarm | J100-06-2TT-001 - Potable Water - Temperature Low Alarm | J100-06-2TT-001_PotWtrSupTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J100-06-2TT-001_PotWtrSupTempLoAlm | 2 | Y | - | bar: State 2 to State 64
2.1 | 128 | J270-06-1PNL-001 | J100-06-2TT-001 | Setting | J100-06-2TT-001 - Potable Water - Temperature | J100-06-2TT-001_PotWtrSupTemp_LASP | J100-06-2TT-001_PotWtrSupTemp_LASP | 15 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 129 | J270-06-1PNL-001 | J100-06-2TT-001 | Setting | J100-06-2TT-001 - Potable Water - Temperature Calibration Mode Selection | J100-06-2TT-001_PotWtrSupTempCalModeSel | J100-06-2TT-001_PotWtrSupTempCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 130 | J270-06-1PNL-001 | J100-06-2TT-001 | Alarm | J100-06-2TT-001 - Potable Water - Temperature Calibration Still Active Alarm | J100-06-2TT-001_PotWtrSupTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J100-06-2TT-001_PotWtrSupTempCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 131 | J270-06-1PNL-001 | J100-06-2FT-001 | Alarm | J100-06-2FT-001 - Potable Water - Flow Communication Failure Alarm | J100-06-2FT-001_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J100-06-2FT-001_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 132 | J270-06-1PNL-001 | J100-06-2FT-001 | Measurement | J100-06-2FT-001 - Potable Water - Flow Fabrication Number | J100-06-2FT-001_FabNo | J100-06-2FT-001_FabNo | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 133 | J270-06-1PNL-001 | J100-06-2FT-001 | Measurement | J100-06-2FT-001 - Potable Water - Flow Cust. ID | J100-06-2FT-001_CustID | J100-06-2FT-001_CustID | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 134 | J270-06-1PNL-001 | J100-06-2FT-001 | Measurement | J100-06-2FT-001 - Potable Water - Flow Time Point | J100-06-2FT-001_TimePt | J100-06-2FT-001_TimePt | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 135 | J270-06-1PNL-001 | J100-06-2FT-001 | Measurement | J100-06-2FT-001 - Potable Water - Flow Bat. time | J100-06-2FT-001_BatTime | J100-06-2FT-001_BatTime | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 136 | J270-06-1PNL-001 | J100-06-2FT-001 | Measurement | J100-06-2FT-001 - Potable Water - Flow Volume | J100-06-2FT-001_Vol1 | J100-06-2FT-001_Vol1 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 137 | J270-06-1PNL-001 | J100-06-2FT-001 | Measurement | J100-06-2FT-001 - Potable Water - Flow Volume [l]/Next VIFE Manufacturer specific | J100-06-2FT-001_NextVIFE | J100-06-2FT-001_NextVIFE | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 138 | J270-06-1PNL-001 | J100-06-2FT-001 | Measurement | J100-06-2FT-001 - Potable Water - Flow Volume | J100-06-2FT-001_Vol2 | J100-06-2FT-001_Vol2 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 139 | J270-06-1PNL-001 | J100-06-2FT-001 | Measurement | J100-06-2FT-001 - Potable Water - Flow Manufacturer specific data structure | J100-06-2FT-001_Data | J100-06-2FT-001_Data | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 140 | J270-06-1PNL-001 | J100-06-2TT-002 | Measurement | J100-06-2TT-002 - Potable Hot Water - Inlet Temperature Heater | J100-06-2TT-002_HotWtrInlTmp | J100-06-2TT-002_HotWtrInlTmp | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 141 | J270-06-1PNL-001 | J100-06-2TT-002 | Measurement | J100-06-2TT-002 - Potable Hot Water - Inlet Temperature Heater Field | J100-06-2TT-002_HotWtrInlTmp_Field | J100-06-2TT-002_HotWtrInlTmp_Field | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 142 | J270-06-1PNL-001 | J100-06-2TT-002 | Alarm | J100-06-2TT-002 - Potable Hot Water - Inlet Temperature Heater High Alarm | J100-06-2TT-002_HotWtrInlTmpHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J100-06-2TT-002_HotWtrInlTmpHiAlm | 1 | Y | - | bar: State 2 to State 64
2.1 | 143 | J270-06-1PNL-001 | J100-06-2TT-002 | Setting | J100-06-2TT-002 - Potable Hot Water - Inlet Temperature Heater | J100-06-2TT-002_HotWtrInlTmp_HASP | J100-06-2TT-002_HotWtrInlTmp_HASP | - | 35 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 144 | J270-06-1PNL-001 | J100-06-2TT-002 | Alarm | J100-06-2TT-002 - Potable Hot Water - Inlet Temperature Heater Low Alarm | J100-06-2TT-002_HotWtrInlTmpLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J100-06-2TT-002_HotWtrInlTmpLoAlm | 1 | Y | - | bar: State 2 to State 64
2.1 | 145 | J270-06-1PNL-001 | J100-06-2TT-002 | Setting | J100-06-2TT-002 - Potable Hot Water - Inlet Temperature Heater | J100-06-2TT-002_HotWtrInlTmp_LASP | J100-06-2TT-002_HotWtrInlTmp_LASP | 25 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 146 | J270-06-1PNL-001 | J100-06-2TT-002 | Setting | J100-06-2TT-002 - Potable Hot Water - Inlet Temperature Heater Calibration Mode Selection | J100-06-2TT-002_HotWtrInlTmpCalModeSel | J100-06-2TT-002_HotWtrInlTmpCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 147 | J270-06-1PNL-001 | J100-06-2TT-002 | Alarm | J100-06-2TT-002 - Potable Hot Water - Inlet Temperature Heater Calibration Still Active Alarm | J100-06-2TT-002_HotWtrInlTmpCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J100-06-2TT-002_HotWtrInlTmpCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 148 | J270-06-1PNL-001 | J100-06-2XCV-001 | Measurement | J100-06-2XCV-001 - Legionella Dump Valve | J100-06-2TCT-001_LegDmpVlv | J100-06-2TCT-001_LegDmpVlv | CLOSE | OPEN | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 149 | J270-06-1PNL-001 | J130-06-2TT-001 | Measurement | J130-06-2TT-001 - Non Potable Water - Temperature | J130-06-2TT-001_NPotWtrSupTemp | J130-06-2TT-001_NPotWtrSupTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 150 | J270-06-1PNL-001 | J130-06-2TT-001 | Measurement | J130-06-2TT-001 - Non Potable Water - Temperature Field | J130-06-2TT-001_NPotWtrSupTemp_Field | J130-06-2TT-001_NPotWtrSupTemp_Field | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 151 | J270-06-1PNL-001 | J130-06-2TT-001 | Alarm | J130-06-2TT-001 - Non Potable Water - Temperature High Alarm | J130-06-2TT-001_NPotWtrSupTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J130-06-2TT-001_NPotWtrSupTempHiAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 152 | J270-06-1PNL-001 | J130-06-2TT-001 | Setting | J130-06-2TT-001 - Non Potable Water - Temperature | J130-06-2TT-001_NPotWtrSupTemp_HASP | J130-06-2TT-001_NPotWtrSupTemp_HASP | - | 30 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 153 | J270-06-1PNL-001 | J130-06-2TT-001 | Alarm | J130-06-2TT-001 - Non Potable Water - Temperature Low Alarm | J130-06-2TT-001_NPotWtrSupTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J130-06-2TT-001_NPotWtrSupTempLoAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 154 | J270-06-1PNL-001 | J130-06-2TT-001 | Setting | J130-06-2TT-001 - Non Potable Water - Temperature | J130-06-2TT-001_NPotWtrSupTemp_LASP | J130-06-2TT-001_NPotWtrSupTemp_LASP | 10 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 155 | J270-06-1PNL-001 | J130-06-2TT-001 | Setting | J130-06-2TT-001 - Non Potable Water - Temperature Calibration Mode Selection | J130-06-2TT-001_NPotWtrSupTempCalModeSel | J130-06-2TT-001_NPotWtrSupTempCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 156 | J270-06-1PNL-001 | J130-06-2TT-001 | Alarm | J130-06-2TT-001 - Non Potable Water - Temperature Calibration Still Active Alarm | J130-06-2TT-001_NPotWtrSupTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J130-06-2TT-001_NPotWtrSupTempCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 157 | J270-06-1PNL-001 | J130-06-2PT-001 | Measurement | J130-06-2PT-001 - Non Potable Water - Pressure | J130-06-2PT-001_NPotWtrSupPress | J130-06-2PT-001_NPotWtrSupPress | 0 | 6 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 158 | J270-06-1PNL-001 | J130-06-2PT-001 | Measurement | J130-06-2PT-001 - Non Potable Water - Pressure Field | J130-06-2PT-001_NPotWtrSupPress_Field | J130-06-2PT-001_NPotWtrSupPress_Field | 0 | 6 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 159 | J270-06-1PNL-001 | J130-06-2PT-001 | Alarm | J130-06-2PT-001 - Non Potable Water - Pressure High Alarm | J130-06-2PT-001_NPotWtrSupPressHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J130-06-2PT-001_NPotWtrSupPressHiAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 160 | J270-06-1PNL-001 | J130-06-2PT-001 | Setting | J130-06-2PT-001 - Non Potable Water - Pressure | J130-06-2PT-001_NPotWtrSupPress_HASP | J130-06-2PT-001_NPotWtrSupPress_HASP | - | 10 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 161 | J270-06-1PNL-001 | J130-06-2PT-001 | Alarm | J130-06-2PT-001 - Non Potable Water - Pressure Low Alarm | J130-06-2PT-001_NPotWtrSupPressLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J130-06-2PT-001_NPotWtrSupPressLoAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 162 | J270-06-1PNL-001 | J130-06-2PT-001 | Setting | J130-06-2PT-001 - Non Potable Water - Pressure | J130-06-2PT-001_NPotWtrSupPress_LASP | J130-06-2PT-001_NPotWtrSupPress_LASP | 7 | - | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 163 | J270-06-1PNL-001 | J130-06-2PT-001 | Setting | J130-06-2PT-001 - Non Potable Water - Pressure Calibration Mode Selection | J130-06-2PT-001_NPotWtrSupPresCalModeSel | J130-06-2PT-001_NPotWtrSupPresCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 164 | J270-06-1PNL-001 | J130-06-2PT-001 | Alarm | J130-06-2PT-001 - Non Potable Water - Pressure Calibration Still Active Alarm | J130-06-2PT-001_NPotWtrSupPresCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J130-06-2PT-001_NPotWtrSupPresCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 165 | J270-06-1PNL-001 | J130-06-2FT-001 | Alarm | J130-06-2FT-001 - Non Potable Water - Flow Communication Failure Alarm | J130-06-2FT-001_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J130-06-2FT-001_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 166 | J270-06-1PNL-001 | J130-06-2FT-001 | Measurement | J130-06-2FT-001 - Non Potable Water - Flow Fabrication Number | J130-06-2FT-001_FabNo | J130-06-2FT-001_FabNo | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 167 | J270-06-1PNL-001 | J130-06-2FT-001 | Measurement | J130-06-2FT-001 - Non Potable Water - Flow Cust. ID | J130-06-2FT-001_CustID | J130-06-2FT-001_CustID | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 168 | J270-06-1PNL-001 | J130-06-2FT-001 | Measurement | J130-06-2FT-001 - Non Potable Water - Flow Time Point | J130-06-2FT-001_TimePt | J130-06-2FT-001_TimePt | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 169 | J270-06-1PNL-001 | J130-06-2FT-001 | Measurement | J130-06-2FT-001 - Non Potable Water - Flow Bat. time | J130-06-2FT-001_BatTime | J130-06-2FT-001_BatTime | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 170 | J270-06-1PNL-001 | J130-06-2FT-001 | Measurement | J130-06-2FT-001 - Non Potable Water - Flow Volume | J130-06-2FT-001_Vol1 | J130-06-2FT-001_Vol1 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 171 | J270-06-1PNL-001 | J130-06-2FT-001 | Measurement | J130-06-2FT-001 - Non Potable Water - Flow Volume [l]/Next VIFE Manufacturer specific | J130-06-2FT-001_NextVIFE | J130-06-2FT-001_NextVIFE | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 172 | J270-06-1PNL-001 | J130-06-2FT-001 | Measurement | J130-06-2FT-001 - Non Potable Water - Flow Volume | J130-06-2FT-001_Vol2 | J130-06-2FT-001_Vol2 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 173 | J270-06-1PNL-001 | J130-06-2FT-001 | Measurement | J130-06-2FT-001 - Non Potable Water - Flow Manufacturer specific data structure | J130-06-2FT-001_Data | J130-06-2FT-001_Data | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 174 | J270-06-1PNL-001 | J305-06-2FT-001 | Alarm | J305-06-2FT-001 - Compressed Air - Flow Meter Communication Failure Alarm | J305-06-2FT-001_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J305-06-2FT-001_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 175 | J270-06-1PNL-001 | J305-06-2FT-001 | Measurement | J305-06-2FT-001 - Compressed Air - Reset Alarm | J305-06-2FT-001_Reset | J305-06-2FT-001_Reset | NORESET | RSTCNTR | RSTALM | RSTCNTR | RDISCNTR | RSTFWPRG | RAIERBIT | RAIWNBIT | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 176 | J270-06-1PNL-001 | J305-06-2FT-001 | Measurement | J305-06-2FT-001 - Compressed Air - Gas Flow Percentage | J305-06-2FT-001_FlowPerc | J305-06-2FT-001_FlowPerc | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 177 | J270-06-1PNL-001 | J305-06-2FT-001 | Measurement | J305-06-2FT-001 - Compressed Air - Gas Flow | J305-06-2FT-001_Flow | J305-06-2FT-001_Flow | 4 | 750 | [11 empty] | - | - | - | - | - | - | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 178 | J270-06-1PNL-001 | J305-06-2FT-001 | Measurement | J305-06-2FT-001 - Compressed Air - Gas Flow Alarm | J305-06-2FT-001_Alm | J305-06-2FT-001_Alm | - | ERROR | WARNING | - | MINALM | - | - | - | MAXALM | - | BCNTRALM | PWRUPALM | MSALARM | HWALARM | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 179 | J270-06-1PNL-001 | J305-06-2PT-001 | Measurement | J305-06-2PT-001 - Compressed Air - Pressure | J305-06-2PT-001_CompAirPress | J305-06-2PT-001_CompAirPress | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 180 | J270-06-1PNL-001 | J305-06-2PT-001 | Measurement | J305-06-2PT-001 - Compressed Air - Pressure Field | J305-06-2PT-001_CompAirPress_Field | J305-06-2PT-001_CompAirPress_Field | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 181 | J270-06-1PNL-001 | J305-06-2PT-001 | Alarm | J305-06-2PT-001 - Compressed Air - Pressure High Alarm | J305-06-2PT-001_CompAirPressHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J305-06-2PT-001_CompAirPressHiAlm | 2 | Y | - | bar: State 2 to State 64
2.1 | 182 | J270-06-1PNL-001 | J305-06-2PT-001 | Setting | J305-06-2PT-001 - Compressed Air - Pressure | J305-06-2PT-001_CompAirPress_HASP | J305-06-2PT-001_CompAirPress_HASP | - | 5 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 183 | J270-06-1PNL-001 | J305-06-2PT-001 | Alarm | J305-06-2PT-001 - Compressed Air - Pressure Low Alarm | J305-06-2PT-001_CompAirPressLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J305-06-2PT-001_CompAirPressLoAlm | 2 | Y | - | bar: State 2 to State 64
2.1 | 184 | J270-06-1PNL-001 | J305-06-2PT-001 | Setting | J305-06-2PT-001 - Compressed Air - Pressure | J305-06-2PT-001_CompAirPress_LASP | J305-06-2PT-001_CompAirPress_LASP | 1 | - | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 185 | J270-06-1PNL-001 | J305-06-2PT-001 | Setting | J305-06-2PT-001 - Compressed Air - Pressure Calibration Mode Selection | J305-06-2PT-001_CompAirPressCalModeSel | J305-06-2PT-001_CompAirPressCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 186 | J270-06-1PNL-001 | J305-06-2PT-001 | Alarm | J305-06-2PT-001 - Compressed Air - Pressure Calibration Still Active Alarm | J305-06-2PT-001_CompAirPressCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J305-06-2PT-001_CompAirPressCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 187 | J270-06-1PNL-001 | J305-06-2MT-001 | Measurement | J305-06-2MT-001 - Compressed Air - Dewpoint | J305-06-2MT-001_CompAirDP | J305-06-2MT-001_CompAirDP | -20 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 188 | J270-06-1PNL-001 | J305-06-2MT-001 | Measurement | J305-06-2MT-001 - Compressed Air - Dewpoint Field | J305-06-2MT-001_CompAirDP_Field | J305-06-2MT-001_CompAirDP_Field | -20 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 189 | J270-06-1PNL-001 | J305-06-2MT-001 | Alarm | J305-06-2MT-001 - Compressed Air - Dewpoint High Alarm | J305-06-2MT-001_CompAirDPHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J305-06-2MT-001_CompAirDPHiAlm | 2 | Y | - | bar: State 2 to State 64
2.1 | 190 | J270-06-1PNL-001 | J305-06-2MT-001 | Setting | J305-06-2MT-001 - Compressed Air - Dewpoint | J305-06-2MT-001_CompAirDP_HASP | J305-06-2MT-001_CompAirDP_HASP | - | 30 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 191 | J270-06-1PNL-001 | J305-06-2MT-001 | Alarm | J305-06-2MT-001 - Compressed Air - Dewpoint Low Alarm | J305-06-2MT-001_CompAirDPLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J305-06-2MT-001_CompAirDPLoAlm | 2 | Y | - | bar: State 2 to State 64
2.1 | 192 | J270-06-1PNL-001 | J305-06-2MT-001 | Setting | J305-06-2MT-001 - Compressed Air - Dewpoint | J305-06-2MT-001_CompAirDP_LASP | J305-06-2MT-001_CompAirDP_LASP | 10 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 193 | J270-06-1PNL-001 | J305-06-2MT-001 | Setting | J305-06-2MT-001 - Compressed Air - Dewpoint Calibration Mode Selection | J305-06-2MT-001_CompAirDPCalModeSel | J305-06-2MT-001_CompAirDPCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 194 | J270-06-1PNL-001 | J305-06-2MT-001 | Alarm | J305-06-2MT-001 - Compressed Air - Dewpoint Calibration Still Active Alarm | J305-06-2MT-001_CompAirDPCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J305-06-2MT-001_CompAirDPCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 195 | J270-06-1PNL-001 | J320-06-2FT-001 | Alarm | J320-06-2FT-001 - Carbon Dioxide Gas - Flow Meter Communication Failure Alarm | J320-06-2FT-001_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | J320-06-2FT-001_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 196 | J270-06-1PNL-001 | J320-06-2FT-001 | Measurement | J320-06-2FT-001 - Carbon Dioxide Gas - Reset Alarm | J320-06-2FT-001_Reset | J320-06-2FT-001_Reset | NORESET | RSTCNTR | RSTALM | RSTCNTR | RDISCNTR | RSTFWPRG | RAIERBIT | RAIWNBIT | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 197 | J270-06-1PNL-001 | J320-06-2FT-001 | Measurement | J320-06-2FT-001 - Carbon Dioxide Gas - Gas Flow Percentage | J320-06-2FT-001_FlowPerc | J320-06-2FT-001_FlowPerc | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 198 | J270-06-1PNL-001 | J320-06-2FT-001 | Measurement | J320-06-2FT-001 - Carbon Dioxide Gas - Gas Flow | J320-06-2FT-001_Flow | J320-06-2FT-001_Flow | 3 | 390 | [11 empty] | - | - | - | - | - | - | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 199 | J270-06-1PNL-001 | J320-06-2FT-001 | Measurement | J320-06-2FT-001 - Carbon Dioxide Gas - Gas Flow Alarm | J320-06-2FT-001_Alm | J320-06-2FT-001_Alm | - | ERROR | WARNING | - | MINALM | - | - | - | MAXALM | - | BCNTRALM | PWRUPALM | MSALARM | HWALARM | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 200 | J270-06-1PNL-001 | J320-06-2PT-001 | Measurement | J320-06-2PT-001 - Carbon Dioxide Gas - Pressure | J320-06-2PT-001_CO2Press | J320-06-2PT-001_CO2Press | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 201 | J270-06-1PNL-001 | J320-06-2PT-001 | Measurement | J320-06-2PT-001 - Carbon Dioxide Gas - Pressure Field | J320-06-2PT-001_CO2Press_Field | J320-06-2PT-001_CO2Press_Field | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 202 | J270-06-1PNL-001 | J320-06-2PT-001 | Alarm | J320-06-2PT-001 - Carbon Dioxide Gas - Pressure High Alarm | J320-06-2PT-001_CO2PressHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J320-06-2PT-001_CO2PressHiAlm | 2 | Y | - | bar: State 2 to State 64
2.1 | 203 | J270-06-1PNL-001 | J320-06-2PT-001 | Setting | J320-06-2PT-001 - Carbon Dioxide Gas - Pressure | J320-06-2PT-001_CO2Press_HASP | J320-06-2PT-001_CO2Press_HASP | - | 8 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 204 | J270-06-1PNL-001 | J320-06-2PT-001 | Alarm | J320-06-2PT-001 - Carbon Dioxide Gas - Pressure Low Alarm | J320-06-2PT-001_CO2PressLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J320-06-2PT-001_CO2PressLoAlm | 2 | Y | - | bar: State 2 to State 64
2.1 | 205 | J270-06-1PNL-001 | J320-06-2PT-001 | Setting | J320-06-2PT-001 - Carbon Dioxide Gas - Pressure | J320-06-2PT-001_CO2Press_LASP | J320-06-2PT-001_CO2Press_LASP | 3 | - | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 206 | J270-06-1PNL-001 | J320-06-2PT-001 | Setting | J320-06-2PT-001 - Carbon Dioxide Gas - Pressure Calibration Mode Selection | J320-06-2PT-001_CO2PressCalModeSel | J320-06-2PT-001_CO2PressCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 207 | J270-06-1PNL-001 | J320-06-2PT-001 | Alarm | J320-06-2PT-001 - Carbon Dioxide Gas - Pressure Calibration Still Active Alarm | J320-06-2PT-001_CO2PressCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J320-06-2PT-001_CO2PressCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 208 | J270-06-1PNL-001 | J330-06-2PT-001 | Alarm | J330-06-2FT-001 - Nitrogen Gas - Flow Meter Communication Failure Alarm | J330-06-2FT-001_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J330-06-2FT-001_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 209 | J270-06-1PNL-001 | J330-06-2FT-001 | Measurement | J330-06-2FT-001 - Nitrogen Gas - Reset Alarm | J330-06-2FT-001_Reset | J330-06-2FT-001_Reset | NORESET | RSTCNTR | RSTALM | RSTCNTR | RDISCNTR | RSTFWPRG | RAIERBIT | RAIWNBIT | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 210 | J270-06-1PNL-001 | J330-06-2FT-001 | Measurement | J330-06-2FT-001 - Nitrogen Gas - Gas Flow Percentage | J330-06-2FT-001_FlowPerc | J330-06-2FT-001_FlowPerc | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 211 | J270-06-1PNL-001 | J330-06-2FT-001 | Measurement | J330-06-2FT-001 - Nitrogen Gas - Gas Flow | J330-06-2FT-001_Flow | J330-06-2FT-001_Flow | 0.6 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 212 | J270-06-1PNL-001 | J330-06-2FT-001 | Measurement | J330-06-2FT-001 - Nitrogen Gas - Gas Flow Alarm | J330-06-2FT-001_Alm | J330-06-2FT-001_Alm | - | ERROR | WARNING | - | MINALM | - | - | - | MAXALM | - | BCNTRALM | PWRUPALM | MSALARM | HWALARM | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 213 | J270-06-1PNL-001 | J330-06-2PT-001 | Measurement | J330-06-2PT-001 - Nitrogen Gas - Pressure | J330-06-2PT-001_NitroPress | J330-06-2PT-001_NitroPress | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 214 | J270-06-1PNL-001 | J330-06-2PT-001 | Measurement | J330-06-2PT-001 - Nitrogen Gas - Pressure Field | J330-06-2PT-001_NitroPress_Field | J330-06-2PT-001_NitroPress_Field | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 215 | J270-06-1PNL-001 | J330-06-2PT-001 | Alarm | J330-06-2PT-001 - Nitrogen Gas - Pressure High Alarm | J330-06-2PT-001_NitroPressHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J330-06-2PT-001_NitroPressHiAlm | 2 | Y | - | bar: State 2 to State 64
2.1 | 216 | J270-06-1PNL-001 | J330-06-2PT-001 | Setting | J330-06-2PT-001 - Nitrogen Gas - Pressure | J330-06-2PT-001_NitroPress_HASP | J330-06-2PT-001_NitroPress_HASP | - | 10 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 217 | J270-06-1PNL-001 | J330-06-2PT-001 | Alarm | J330-06-2PT-001 - Nitrogen Gas - Pressure Low Alarm | J330-06-2PT-001_NitroPressLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J330-06-2PT-001_NitroPressLoAlm | 2 | Y | - | bar: State 2 to State 64
2.1 | 218 | J270-06-1PNL-001 | J330-06-2PT-001 | Setting | J330-06-2PT-001 - Nitrogen Gas - Pressure | J330-06-2PT-001_NitroPress_LASP | J330-06-2PT-001_NitroPress_LASP | 7 | - | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 219 | J270-06-1PNL-001 | J330-06-2PT-001 | Setting | J330-06-2PT-001 - Nitrogen Gas - Pressure Calibration Mode Selection | J330-06-2PT-001_NitroPressCalModeSel | J330-06-2PT-001_NitroPressCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 220 | J270-06-1PNL-001 | J330-06-2PT-001 | Alarm | J330-06-2PT-001 - Nitrogen Gas - Pressure Calibration Still Active Alarm | J330-06-2PT-001_NitroPressCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J330-06-2PT-001_NitroPressCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 221 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter Current Phase L1 | J229-06-1QIT-001_CurrPhase1 | J229-06-1QIT-001_CurrPhase1 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 222 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter Current Phase L2 | J229-06-1QIT-001_CurrPhase2 | J229-06-1QIT-001_CurrPhase2 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 223 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter Current Phase L3 | J229-06-1QIT-001_CurrPhase3 | J229-06-1QIT-001_CurrPhase3 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 224 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter 3-Phase Average | J229-06-1QIT-001_3PhaseAvg | J229-06-1QIT-001_3PhaseAvg | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 225 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter Voltage Phase A-B | J229-06-1QIT-001_VoltPhaseA_B | J229-06-1QIT-001_VoltPhaseA_B | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 226 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter Voltage Phase B-C | J229-06-1QIT-001_VoltPhaseB_C | J229-06-1QIT-001_VoltPhaseB_C | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 227 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter Voltage Phase C-A | J229-06-1QIT-001_VoltPhaseC_A | J229-06-1QIT-001_VoltPhaseC_A | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 228 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter L-L Average | J229-06-1QIT-001_LLAverage | J229-06-1QIT-001_LLAverage | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 229 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter L-N Average | J229-06-1QIT-001_LNAverage | J229-06-1QIT-001_LNAverage | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 230 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter Real Power | J229-06-1QIT-001_RealPower | J229-06-1QIT-001_RealPower | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 231 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter Reactive Power | J229-06-1QIT-001_ReactivePower | J229-06-1QIT-001_ReactivePower | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kVAr | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 232 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter Apparent Power | J229-06-1QIT-001_ApparentPower | J229-06-1QIT-001_ApparentPower | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kVAr | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 233 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter Frequency | J229-06-1QIT-001_Frequency | J229-06-1QIT-001_Frequency | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 234 | J270-06-1PNL-001 | J229-06-1QIT-002 | Measurement | J229-06-1QIT-002 - VK-6H-1 - Energy Meter Current Phase L1 | J229-06-1QIT-002_CurrPhase1 | J229-06-1QIT-002_CurrPhase1 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 235 | J270-06-1PNL-001 | J229-06-1QIT-002 | Measurement | J229-06-1QIT-002 - VK-6H-1 - Energy Meter Current Phase L2 | J229-06-1QIT-002_CurrPhase2 | J229-06-1QIT-002_CurrPhase2 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 236 | J270-06-1PNL-001 | J229-06-1QIT-002 | Measurement | J229-06-1QIT-002 - VK-6H-1 - Energy Meter Current Phase L3 | J229-06-1QIT-002_CurrPhase3 | J229-06-1QIT-002_CurrPhase3 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 237 | J270-06-1PNL-001 | J229-06-1QIT-002 | Measurement | J229-06-1QIT-002 - VK-6H-1 - Energy Meter 3-Phase Average | J229-06-1QIT-002_3PhaseAvg | J229-06-1QIT-002_3PhaseAvg | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 238 | J270-06-1PNL-001 | J229-06-1QIT-002 | Measurement | J229-06-1QIT-002 - VK-6H-1 - Energy Meter Voltage Phase A-B | J229-06-1QIT-002_VoltPhaseA_B | J229-06-1QIT-002_VoltPhaseA_B | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 239 | J270-06-1PNL-001 | J229-06-1QIT-002 | Measurement | J229-06-1QIT-002 - VK-6H-1 - Energy Meter Voltage Phase B-C | J229-06-1QIT-002_VoltPhaseB_C | J229-06-1QIT-002_VoltPhaseB_C | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 240 | J270-06-1PNL-001 | J229-06-1QIT-002 | Measurement | J229-06-1QIT-002 - VK-6H-1 - Energy Meter Voltage Phase C-A | J229-06-1QIT-002_VoltPhaseC_A | J229-06-1QIT-002_VoltPhaseC_A | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 241 | J270-06-1PNL-001 | J229-06-1QIT-002 | Measurement | J229-06-1QIT-002 - VK-6H-1 - Energy Meter L-L Average | J229-06-1QIT-002_LLAverage | J229-06-1QIT-002_LLAverage | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 242 | J270-06-1PNL-001 | J229-06-1QIT-002 | Measurement | J229-06-1QIT-002 - VK-6H-1 - Energy Meter L-N Average | J229-06-1QIT-002_LNAverage | J229-06-1QIT-002_LNAverage | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 243 | J270-06-1PNL-001 | J229-06-1QIT-002 | Measurement | J229-06-1QIT-002 - VK-6H-1 - Energy Meter Real Power | J229-06-1QIT-002_RealPower | J229-06-1QIT-002_RealPower | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 244 | J270-06-1PNL-001 | J229-06-1QIT-002 | Measurement | J229-06-1QIT-002 - VK-6H-1 - Energy Meter Reactive Power | J229-06-1QIT-002_ReactivePower | J229-06-1QIT-002_ReactivePower | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kVAr | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 245 | J270-06-1PNL-001 | J229-06-1QIT-002 | Measurement | J229-06-1QIT-002 - VK-6H-1 - Energy Meter Apparent Power | J229-06-1QIT-002_ApparentPower | J229-06-1QIT-002_ApparentPower | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kVAr | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 246 | J270-06-1PNL-001 | J229-06-1QIT-002 | Measurement | J229-06-1QIT-002 - VK-6H-1 - Energy Meter Frequency | J229-06-1QIT-002_Frequency | J229-06-1QIT-002_Frequency | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 247 | J270-06-1PNL-001 | J229-06-1QIT-003 | Measurement | J229-06-1QIT-003 - VK-6H-2 - Energy Meter Current Phase L1 | J229-06-1QIT-003_CurrPhase1 | J229-06-1QIT-003_CurrPhase1 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 248 | J270-06-1PNL-001 | J229-06-1QIT-003 | Measurement | J229-06-1QIT-003 - VK-6H-2 - Energy Meter Current Phase L2 | J229-06-1QIT-003_CurrPhase2 | J229-06-1QIT-003_CurrPhase2 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 249 | J270-06-1PNL-001 | J229-06-1QIT-003 | Measurement | J229-06-1QIT-003 - VK-6H-2 - Energy Meter Current Phase L3 | J229-06-1QIT-003_CurrPhase3 | J229-06-1QIT-003_CurrPhase3 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 250 | J270-06-1PNL-001 | J229-06-1QIT-003 | Measurement | J229-06-1QIT-003 - VK-6H-2 - Energy Meter 3-Phase Average | J229-06-1QIT-003_3PhaseAvg | J229-06-1QIT-003_3PhaseAvg | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 251 | J270-06-1PNL-001 | J229-06-1QIT-003 | Measurement | J229-06-1QIT-003 - VK-6H-2 - Energy Meter Voltage Phase A-B | J229-06-1QIT-003_VoltPhaseA_B | J229-06-1QIT-003_VoltPhaseA_B | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 252 | J270-06-1PNL-001 | J229-06-1QIT-003 | Measurement | J229-06-1QIT-003 - VK-6H-2 - Energy Meter Voltage Phase B-C | J229-06-1QIT-003_VoltPhaseB_C | J229-06-1QIT-003_VoltPhaseB_C | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 253 | J270-06-1PNL-001 | J229-06-1QIT-003 | Measurement | J229-06-1QIT-003 - VK-6H-2 - Energy Meter Voltage Phase C-A | J229-06-1QIT-003_VoltPhaseC_A | J229-06-1QIT-003_VoltPhaseC_A | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 254 | J270-06-1PNL-001 | J229-06-1QIT-003 | Measurement | J229-06-1QIT-003 - VK-6H-2 - Energy Meter L-L Average | J229-06-1QIT-003_LLAverage | J229-06-1QIT-003_LLAverage | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 255 | J270-06-1PNL-001 | J229-06-1QIT-003 | Measurement | J229-06-1QIT-003 - VK-6H-2 - Energy Meter L-N Average | J229-06-1QIT-003_LNAverage | J229-06-1QIT-003_LNAverage | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 256 | J270-06-1PNL-001 | J229-06-1QIT-003 | Measurement | J229-06-1QIT-003 - VK-6H-2 - Energy Meter Real Power | J229-06-1QIT-003_RealPower | J229-06-1QIT-003_RealPower | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 257 | J270-06-1PNL-001 | J229-06-1QIT-003 | Measurement | J229-06-1QIT-003 - VK-6H-2 - Energy Meter Reactive Power | J229-06-1QIT-003_ReactivePower | J229-06-1QIT-003_ReactivePower | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kVAr | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 258 | J270-06-1PNL-001 | J229-06-1QIT-003 | Measurement | J229-06-1QIT-003 - VK-6H-2 - Energy Meter Apparent Power | J229-06-1QIT-003_ApparentPower | J229-06-1QIT-003_ApparentPower | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kVAr | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 259 | J270-06-1PNL-001 | J229-06-1QIT-003 | Measurement | J229-06-1QIT-003 - VK-6H-2 - Energy Meter Frequency | J229-06-1QIT-003_Frequency | J229-06-1QIT-003_Frequency | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 260 | J270-06-1PNL-001 | J229-06-1QIT-004 | Measurement | J229-06-1QIT-004 - VK-6H-3 - Energy Meter Current Phase L1 | J229-06-1QIT-004_CurrPhase1 | J229-06-1QIT-004_CurrPhase1 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 261 | J270-06-1PNL-001 | J229-06-1QIT-004 | Measurement | J229-06-1QIT-004 - VK-6H-3 - Energy Meter Current Phase L2 | J229-06-1QIT-004_CurrPhase2 | J229-06-1QIT-004_CurrPhase2 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 262 | J270-06-1PNL-001 | J229-06-1QIT-004 | Measurement | J229-06-1QIT-004 - VK-6H-3 - Energy Meter Current Phase L3 | J229-06-1QIT-004_CurrPhase3 | J229-06-1QIT-004_CurrPhase3 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 263 | J270-06-1PNL-001 | J229-06-1QIT-004 | Measurement | J229-06-1QIT-004 - VK-6H-3 - Energy Meter 3-Phase Average | J229-06-1QIT-004_3PhaseAvg | J229-06-1QIT-004_3PhaseAvg | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 264 | J270-06-1PNL-001 | J229-06-1QIT-004 | Measurement | J229-06-1QIT-004 - VK-6H-3 - Energy Meter Voltage Phase A-B | J229-06-1QIT-004_VoltPhaseA_B | J229-06-1QIT-004_VoltPhaseA_B | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 265 | J270-06-1PNL-001 | J229-06-1QIT-004 | Measurement | J229-06-1QIT-004 - VK-6H-3 - Energy Meter Voltage Phase B-C | J229-06-1QIT-004_VoltPhaseB_C | J229-06-1QIT-004_VoltPhaseB_C | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 266 | J270-06-1PNL-001 | J229-06-1QIT-004 | Measurement | J229-06-1QIT-004 - VK-6H-3 - Energy Meter Voltage Phase C-A | J229-06-1QIT-004_VoltPhaseC_A | J229-06-1QIT-004_VoltPhaseC_A | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 267 | J270-06-1PNL-001 | J229-06-1QIT-004 | Measurement | J229-06-1QIT-004 - VK-6H-3 - Energy Meter L-L Average | J229-06-1QIT-004_LLAverage | J229-06-1QIT-004_LLAverage | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 268 | J270-06-1PNL-001 | J229-06-1QIT-004 | Measurement | J229-06-1QIT-004 - VK-6H-3 - Energy Meter L-N Average | J229-06-1QIT-004_LNAverage | J229-06-1QIT-004_LNAverage | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 269 | J270-06-1PNL-001 | J229-06-1QIT-004 | Measurement | J229-06-1QIT-004 - VK-6H-3 - Energy Meter Real Power | J229-06-1QIT-004_RealPower | J229-06-1QIT-004_RealPower | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 270 | J270-06-1PNL-001 | J229-06-1QIT-004 | Measurement | J229-06-1QIT-004 - VK-6H-3 - Energy Meter Reactive Power | J229-06-1QIT-004_ReactivePower | J229-06-1QIT-004_ReactivePower | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kVAr | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 271 | J270-06-1PNL-001 | J229-06-1QIT-004 | Measurement | J229-06-1QIT-004 - VK-6H-3 - Energy Meter Apparent Power | J229-06-1QIT-004_ApparentPower | J229-06-1QIT-004_ApparentPower | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kVAr | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 272 | J270-06-1PNL-001 | J229-06-1QIT-004 | Measurement | J229-06-1QIT-004 - VK-6H-3 - Energy Meter Frequency | J229-06-1QIT-004_Frequency | J229-06-1QIT-004_Frequency | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 273 | J270-06-1PNL-001 | J229-06-1QIT-005 | Measurement | J229-06-1QIT-005 - VK-6H-4 - Energy Meter Current Phase L1 | J229-06-1QIT-005_CurrPhase1 | J229-06-1QIT-005_CurrPhase1 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 274 | J270-06-1PNL-001 | J229-06-1QIT-005 | Measurement | J229-06-1QIT-005 - VK-6H-4 - Energy Meter Current Phase L2 | J229-06-1QIT-005_CurrPhase2 | J229-06-1QIT-005_CurrPhase2 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 275 | J270-06-1PNL-001 | J229-06-1QIT-005 | Measurement | J229-06-1QIT-005 - VK-6H-4 - Energy Meter Current Phase L3 | J229-06-1QIT-005_CurrPhase3 | J229-06-1QIT-005_CurrPhase3 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 276 | J270-06-1PNL-001 | J229-06-1QIT-005 | Measurement | J229-06-1QIT-005 - VK-6H-4 - Energy Meter 3-Phase Average | J229-06-1QIT-005_3PhaseAvg | J229-06-1QIT-005_3PhaseAvg | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 277 | J270-06-1PNL-001 | J229-06-1QIT-005 | Measurement | J229-06-1QIT-005 - VK-6H-4 - Energy Meter Voltage Phase A-B | J229-06-1QIT-005_VoltPhaseA_B | J229-06-1QIT-005_VoltPhaseA_B | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 278 | J270-06-1PNL-001 | J229-06-1QIT-005 | Measurement | J229-06-1QIT-005 - VK-6H-4 - Energy Meter Voltage Phase B-C | J229-06-1QIT-005_VoltPhaseB_C | J229-06-1QIT-005_VoltPhaseB_C | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 279 | J270-06-1PNL-001 | J229-06-1QIT-005 | Measurement | J229-06-1QIT-005 - VK-6H-4 - Energy Meter Voltage Phase C-A | J229-06-1QIT-005_VoltPhaseC_A | J229-06-1QIT-005_VoltPhaseC_A | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 280 | J270-06-1PNL-001 | J229-06-1QIT-005 | Measurement | J229-06-1QIT-005 - VK-6H-4 - Energy Meter L-L Average | J229-06-1QIT-005_LLAverage | J229-06-1QIT-005_LLAverage | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 281 | J270-06-1PNL-001 | J229-06-1QIT-005 | Measurement | J229-06-1QIT-005 - VK-6H-4 - Energy Meter L-N Average | J229-06-1QIT-005_LNAverage | J229-06-1QIT-005_LNAverage | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 282 | J270-06-1PNL-001 | J229-06-1QIT-005 | Measurement | J229-06-1QIT-005 - VK-6H-4 - Energy Meter Real Power | J229-06-1QIT-005_RealPower | J229-06-1QIT-005_RealPower | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 283 | J270-06-1PNL-001 | J229-06-1QIT-005 | Measurement | J229-06-1QIT-005 - VK-6H-4 - Energy Meter Reactive Power | J229-06-1QIT-005_ReactivePower | J229-06-1QIT-005_ReactivePower | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kVAr | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 284 | J270-06-1PNL-001 | J229-06-1QIT-005 | Measurement | J229-06-1QIT-005 - VK-6H-4 - Energy Meter Apparent Power | J229-06-1QIT-005_ApparentPower | J229-06-1QIT-005_ApparentPower | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kVAr | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 285 | J270-06-1PNL-001 | J229-06-1QIT-005 | Measurement | J229-06-1QIT-005 - VK-6H-4 - Energy Meter Frequency | J229-06-1QIT-005_Frequency | J229-06-1QIT-005_Frequency | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 286 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Outpower Phase 1 | J232-06-1UPS-001_OutPower0 | J232-06-1UPS-001_OutPower0 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 287 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Outpower Phase 2 | J232-06-1UPS-001_OutPower1 | J232-06-1UPS-001_OutPower1 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 288 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Outpower Phase 3 | J232-06-1UPS-001_OutPower2 | J232-06-1UPS-001_OutPower2 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 289 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Battery Capacity | J232-06-1UPS-001_Battcap | J232-06-1UPS-001_Battcap | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 290 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Temperature | J232-06-1UPS-001_Temp | J232-06-1UPS-001_Temp | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 291 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Autonomy Time | J232-06-1UPS-001_Autonomtime | J232-06-1UPS-001_Autonomtime | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 292 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor UPS MDF Room Status | J232-06-1UPS-001_Status | J232-06-1UPS-001_Status | NORMAL | BYPMODE | SHUTDOWN | UPSOK | BCKMODE | BATTLOW | OVRTEMP | TSTACTV | INHIGH | OUTHIGH | INVFAIL | BATTBAD | ECOMODE | INVWARN | UPSFAIL | COMMLOST | DVGALM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 293 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Battery Voltage | J232-06-1UPS-001_BattVolt | J232-06-1UPS-001_BattVolt | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 294 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Powerfail Counter | J232-06-1UPS-001_CNT_PF | J232-06-1UPS-001_CNT_PF | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 295 | J270-06-1PNL-001 | J232-06-1UPS-001 | Alarm | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Alarm | J232-06-1UPS-001_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J232-06-1UPS-001_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 296 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Output Voltage Phase 1 | J232-06-1UPS-001_OutVolt0 | J232-06-1UPS-001_OutVolt0 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 297 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Output Voltage Phase 2 | J232-06-1UPS-001_OutVolt1 | J232-06-1UPS-001_OutVolt1 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 298 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Output Voltage Phase 3 | J232-06-1UPS-001_OutVolt2 | J232-06-1UPS-001_OutVolt2 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 299 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Output Current Phase 1 | J232-06-1UPS-001_OutCurrent0 | J232-06-1UPS-001_OutCurrent0 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 300 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Output Current Phase 2 | J232-06-1UPS-001_OutCurrent1 | J232-06-1UPS-001_OutCurrent1 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 301 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Output Current Phase 3 | J232-06-1UPS-001_OutCurrent2 | J232-06-1UPS-001_OutCurrent2 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 302 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor True Output Power Phase 1 | J232-06-1UPS-001_TrueOutPower0 | J232-06-1UPS-001_TrueOutPower0 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 303 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor True Output Power Phase 2 | J232-06-1UPS-001_TrueOutPower1 | J232-06-1UPS-001_TrueOutPower1 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 304 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor True Output Power Phase 3 | J232-06-1UPS-001_TrueOutPower2 | J232-06-1UPS-001_TrueOutPower2 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 305 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Battery Current | J232-06-1UPS-001_BattCurrent | J232-06-1UPS-001_BattCurrent | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 306 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Output Frequency Phase 1 | J232-06-1UPS-001_OutFreq0 | J232-06-1UPS-001_OutFreq0 | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 307 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Battery Condition | J232-06-1UPS-001_BattCond | J232-06-1UPS-001_BattCond | GOOD | WEAK | REPLACE | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 308 | J270-06-1PNL-001 | J460-01-2FCV-001 | Alarm | J460-01-2FCV-001 - Chilled Water Valve - Controller - Communication Failure Alarm | J460-01-2FCV-001_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-001_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 309 | J270-06-1PNL-001 | J460-01-2FCV-001 | Measurement | J460-01-2FCV-001 - Chilled Water Valve - Forced Position | J460-01-2FCV-001_ForcePos | J460-01-2FCV-001_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 310 | J270-06-1PNL-001 | J460-01-2FCV-001 | Setting | J460-01-2FCV-001 - Chilled Water Valve - Forced Calibration | J460-01-2FCV-001_ForceCal | J460-01-2FCV-001_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 311 | J270-06-1PNL-001 | J460-01-2FCV-001 | Measurement | J460-01-2FCV-001 - Chilled Water Valve - Status | J460-01-2FCV-001_MotState | J460-01-2FCV-001_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 312 | J270-06-1PNL-001 | J460-01-2FCV-001 | Measurement | J460-01-2FCV-001 - Chilled Water Valve - Actual SP | J460-01-2FCV-001_ActSP | J460-01-2FCV-001_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 313 | J270-06-1PNL-001 | J460-01-2FCV-001 | Setting | J460-01-2FCV-001 - Chilled Water Valve - SP | J460-01-2FCV-001_SP | J460-01-2FCV-001_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 314 | J270-06-1PNL-001 | J460-01-2FCV-001 | Alarm | J460-01-2FCV-001 - Chilled Water Valve - Controller Fail to Open Alarm | J460-01-2FCV-001_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-001_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 315 | J270-06-1PNL-001 | J460-01-2FCV-001 | Alarm | J460-01-2FCV-001 - Chilled Water Valve - Controller Fail to Close Alarm | J460-01-2FCV-001_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-001_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 316 | J270-06-1PNL-001 | J460-01-2FCV-001 | Measurement | J460-01-2FCV-001 - Chilled Water Valve - Error Code | J460-01-2FCV-001_Err | J460-01-2FCV-001_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 317 | J270-06-1PNL-001 | J460-01-1PMP-001 | Alarm | J460-01-1PMP-001 - Chilled Water Circulation Pump - Controller - Communication Failure Alarm | J460-01-1PMP-001_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1PMP-001_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 318 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - Error Code | J460-01-1PMP-001_ErrCode | J460-01-1PMP-001_ErrCode | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 319 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - Speed | J460-01-1PMP-001_Spd | J460-01-1PMP-001_Spd | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | rpm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 320 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - Frequency | J460-01-1PMP-001_Frq | J460-01-1PMP-001_Frq | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 321 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - Motor Current | J460-01-1PMP-001_MtrCur | J460-01-1PMP-001_MtrCur | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 322 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - DC Link Voltage | J460-01-1PMP-001_DCVolt | J460-01-1PMP-001_DCVolt | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 323 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - Power | J460-01-1PMP-001_Pwr | J460-01-1PMP-001_Pwr | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | W | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 324 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - Run Time | J460-01-1PMP-001_RunTime | J460-01-1PMP-001_RunTime | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 325 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - Load Percentage | J460-01-1PMP-001_LdPerc | J460-01-1PMP-001_LdPerc | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 326 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - Control Source | J460-01-1PMP-001_CntSrc | J460-01-1PMP-001_CntSrc | LOCCNT | BUSCNT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 327 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - Rotation Status | J460-01-1PMP-001_Rot | J460-01-1PMP-001_Rot | NOROT | ROT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 328 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - Actual Operation Mode | J460-01-1PMP-001_ActOpMode | J460-01-1PMP-001_ActOpMode | - | START | STOP | MINIMUM | MAXIMUM | USERDEF | LOCMODE | EMGMODE | HANDMODE | UNKNOWN | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 329 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - Operation Mode | J460-01-1PMP-001_OpMode | J460-01-1PMP-001_OpMode | - | START | STOP | MINIMUM | MAXIMUM | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1.0 | 330 | J270-06-1PNL-001 | J460-02-2FCV-624 | Alarm | J460-02-2FCV-624 - Chilled Water Valve - Controller - Communication Failure Alarm | J460-02-2FCV-624_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-624_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 331 | J270-06-1PNL-001 | J460-02-2FCV-624 | Measurement | J460-02-2FCV-624 - Chilled Water Valve - Forced Position | J460-02-2FCV-624_ForcePos | J460-02-2FCV-624_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 332 | J270-06-1PNL-001 | J460-02-2FCV-624 | Setting | J460-02-2FCV-624 - Chilled Water Valve - Forced Calibration | J460-02-2FCV-624_ForceCal | J460-02-2FCV-624_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 333 | J270-06-1PNL-001 | J460-02-2FCV-624 | Measurement | J460-02-2FCV-624 - Chilled Water Valve - Status | J460-02-2FCV-624_MotState | J460-02-2FCV-624_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 334 | J270-06-1PNL-001 | J460-02-2FCV-624 | Measurement | J460-02-2FCV-624 - Chilled Water Valve - Actual SP | J460-02-2FCV-624_ActSP | J460-02-2FCV-624_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 335 | J270-06-1PNL-001 | J460-02-2FCV-624 | Setting | J460-02-2FCV-624 - Chilled Water Valve - SP | J460-02-2FCV-624_SP | J460-02-2FCV-624_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 336 | J270-06-1PNL-001 | J460-02-2FCV-624 | Alarm | J460-02-2FCV-624 - Chilled Water Valve - Controller Fail to Open Alarm | J460-02-2FCV-624_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-624_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 337 | J270-06-1PNL-001 | J460-02-2FCV-624 | Alarm | J460-02-2FCV-624 - Chilled Water Valve - Controller Fail to Close Alarm | J460-02-2FCV-624_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-624_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 338 | J270-06-1PNL-001 | J460-02-2FCV-624 | Measurement | J460-02-2FCV-624 - Chilled Water Valve - Error Code | J460-02-2FCV-624_Err | J460-02-2FCV-624_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 339 | J270-06-1PNL-001 | J460-02-1PMP-601 | Alarm | J460-02-1PMP-601 - Chilled Water Circulation Pump - Controller - Communication Failure Alarm | J460-02-1PMP-601_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1PMP-601_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 340 | J270-06-1PNL-001 | J460-02-1PMP-601 | Measurement | J460-02-1PMP-601 - Chilled Water Circulation Pump - Error Code | J460-02-1PMP-601_ErrCode | J460-02-1PMP-601_ErrCode | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 341 | J270-06-1PNL-001 | J460-02-1PMP-601 | Measurement | J460-02-1PMP-601 - Chilled Water Circulation Pump - Speed | J460-02-1PMP-601_Spd | J460-02-1PMP-601_Spd | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | rpm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 342 | J270-06-1PNL-001 | J460-02-1PMP-601 | Measurement | J460-02-1PMP-601 - Chilled Water Circulation Pump - Frequency | J460-02-1PMP-601_Frq | J460-02-1PMP-601_Frq | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 343 | J270-06-1PNL-001 | J460-02-1PMP-601 | Measurement | J460-02-1PMP-601 - Chilled Water Circulation Pump - Motor Current | J460-02-1PMP-601_MtrCur | J460-02-1PMP-601_MtrCur | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 344 | J270-06-1PNL-001 | J460-02-1PMP-601 | Measurement | J460-02-1PMP-601 - Chilled Water Circulation Pump - DC Link Voltage | J460-02-1PMP-601_DCVolt | J460-02-1PMP-601_DCVolt | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 345 | J270-06-1PNL-001 | J460-02-1PMP-601 | Measurement | J460-02-1PMP-601 - Chilled Water Circulation Pump - Power | J460-02-1PMP-601_Pwr | J460-02-1PMP-601_Pwr | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | W | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 346 | J270-06-1PNL-001 | J460-02-1PMP-601 | Measurement | J460-02-1PMP-601 - Chilled Water Circulation Pump - Run Time | J460-02-1PMP-601_RunTime | J460-02-1PMP-601_RunTime | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 347 | J270-06-1PNL-001 | J460-02-1PMP-601 | Measurement | J460-02-1PMP-601 - Chilled Water Circulation Pump - Load Percentage | J460-02-1PMP-601_LdPerc | J460-02-1PMP-601_LdPerc | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 348 | J270-06-1PNL-001 | J460-02-1PMP-601 | Measurement | J460-02-1PMP-601 - Chilled Water Circulation Pump - Control Source | J460-02-1PMP-601_CntSrc | J460-02-1PMP-601_CntSrc | LOCCNT | BUSCNT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 349 | J270-06-1PNL-001 | J460-02-1PMP-601 | Measurement | J460-02-1PMP-601 - Chilled Water Circulation Pump - Rotation Status | J460-02-1PMP-601_Rot | J460-02-1PMP-601_Rot | NOROT | ROT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 350 | J270-06-1PNL-001 | J460-02-1PMP-601 | Measurement | J460-02-1PMP-601 - Chilled Water Circulation Pump - Actual Operation Mode | J460-02-1PMP-601_ActOpMode | J460-02-1PMP-601_ActOpMode | - | START | STOP | MINIMUM | MAXIMUM | USERDEF | LOCMODE | EMGMODE | HANDMODE | UNKNOWN | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 351 | J270-06-1PNL-001 | J460-02-1PMP-601 | Measurement | J460-02-1PMP-601 - Chilled Water Circulation Pump - Operation Mode | J460-02-1PMP-601_OpMode | J460-02-1PMP-601_OpMode | - | START | STOP | MINIMUM | MAXIMUM | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1.0 | 352 | J229-06-1PNL-001 | J229-06-2XA-101 | Measurement | J229-06-2XA-101 - SVK-6H - Circuit Breaker Tripped | J229-06-2XA-101_CirBrkTrip | J229-06-2XA-101_CirBrkTrip | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 353 | J229-06-1PNL-001 | J229-06-2XA-101 | Alarm | J229-06-2XA-101 - SVK-6H - Circuit Breaker Tripped Alarm | J229-06-2XA-101_CirBrkTrip_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J229-06-2XA-101_CirBrkTrip_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 354 | J229-06-1PNL-001 | J229-06-2XA-102 | Measurement | J229-06-2XA-102 - SVK-6H - Voltage Surge Arrestor | J229-06-2XA-102_SurgeVoltArr | J229-06-2XA-102_SurgeVoltArr | NORMAL | FAULT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 355 | J229-06-1PNL-001 | J229-06-2XA-102 | Alarm | J229-06-2XA-102 - SVK-6H - Voltage Surge Arrestor Alarm | J229-06-2XA-102_SurgeVoltArr_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J229-06-2XA-102_SurgeVoltArr_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 356 | J229-06-1PNL-001 | J229-06-2XA-103 | Measurement | J229-06-2XA-103 - VK-6H-1 - Circuit Breaker Tripped | J229-06-2XA-103_CirBrkTrip | J229-06-2XA-103_CirBrkTrip | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 357 | J229-06-1PNL-001 | J229-06-2XA-103 | Alarm | J229-06-2XA-103 - VK-6H-1 - Circuit Breaker Tripped Alarm | J229-06-2XA-103_CirBrkTrip_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J229-06-2XA-103_CirBrkTrip_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 358 | J229-06-1PNL-001 | J229-06-2XA-104 | Measurement | J229-06-2XA-104 - VK-6H-1 - Voltage Surge Arrestor | J229-06-2XA-104_SurgeVoltArr | J229-06-2XA-104_SurgeVoltArr | NORMAL | FAULT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 359 | J229-06-1PNL-001 | J229-06-2XA-104 | Alarm | J229-06-2XA-104 - VK-6H-1 - Voltage Surge Arrestor Alarm | J229-06-2XA-104_SurgeVoltArr_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J229-06-2XA-104_SurgeVoltArr_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 360 | J229-06-1PNL-001 | J229-06-2XA-105 | Measurement | J229-06-2XA-105 - VK-6H-2 - Circuit Breaker Tripped | J229-06-2XA-105_CirBrkTrip | J229-06-2XA-105_CirBrkTrip | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 361 | J229-06-1PNL-001 | J229-06-2XA-105 | Alarm | J229-06-2XA-105 - VK-6H-2 - Circuit Breaker Tripped Alarm | J229-06-2XA-105_CirBrkTrip_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J229-06-2XA-105_CirBrkTrip_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 362 | J229-06-1PNL-001 | J229-06-2XA-106 | Measurement | J229-06-2XA-106 - VK-6H-2 - Voltage Surge Arrestor | J229-06-2XA-106_SurgeVoltArr | J229-06-2XA-106_SurgeVoltArr | NORMAL | FAULT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 363 | J229-06-1PNL-001 | J229-06-2XA-106 | Alarm | J229-06-2XA-106 - VK-6H-2 - Voltage Surge Arrestor Alarm | J229-06-2XA-106_SurgeVoltArr_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J229-06-2XA-106_SurgeVoltArr_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 364 | J229-06-1PNL-001 | J229-06-2XA-107 | Measurement | J229-06-2XA-107 - VK-6H-3 - Circuit Breaker Tripped | J229-06-2XA-107_CirBrkTrip | J229-06-2XA-107_CirBrkTrip | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 365 | J229-06-1PNL-001 | J229-06-2XA-107 | Alarm | J229-06-2XA-107 - VK-6H-3 - Circuit Breaker Tripped Alarm | J229-06-2XA-107_CirBrkTrip_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J229-06-2XA-107_CirBrkTrip_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 366 | J229-06-1PNL-001 | J229-06-2XA-108 | Measurement | J229-06-2XA-108 - VK-6H-3 - Voltage Surge Arrestor | J229-06-2XA-108_SurgeVoltArr | J229-06-2XA-108_SurgeVoltArr | NORMAL | FAULT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 367 | J229-06-1PNL-001 | J229-06-2XA-108 | Alarm | J229-06-2XA-108 - VK-6H-3 - Voltage Surge Arrestor Alarm | J229-06-2XA-108_SurgeVoltArr_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J229-06-2XA-108_SurgeVoltArr_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 368 | J229-06-1PNL-001 | J229-06-2XA-109 | Measurement | J229-06-2XA-109 - VK-6H-4 - Circuit Breaker Tripped | J229-06-2XA-109_CirBrkTrip | J229-06-2XA-109_CirBrkTrip | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 369 | J229-06-1PNL-001 | J229-06-2XA-109 | Alarm | J229-06-2XA-109 - VK-6H-4 - Circuit Breaker Tripped Alarm | J229-06-2XA-109_CirBrkTrip_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J229-06-2XA-109_CirBrkTrip_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 370 | J229-06-1PNL-001 | J229-06-2XA-110 | Measurement | J229-06-2XA-110 - VK-6H-4 - Voltage Surge Arrestor | J229-06-2XA-110_SurgeVoltArr | J229-06-2XA-110_SurgeVoltArr | NORMAL | FAULT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 371 | J229-06-1PNL-001 | J229-06-2XA-110 | Alarm | J229-06-2XA-110 - VK-6H-4 - Voltage Surge Arrestor Alarm | J229-06-2XA-110_SurgeVoltArr_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J229-06-2XA-110_SurgeVoltArr_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 372 | J270-06-1PNL-001 | J229-06-2XA-111 | Measurement | J229-06-2XA-111 - VK-UPS-6H-5 - Circuit Breaker Tripped | J229-06-2XA-111_CirBrkTrip | J229-06-2XA-111_CirBrkTrip | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 373 | J270-06-1PNL-001 | J229-06-2XA-111 | Alarm | J229-06-2XA-111 - VK-UPS-6H-5 - Circuit Breaker Tripped Alarm | J229-06-2XA-111_CirBrkTrip_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J229-06-2XA-111_CirBrkTrip_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 374 | J270-06-1PNL-001 | J229-06-2XA-112 | Measurement | J229-06-2XA-112 - VK-UPS-6H-5 - Voltage Surge Arrestor | J229-06-2XA-112_SurgeVoltArr | J229-06-2XA-112_SurgeVoltArr | NORMAL | FAULT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 375 | J270-06-1PNL-001 | J229-06-2XA-112 | Alarm | J229-06-2XA-112 - VK-UPS-6H-5 - Voltage Surge Arrestor Alarm | J229-06-2XA-112_SurgeVoltArr_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J229-06-2XA-112_SurgeVoltArr_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 376 | J270-06-1PNL-001 | J460-02-2FT-601 | Measurement | J460-02-2FT-601 - 61LBK2 - Supply Air Flow | J460-02-2FT-601_SupAirFlow | J460-02-2FT-601_SupAirFlow | 0 | 21690 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 377 | J270-06-1PNL-001 | J460-02-2FT-601 | Measurement | J460-02-2FT-601 - 61LBK2 - Supply Air Flow Field | J460-02-2FT-601_SupAirFlow_Field | J460-02-2FT-601_SupAirFlow_Field | 0 | 21690 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 378 | J270-06-1PNL-001 | J460-02-2FT-601 | Alarm | J460-02-2FT-601 - 61LBK2 - Supply Air Flow High Alarm | J460-02-2FT-601_SupAirFlowHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FT-601_SupAirFlowHiAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 379 | J270-06-1PNL-001 | J460-02-2FT-601 | Setting | J460-02-2FT-601 - 61LBK2 - Supply Air Flow | J460-02-2FT-601_SupAirFlow_HASP | J460-02-2FT-601_SupAirFlow_HASP | - | 15100 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 380 | J270-06-1PNL-001 | J460-02-2FT-601 | Alarm | J460-02-2FT-601 - 61LBK2 - Supply Air Flow Low Alarm | J460-02-2FT-601_SupAirFlowLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FT-601_SupAirFlowLoAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 381 | J270-06-1PNL-001 | J460-02-2FT-601 | Setting | J460-02-2FT-601 - 61LBK2 - Supply Air Flow | J460-02-2FT-601_SupAirFlow_LASP | J460-02-2FT-601_SupAirFlow_LASP | 13660 | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 382 | J270-06-1PNL-001 | J460-02-2FT-601 | Setting | J460-02-2FT-601 - 61LBK2 - Supply Air Flow Calibration Mode Selection | J460-02-2FT-601_SupAirFlowCalModeSel | J460-02-2FT-601_SupAirFlowCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 383 | J270-06-1PNL-001 | J460-02-2FT-601 | Alarm | J460-02-2FT-601 - 61LBK2 - Supply Air Flow Calibration Still Active Alarm | J460-02-2FT-601_SupAirFlowCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FT-601_SupAirFlowCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 384 | J270-06-1PNL-001 | J460-02-2FT-602 | Measurement | J460-02-2FT-602 - 61LBK2 - Return Air Flow | J460-02-2FT-602_RetAirFlow | J460-02-2FT-602_RetAirFlow | 0 | 21690 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 385 | J270-06-1PNL-001 | J460-02-2FT-602 | Measurement | J460-02-2FT-602 - 61LBK2 - Return Air Flow Field | J460-02-2FT-602_RetAirFlow_Field | J460-02-2FT-602_RetAirFlow_Field | 0 | 21690 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 386 | J270-06-1PNL-001 | J460-02-2FT-602 | Alarm | J460-02-2FT-602 - 61LBK2 - Return Air Flow High Alarm | J460-02-2FT-602_RetAirFlowHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FT-602_RetAirFlowHiAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 387 | J270-06-1PNL-001 | J460-02-2FT-602 | Setting | J460-02-2FT-602 - 61LBK2 - Return Air Flow | J460-02-2FT-602_RetAirFlow_HASP | J460-02-2FT-602_RetAirFlow_HASP | - | 13880 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 388 | J270-06-1PNL-001 | J460-02-2FT-602 | Alarm | J460-02-2FT-602 - 61LBK2 - Return Air Flow Low Alarm | J460-02-2FT-602_RetAirFlowLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FT-602_RetAirFlowLoAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 389 | J270-06-1PNL-001 | J460-02-2FT-602 | Setting | J460-02-2FT-602 - 61LBK2 - Return Air Flow | J460-02-2FT-602_RetAirFlow_LASP | J460-02-2FT-602_RetAirFlow_LASP | 12560 | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 390 | J270-06-1PNL-001 | J460-02-2FT-602 | Setting | J460-02-2FT-602 - 61LBK2 - Return Air Flow Calibration Mode Selection | J460-02-2FT-602_RetAirFlowCalModeSel | J460-02-2FT-602_RetAirFlowCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 391 | J270-06-1PNL-001 | J460-02-2FT-602 | Alarm | J460-02-2FT-602 - 61LBK2 - Return Air Flow Calibration Still Active Alarm | J460-02-2FT-602_RetAirFlowCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FT-602_RetAirFlowCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 392 | J270-06-1PNL-001 | J460-02-2TT-607 | Measurement | J460-02-2TT-607 - 61LBK2 - Supply Air Temperature | J460-02-2TT-607_SupAirTemp | J460-02-2TT-607_SupAirTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 393 | J270-06-1PNL-001 | J460-02-2TT-607 | Measurement | J460-02-2TT-607 - 61LBK2 - Supply Air Temperature Field | J460-02-2TT-607_SupAirTemp_Field | J460-02-2TT-607_SupAirTemp_Field | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 394 | J270-06-1PNL-001 | J460-02-2TT-607 | Alarm | J460-02-2TT-607 - 61LBK2 - Supply Air Temperature High Alarm | J460-02-2TT-607_SupAirTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-607_SupAirTempHiAlm | 1 | Y | - | bar: State 2 to State 64
2.1 | 395 | J270-06-1PNL-001 | J460-02-2TT-607 | Setting | J460-02-2TT-607 - 61LBK2 - Supply Air Temperature | J460-02-2TT-607_SupAirTemp_HASP | J460-02-2TT-607_SupAirTemp_HASP | - | 21 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 396 | J270-06-1PNL-001 | J460-02-2TT-607 | Alarm | J460-02-2TT-607 - 61LBK2 - Supply Air Temperature Low Alarm | J460-02-2TT-607_SupAirTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-607_SupAirTempLoAlm | 1 | Y | - | bar: State 2 to State 64
2.1 | 397 | J270-06-1PNL-001 | J460-02-2TT-607 | Setting | J460-02-2TT-607 - 61LBK2 - Supply Air Temperature | J460-02-2TT-607_SupAirTemp_LASP | J460-02-2TT-607_SupAirTemp_LASP | 15 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 398 | J270-06-1PNL-001 | J460-02-2TT-607 | Setting | J460-02-2TT-607 - 61LBK2 - Supply Air Temperature Calibration Mode Selection | J460-02-2TT-607_SupAirTempCalModeSel | J460-02-2TT-607_SupAirTempCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 399 | J270-06-1PNL-001 | J460-02-2TT-607 | Alarm | J460-02-2TT-607 - 61LBK2 - Supply Air Temperature Calibration Still Active Alarm | J460-02-2TT-607_SupAirTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-607_SupAirTempCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 400 | J270-06-1PNL-001 | J460-02-2TT-608 | Measurement | J460-02-2TT-608 - 61LBK2 - Return Air Temperature | J460-02-2TT-608_RetAirTemp | J460-02-2TT-608_RetAirTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 401 | J270-06-1PNL-001 | J460-02-2TT-608 | Measurement | J460-02-2TT-608 - 61LBK2 - Return Air Temperature Field | J460-02-2TT-608_RetAirTemp_Field | J460-02-2TT-608_RetAirTemp_Field | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 402 | J270-06-1PNL-001 | J460-02-2TT-608 | Alarm | J460-02-2TT-608 - 61LBK2 - Return Air Temperature High Alarm | J460-02-2TT-608_RetAirTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-608_RetAirTempHiAlm | 1 | Y | - | bar: State 2 to State 64
2.1 | 403 | J270-06-1PNL-001 | J460-02-2TT-608 | Setting | J460-02-2TT-608 - 61LBK2 - Return Air Temperature | J460-02-2TT-608_RetAirTemp_HASP | J460-02-2TT-608_RetAirTemp_HASP | - | 26 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 404 | J270-06-1PNL-001 | J460-02-2TT-608 | Alarm | J460-02-2TT-608 - 61LBK2 - Return Air Temperature Low Alarm | J460-02-2TT-608_RetAirTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-608_RetAirTempLoAlm | 1 | Y | - | bar: State 2 to State 64
2.1 | 405 | J270-06-1PNL-001 | J460-02-2TT-608 | Setting | J460-02-2TT-608 - 61LBK2 - Return Air Temperature | J460-02-2TT-608_RetAirTemp_LASP | J460-02-2TT-608_RetAirTemp_LASP | 18 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 406 | J270-06-1PNL-001 | J460-02-2TT-608 | Setting | J460-02-2TT-608 - 61LBK2 - Return Air Temperature Calibration Mode Selection | J460-02-2TT-608_RetAirTempCalModeSel | J460-02-2TT-608_RetAirTempCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 407 | J270-06-1PNL-001 | J460-02-2TT-608 | Alarm | J460-02-2TT-608 - 61LBK2 - Return Air Temperature Calibration Still Active Alarm | J460-02-2TT-608_RetAirTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-608_RetAirTempCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 408 | J270-06-1PNL-001 | J460-02-2MT-607 | Measurement | J460-02-2MT-607 - 61LBK2 - Supply Air Humidity | J460-02-2MT-607_SupAirHum | J460-02-2MT-607_SupAirHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 409 | J270-06-1PNL-001 | J460-02-2MT-607 | Measurement | J460-02-2MT-607 - 61LBK2 - Supply Air Humidity Field | J460-02-2MT-607_SupAirHum_Field | J460-02-2MT-607_SupAirHum_Field | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 410 | J270-06-1PNL-001 | J460-02-2MT-607 | Alarm | J460-02-2MT-607 - 61LBK2 - Supply Air Humidity High Alarm | J460-02-2MT-607_SupAirHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-607_SupAirHumHiAlm | 1 | Y | - | bar: State 2 to State 64
2.1 | 411 | J270-06-1PNL-001 | J460-02-2MT-607 | Setting | J460-02-2MT-607 - 61LBK2 - Supply Air Humidity | J460-02-2MT-607_SupAirHum_HASP | J460-02-2MT-607_SupAirHum_HASP | - | 80 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 412 | J270-06-1PNL-001 | J460-02-2MT-607 | Alarm | J460-02-2MT-607 - 61LBK2 - Supply Air Humidity Low Alarm | J460-02-2MT-607_SupAirHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-607_SupAirHumLoAlm | 1 | Y | - | bar: State 2 to State 64
2.1 | 413 | J270-06-1PNL-001 | J460-02-2MT-607 | Setting | J460-02-2MT-607 - 61LBK2 - Supply Air Humidity | J460-02-2MT-607_SupAirHum_LASP | J460-02-2MT-607_SupAirHum_LASP | 30 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 414 | J270-06-1PNL-001 | J460-02-2MT-607 | Setting | J460-02-2MT-607 - 61LBK2 - Supply Air Humidity Calibration Mode Selection | J460-02-2MT-607_SupAirHumCalModeSel | J460-02-2MT-607_SupAirHumCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 415 | J270-06-1PNL-001 | J460-02-2MT-607 | Alarm | J460-02-2MT-607 - 61LBK2 - Supply Air Humidity Calibration Still Active Alarm | J460-02-2MT-607_SupAirHumCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-607_SupAirHumCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 416 | J270-06-1PNL-001 | J460-02-2KS-603 | Measurement | J460-02-2KS-603 - Labs Day Extention Timer - Timer | J460-02-2KS-603_DET | J460-02-2KS-603_DET | OFF | ON | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 417 | J270-06-1PNL-001 | J460-02-2XI-603 | Setting | J460-02-2XI-603 - Labs Day Extention Timer - Indicator | J460-02-2XI-603_DETLamp | J460-02-2XI-603_DETLamp | OFF | ON | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 418 | J270-06-1PNL-001 | J460-02-2XS-603 | Setting | J460-02-2XS-603 - Labs Day Extention Timer - Enable | J460-02-2XS-603_DETEna | J460-02-2XS-603_DETEna | DISABLE | ENABLE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 419 | J270-06-1PNL-001 | J460-01-2TT-002 | Measurement | J460-01-2TT-002 - Chilled Water - Supply Temperature | J460-01-2TT-002_ChlWtrSupTemp | J460-01-2TT-002_ChlWtrSupTemp | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 420 | J270-06-1PNL-001 | J460-01-2TT-002 | Measurement | J460-01-2TT-002 - Chilled Water - Supply Temperature Field | J460-01-2TT-002_ChlWtrSupTemp_Field | J460-01-2TT-002_ChlWtrSupTemp_Field | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 421 | J270-06-1PNL-001 | J460-01-2TT-002 | Alarm | J460-01-2TT-002 - Chilled Water - Supply Temperature High Alarm | J460-01-2TT-002_ChlWtrSupTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-002_ChlWtrSupTempHiAlm | 2 | Y | - | bar: State 2 to State 64
2.1 | 422 | J270-06-1PNL-001 | J460-01-2TT-002 | Setting | J460-01-2TT-002 - Chilled Water - Supply Temperature | J460-01-2TT-002_ChlWtrSupTemp_HASP | J460-01-2TT-002_ChlWtrSupTemp_HASP | - | 16 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 423 | J270-06-1PNL-001 | J460-01-2TT-002 | Alarm | J460-01-2TT-002 - Chilled Water - Supply Temperature Low Alarm | J460-01-2TT-002_ChlWtrSupTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-002_ChlWtrSupTempLoAlm | 2 | Y | - | bar: State 2 to State 64
2.1 | 424 | J270-06-1PNL-001 | J460-01-2TT-002 | Setting | J460-01-2TT-002 - Chilled Water - Supply Temperature | J460-01-2TT-002_ChlWtrSupTemp_LASP | J460-01-2TT-002_ChlWtrSupTemp_LASP | 6 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 425 | J270-06-1PNL-001 | J460-01-2TT-002 | Setting | J460-01-2TT-002 - Chilled Water - Supply Temperature Calibration Mode Selection | J460-01-2TT-002_ChlWtrSupTempCalModeSel | J460-01-2TT-002_ChlWtrSupTempCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 426 | J270-06-1PNL-001 | J460-01-2TT-002 | Alarm | J460-01-2TT-002 - Chilled Water - Supply Temperature Calibration Still Active Alarm | J460-01-2TT-002_ChlWtrSupTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-002_ChlWtrSupTempCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 427 | J270-06-1PNL-001 | J460-01-2TT-002 | Setting | J460-01-2TT-002 - Chilled Water - Supply Temperature Setpoint | J460-01-2TT-002_ChlWtrSupTempSetpoint | J460-01-2TT-002_ChlWtrSupTempSetpoint | 16 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 428 | J270-06-1PNL-001 | N/A | Calculated | BMS Ground Floor Office Room Dew Point Temperature Setpoint | J460-01-2TT-002_OffcDewPtTempSetpoint | J460-01-2TT-002_OffcDewPtTempSetpoint | Calculated | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 429 | J270-06-1PNL-001 | N/A | Setting | BMS Ground Floor Office Room Dew Point Temperature Setpoint Offset | J460-01-2TT-002_OffcDewPtTempSPOffset | J460-01-2TT-002_OffcDewPtTempSPOffset | 1 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 430 | J270-06-1PNL-001 | J460-01-2TT-002 | Setting | J460-01-2TT-002 - Chilled Water - Supply Temperature Proportional Band | J460-01-2TT-002_ChlWtrSupTemp_Set_P | J460-01-2TT-002_ChlWtrSupTemp_Set_P | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 431 | J270-06-1PNL-001 | J460-01-2TT-002 | Setting | J460-01-2TT-002 - Chilled Water - Supply Temperature Integral Time | J460-01-2TT-002_ChlWtrSupTemp_Set_I | J460-01-2TT-002_ChlWtrSupTemp_Set_I | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 432 | J270-06-1PNL-001 | J460-01-2TT-002 | Setting | J460-01-2TT-002 - Chilled Water - Supply Temperature Derivative Time | J460-01-2TT-002_ChlWtrSupTemp_Set_D | J460-01-2TT-002_ChlWtrSupTemp_Set_D | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 433 | J270-06-1PNL-001 | J460-01-2TT-003 | Measurement | J460-01-2TT-003 - Chilled Water - Return Temperature | J460-01-2TT-003_ChlWtrRetTemp | J460-01-2TT-003_ChlWtrRetTemp | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 434 | J270-06-1PNL-001 | J460-01-2TT-003 | Measurement | J460-01-2TT-003 - Chilled Water - Return Temperature Field | J460-01-2TT-003_ChlWtrRetTemp_Field | J460-01-2TT-003_ChlWtrRetTemp_Field | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 435 | J270-06-1PNL-001 | J460-01-2TT-003 | Alarm | J460-01-2TT-003 - Chilled Water - Return Temperature High Alarm | J460-01-2TT-003_ChlWtrRetTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-003_ChlWtrRetTempHiAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 436 | J270-06-1PNL-001 | J460-01-2TT-003 | Setting | J460-01-2TT-003 - Chilled Water - Return Temperature | J460-01-2TT-003_ChlWtrRetTemp_HASP | J460-01-2TT-003_ChlWtrRetTemp_HASP | - | 18.5 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 437 | J270-06-1PNL-001 | J460-01-2TT-003 | Alarm | J460-01-2TT-003 - Chilled Water - Return Temperature Low Alarm | J460-01-2TT-003_ChlWtrRetTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-003_ChlWtrRetTempLoAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 438 | J270-06-1PNL-001 | J460-01-2TT-003 | Setting | J460-01-2TT-003 - Chilled Water - Return Temperature | J460-01-2TT-003_ChlWtrRetTemp_LASP | J460-01-2TT-003_ChlWtrRetTemp_LASP | 12 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 439 | J270-06-1PNL-001 | J460-01-2TT-003 | Setting | J460-01-2TT-003 - Chilled Water - Return Temperature Calibration Mode Selection | J460-01-2TT-003_ChlWtrRetTempCalModeSel | J460-01-2TT-003_ChlWtrRetTempCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 440 | J270-06-1PNL-001 | J460-01-2TT-003 | Alarm | J460-01-2TT-003 - Chilled Water - Return Temperature Calibration Still Active Alarm | J460-01-2TT-003_ChlWtrRetTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-003_ChlWtrRetTempCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 441 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-2XS-001 - Chilled Water Circulation Pump J460-01-1PMP-001 - Enable | J460-01-2XS-001_ChlWtrCirPmpEna | J460-01-2XS-001_ChlWtrCirPmpEna | DISABLE | ENABLE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 442 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-2SC-001 - Chilled Water Circulation Pump J460-01-1PMP-001 - Control Signal | J460-01-2SC-001_ChlWtrCirPmpCntr | J460-01-2SC-001_ChlWtrCirPmpCntr | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 443 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-2XA-001 - Chilled Water Circulation Pump J460-01-1PMP-001 - Alarm | J460-01-2XA-001_ChlWtrCirPmpAlm | J460-01-2XA-001_ChlWtrCirPmpAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 444 | J270-06-1PNL-001 | J460-01-1PMP-001 | Alarm | J460-01-2XA-001 - Chilled Water Circulation Pump J460-01-1PMP-001 - Alarm | J460-01-2XA-001_ChlWtrCirPmpAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2XA-001_ChlWtrCirPmpAlm_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 445 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-2SS-001 - Chilled Water Circulation Pump J460-01-1PMP-001 - Status | J460-01-2SS-001_ChlWtrCirPmpSts | J460-01-2SS-001_ChlWtrCirPmpSts | STOP | RUN | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 446 | J270-06-1PNL-001 | J460-01-1PMP-001 | Alarm | J460-01-1PMP-001 - Chilled Water Circulation Pump - Fail to Start Alarm | J460-01-1PMP-001_FailToStartAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1PMP-001_FailToStartAlm | 1 | M | - | bar: State 2 to State 64
1.0 | 447 | J270-06-1PNL-001 | J460-01-1PMP-001 | Alarm | J460-01-1PMP-001 - Chilled Water Circulation Pump - Fail to Stop Alarm | J460-01-1PMP-001_FailToStopAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1PMP-001_FailToStopAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 448 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-2HSI-001 - Chilled Water Circulation Pump J460-01-1PMP-001 - Maintenance Switch | J460-01-2HSI-001_ChlWtrCirPmpMS | J460-01-2HSI-001_ChlWtrCirPmpMS | OFF | ON | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 449 | J270-06-1PNL-001 | J140-06-2FT-001 | Measurement | J140-06-2FT-001 - Demi Water - Supply Flow | J140-06-2FT-001_DmiWtrSupFlow | J140-06-2FT-001_DmiWtrSupFlow | 2 | 40 | [11 empty] | - | - | - | - | - | - | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 450 | J270-06-1PNL-001 | J140-06-2FT-001 | Measurement | J140-06-2FT-001 - Demi Water - Supply Flow Field | J140-06-2FT-001_DmiWtrSupFlow_Field | J140-06-2FT-001_DmiWtrSupFlow_Field | 2 | 40 | [11 empty] | - | - | - | - | - | - | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 451 | J270-06-1PNL-001 | J140-06-2FT-001 | Alarm | J140-06-2FT-001 - Demi Water - Supply Flow High Alarm | J140-06-2FT-001_DmiWtrSupFlowHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J140-06-2FT-001_DmiWtrSupFlowHiAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 452 | J270-06-1PNL-001 | J140-06-2FT-001 | Setting | J140-06-2FT-001 - Demi Water - Supply Flow | J140-06-2FT-001_DmiWtrSupFlow_HASP | J140-06-2FT-001_DmiWtrSupFlow_HASP | - | 30 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 453 | J270-06-1PNL-001 | J140-06-2FT-001 | Alarm | J140-06-2FT-001 - Demi Water - Supply Flow Low Alarm | J140-06-2FT-001_DmiWtrSupFlowLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J140-06-2FT-001_DmiWtrSupFlowLoAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 454 | J270-06-1PNL-001 | J140-06-2FT-001 | Setting | J140-06-2FT-001 - Demi Water - Supply Flow | J140-06-2FT-001_DmiWtrSupFlow_LASP | J140-06-2FT-001_DmiWtrSupFlow_LASP | 10 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 455 | J270-06-1PNL-001 | J140-06-2FT-001 | Setting | J140-06-2FT-001 - Demi Water - Supply Flow Calibration Mode Selection | J140-06-2FT-001_DmiWtrSupFlowCalModeSel | J140-06-2FT-001_DmiWtrSupFlowCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 456 | J270-06-1PNL-001 | J140-06-2FT-001 | Alarm | J140-06-2FT-001 - Demi Water - Supply Flow Calibration Still Active Alarm | J140-06-2FT-001_DmiWtrSupFlowCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J140-06-2FT-001_DmiWtrSupFlowCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 457 | J270-06-1PNL-001 | J140-06-2FT-002 | Measurement | J140-06-2FT-002 - Demi Water - Return Flow | J140-06-2FT-002_DmiWtrRetFlow | J140-06-2FT-002_DmiWtrRetFlow | 2 | 40 | [11 empty] | - | - | - | - | - | - | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 458 | J270-06-1PNL-001 | J140-06-2FT-002 | Measurement | J140-06-2FT-002 - Demi Water - Return Flow Field | J140-06-2FT-002_DmiWtrRetFlow_Field | J140-06-2FT-002_DmiWtrRetFlow_Field | 2 | 40 | [11 empty] | - | - | - | - | - | - | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 459 | J270-06-1PNL-001 | J140-06-2FT-002 | Alarm | J140-06-2FT-002 - Demi Water - Return Flow High Alarm | J140-06-2FT-002_DmiWtrRetFlowHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J140-06-2FT-002_DmiWtrRetFlowHiAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 460 | J270-06-1PNL-001 | J140-06-2FT-002 | Setting | J140-06-2FT-002 - Demi Water - Return Flow | J140-06-2FT-002_DmiWtrRetFlow_HASP | J140-06-2FT-002_DmiWtrRetFlow_HASP | - | 30 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 461 | J270-06-1PNL-001 | J140-06-2FT-002 | Alarm | J140-06-2FT-002 - Demi Water - Return Flow Low Alarm | J140-06-2FT-002_DmiWtrRetFlowLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J140-06-2FT-002_DmiWtrRetFlowLoAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 462 | J270-06-1PNL-001 | J140-06-2FT-002 | Setting | J140-06-2FT-002 - Demi Water - Return Flow | J140-06-2FT-002_DmiWtrRetFlow_LASP | J140-06-2FT-002_DmiWtrRetFlow_LASP | 10 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 463 | J270-06-1PNL-001 | J140-06-2FT-002 | Setting | J140-06-2FT-002 - Demi Water - Return Flow Calibration Mode Selection | J140-06-2FT-002_DmiWtrRetFlowCalModeSel | J140-06-2FT-002_DmiWtrRetFlowCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 464 | J270-06-1PNL-001 | J140-06-2FT-002 | Alarm | J140-06-2FT-002 - Demi Water - Return Flow Calibration Still Active Alarm | J140-06-2FT-002_DmiWtrRetFlowCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J140-06-2FT-002_DmiWtrRetFlowCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 465 | J270-06-1PNL-001 | J140-06-2PT-001 | Measurement | J140-06-2PT-001 - Demi Water - Inlet Pressure | J140-06-2PT-001_DmiWtrInPress | J140-06-2PT-001_DmiWtrInPress | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 466 | J270-06-1PNL-001 | J140-06-2PT-001 | Measurement | J140-06-2PT-001 - Demi Water - Inlet Pressure Field | J140-06-2PT-001_DmiWtrInPress_Field | J140-06-2PT-001_DmiWtrInPress_Field | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 467 | J270-06-1PNL-001 | J140-06-2PT-001 | Alarm | J140-06-2PT-001 - Demi Water - Inlet Pressure High Alarm | J140-06-2PT-001_DmiWtrInPressHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J140-06-2PT-001_DmiWtrInPressHiAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 468 | J270-06-1PNL-001 | J140-06-2PT-001 | Setting | J140-06-2PT-001 - Demi Water - Inlet Pressure | J140-06-2PT-001_DmiWtrInPress_HASP | J140-06-2PT-001_DmiWtrInPress_HASP | - | 30 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 469 | J270-06-1PNL-001 | J140-06-2PT-001 | Alarm | J140-06-2PT-001 - Demi Water - Inlet Pressure Low Alarm | J140-06-2PT-001_DmiWtrInPressLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J140-06-2PT-001_DmiWtrInPressLoAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 470 | J270-06-1PNL-001 | J140-06-2PT-001 | Setting | J140-06-2PT-001 - Demi Water - Inlet Pressure | J140-06-2PT-001_DmiWtrInPress_LASP | J140-06-2PT-001_DmiWtrInPress_LASP | 10 | - | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 471 | J270-06-1PNL-001 | J140-06-2PT-001 | Setting | J140-06-2PT-001 - Demi Water - Inlet Pressure Calibration Mode Selection | J140-06-2PT-001_DmiWtrInPressCalModeSel | J140-06-2PT-001_DmiWtrInPressCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 472 | J270-06-1PNL-001 | J140-06-2PT-001 | Alarm | J140-06-2PT-001 - Demi Water - Inlet Pressure Calibration Still Active Alarm | J140-06-2PT-001_DmiWtrInPressCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J140-06-2PT-001_DmiWtrInPressCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 473 | J270-06-1PNL-001 | J140-06-2PT-002 | Measurement | J140-06-2PT-002 - Demi Water - Outlet Pressure | J140-06-2PT-002_DmiWtrOutPress | J140-06-2PT-002_DmiWtrOutPress | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 474 | J270-06-1PNL-001 | J140-06-2PT-002 | Measurement | J140-06-2PT-002 - Demi Water - Outlet Pressure Field | J140-06-2PT-002_DmiWtrOutPress_Field | J140-06-2PT-002_DmiWtrOutPress_Field | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 475 | J270-06-1PNL-001 | J140-06-2PT-002 | Alarm | J140-06-2PT-002 - Demi Water - Outlet Pressure High Alarm | J140-06-2PT-002_DmiWtrOutPressHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J140-06-2PT-002_DmiWtrOutPressHiAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 476 | J270-06-1PNL-001 | J140-06-2PT-002 | Setting | J140-06-2PT-002 - Demi Water - Outlet Pressure | J140-06-2PT-002_DmiWtrOutPress_HASP | J140-06-2PT-002_DmiWtrOutPress_HASP | - | 30 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 477 | J270-06-1PNL-001 | J140-06-2PT-002 | Alarm | J140-06-2PT-002 - Demi Water - Outlet Pressure Low Alarm | J140-06-2PT-002_DmiWtrOutPressLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J140-06-2PT-002_DmiWtrOutPressLoAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 478 | J270-06-1PNL-001 | J140-06-2PT-002 | Setting | J140-06-2PT-002 - Demi Water - Outlet Pressure | J140-06-2PT-002_DmiWtrOutPress_LASP | J140-06-2PT-002_DmiWtrOutPress_LASP | 10 | - | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 479 | J270-06-1PNL-001 | J140-06-2PT-002 | Setting | J140-06-2PT-002 - Demi Water - Outlet Pressure Calibration Mode Selection | J140-06-2PT-002_DmiWtrOutPressCalModeSel | J140-06-2PT-002_DmiWtrOutPressCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 480 | J270-06-1PNL-001 | J140-06-2PT-002 | Alarm | J140-06-2PT-002 - Demi Water - Outlet Pressure Calibration Still Active Alarm | J140-06-2PT-002_DmiWtrOutPressCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J140-06-2PT-002_DmiWtrOutPressCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 481 | J270-06-1PNL-001 | J140-06-2PT-003 | Measurement | J140-06-2PT-003 - Demi Water - Return Pressure | J140-06-2PT-003_DmiWtrRetPress | J140-06-2PT-003_DmiWtrRetPress | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 482 | J270-06-1PNL-001 | J140-06-2PT-003 | Measurement | J140-06-2PT-003 - Demi Water - Return Pressure Field | J140-06-2PT-003_DmiWtrRetPress_Field | J140-06-2PT-003_DmiWtrRetPress_Field | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 483 | J270-06-1PNL-001 | J140-06-2PT-003 | Alarm | J140-06-2PT-003 - Demi Water - Return Pressure High Alarm | J140-06-2PT-003_DmiWtrRetPressHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J140-06-2PT-003_DmiWtrRetPressHiAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 484 | J270-06-1PNL-001 | J140-06-2PT-003 | Setting | J140-06-2PT-003 - Demi Water - Return Pressure | J140-06-2PT-003_DmiWtrRetPress_HASP | J140-06-2PT-003_DmiWtrRetPress_HASP | - | 30 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 485 | J270-06-1PNL-001 | J140-06-2PT-003 | Alarm | J140-06-2PT-003 - Demi Water - Return Pressure Low Alarm | J140-06-2PT-003_DmiWtrRetPressLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J140-06-2PT-003_DmiWtrRetPressLoAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 486 | J270-06-1PNL-001 | J140-06-2PT-003 | Setting | J140-06-2PT-003 - Demi Water - Return Pressure | J140-06-2PT-003_DmiWtrRetPress_LASP | J140-06-2PT-003_DmiWtrRetPress_LASP | 10 | - | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 487 | J270-06-1PNL-001 | J140-06-2PT-003 | Setting | J140-06-2PT-003 - Demi Water - Return Pressure Calibration Mode Selection | J140-06-2PT-003_DmiWtrRetPressCalModeSel | J140-06-2PT-003_DmiWtrRetPressCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 488 | J270-06-1PNL-001 | J140-06-2PT-003 | Alarm | J140-06-2PT-003 - Demi Water - Return Pressure Calibration Still Active Alarm | J140-06-2PT-003_DmiWtrRetPressCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J140-06-2PT-003_DmiWtrRetPressCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 489 | J270-06-1PNL-001 | J460-02-2TT-616 | Measurement | J460-02-2TT-616 - Chilled Water - Supply Temperature | J460-02-2TT-616_ChlWtrSupTemp | J460-02-2TT-616_ChlWtrSupTemp | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 490 | J270-06-1PNL-001 | J460-02-2TT-616 | Measurement | J460-02-2TT-616 - Chilled Water - Supply Temperature Field | J460-02-2TT-616_ChlWtrSupTemp_Field | J460-02-2TT-616_ChlWtrSupTemp_Field | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 491 | J270-06-1PNL-001 | J460-02-2TT-616 | Alarm | J460-02-2TT-616 - Chilled Water - Supply Temperature High Alarm | J460-02-2TT-616_ChlWtrSupTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-616_ChlWtrSupTempHiAlm | 2 | Y | - | bar: State 2 to State 64
2.1 | 492 | J270-06-1PNL-001 | J460-02-2TT-616 | Setting | J460-02-2TT-616 - Chilled Water - Supply Temperature | J460-02-2TT-616_ChlWtrSupTemp_HASP | J460-02-2TT-616_ChlWtrSupTemp_HASP | - | 12 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 493 | J270-06-1PNL-001 | J460-02-2TT-616 | Alarm | J460-02-2TT-616 - Chilled Water - Supply Temperature Low Alarm | J460-02-2TT-616_ChlWtrSupTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-616_ChlWtrSupTempLoAlm | 2 | Y | - | bar: State 2 to State 64
2.1 | 494 | J270-06-1PNL-001 | J460-02-2TT-616 | Setting | J460-02-2TT-616 - Chilled Water - Supply Temperature | J460-02-2TT-616_ChlWtrSupTemp_LASP | J460-02-2TT-616_ChlWtrSupTemp_LASP | 6 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 495 | J270-06-1PNL-001 | J460-02-2TT-616 | Setting | J460-02-2TT-616 - Chilled Water - Supply Temperature Calibration Mode Selection | J460-02-2TT-616_ChlWtrSupTempCalModeSel | J460-02-2TT-616_ChlWtrSupTempCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 496 | J270-06-1PNL-001 | J460-02-2TT-616 | Alarm | J460-02-2TT-616 - Chilled Water - Supply Temperature Calibration Still Active Alarm | J460-02-2TT-616_ChlWtrSupTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-616_ChlWtrSupTempCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 497 | J270-06-1PNL-001 | J460-02-2TT-616 | Setting | J460-02-2TT-616 - Chilled Water - Supply Temperature Setpoint | J460-02-2TT-616_ChlWtrSupTempSetpoint | J460-02-2TT-616_ChlWtrSupTempSetpoint | 12 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 498 | J270-06-1PNL-001 | N/A | Calculated | BMS Sixth Floor Lab Room Dew Point Temperature Setpoint Offset | J460-02-2TT-616_LabDewPtTempSetpoint | J460-02-2TT-616_LabDewPtTempSetpoint | Calculated | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 499 | J270-06-1PNL-001 | N/A | Setting | BMS Sixth Floor Lab Room Dew Point Temperature Setpoint Offset | J460-02-2TT-616_LabDewPtTempSPOffset | J460-02-2TT-616_LabDewPtTempSPOffset | 1 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 500 | J270-06-1PNL-001 | J460-02-2TT-616 | Setting | J460-02-2TT-616 - Chilled Water - Supply Temperature Proportional Band | J460-02-2TT-616_ChlWtrSupTemp_Set_P | J460-02-2TT-616_ChlWtrSupTemp_Set_P | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 501 | J270-06-1PNL-001 | J460-02-2TT-616 | Setting | J460-02-2TT-616 - Chilled Water - Supply Temperature Integral Time | J460-02-2TT-616_ChlWtrSupTemp_Set_I | J460-02-2TT-616_ChlWtrSupTemp_Set_I | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 502 | J270-06-1PNL-001 | J460-02-2TT-616 | Setting | J460-02-2TT-616 - Chilled Water - Supply Temperature Derivative Time | J460-02-2TT-616_ChlWtrSupTemp_Set_D | J460-02-2TT-616_ChlWtrSupTemp_Set_D | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 503 | J270-06-1PNL-001 | J460-02-2TT-617 | Measurement | J460-02-2TT-617 - Chilled Water - Return Temperature | J460-02-2TT-617_ChlWtrRetTemp | J460-02-2TT-617_ChlWtrRetTemp | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 504 | J270-06-1PNL-001 | J460-02-2TT-617 | Measurement | J460-02-2TT-617 - Chilled Water - Return Temperature Field | J460-02-2TT-617_ChlWtrRetTemp_Field | J460-02-2TT-617_ChlWtrRetTemp_Field | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 505 | J270-06-1PNL-001 | J460-02-2TT-617 | Alarm | J460-02-2TT-617 - Chilled Water - Return Temperature High Alarm | J460-02-2TT-617_ChlWtrRetTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-617_ChlWtrRetTempHiAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 506 | J270-06-1PNL-001 | J460-02-2TT-617 | Setting | J460-02-2TT-617 - Chilled Water - Return Temperature | J460-02-2TT-617_ChlWtrRetTemp_HASP | J460-02-2TT-617_ChlWtrRetTemp_HASP | - | 18 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 507 | J270-06-1PNL-001 | J460-02-2TT-617 | Alarm | J460-02-2TT-617 - Chilled Water - Return Temperature Low Alarm | J460-02-2TT-617_ChlWtrRetTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-617_ChlWtrRetTempLoAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 508 | J270-06-1PNL-001 | J460-02-2TT-617 | Setting | J460-02-2TT-617 - Chilled Water - Return Temperature | J460-02-2TT-617_ChlWtrRetTemp_LASP | J460-02-2TT-617_ChlWtrRetTemp_LASP | 12 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 509 | J270-06-1PNL-001 | J460-02-2TT-617 | Setting | J460-02-2TT-617 - Chilled Water - Return Temperature Calibration Mode Selection | J460-02-2TT-617_ChlWtrRetTempCalModeSel | J460-02-2TT-617_ChlWtrRetTempCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 510 | J270-06-1PNL-001 | J460-02-2TT-617 | Alarm | J460-02-2TT-617 - Chilled Water - Return Temperature Calibration Still Active Alarm | J460-02-2TT-617_ChlWtrRetTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-617_ChlWtrRetTempCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 511 | J270-06-1PNL-001 | J460-02-1PMP-601 | Measurement | J460-02-2XS-601 - Chilled water Circulation pump J460-02-1PMP-601 - Enable | J460-02-2XS-601_ChlWtrCirPmpEna | J460-02-2XS-601_ChlWtrCirPmpEna | DISABLE | ENABLE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 512 | J270-06-1PNL-001 | J460-02-1PMP-601 | Measurement | J460-02-2SC-601 - Chilled water Circulation pump J460-02-1PMP-601 - Control Signal | J460-02-2SC-601_ChlWtrCirPmpCntr | J460-02-2SC-601_ChlWtrCirPmpCntr | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 513 | J270-06-1PNL-001 | J460-02-1PMP-601 | Measurement | J460-02-2XA-601 - Chilled water Circulation pump J460-02-1PMP-601 - Alarm | J460-02-2XA-601_ChlWtrCirPmpAlm | J460-02-2XA-601_ChlWtrCirPmpAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 514 | J270-06-1PNL-001 | J460-02-1PMP-601 | Alarm | J460-02-2XA-601 - Chilled water Circulation pump J460-02-1PMP-601 - Alarm | J460-02-2XA-601_ChlWtrCirPmpAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2XA-601_ChlWtrCirPmpAlm_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 515 | J270-06-1PNL-001 | J460-02-1PMP-601 | Measurement | J460-02-2SS-601 - Chilled water Circulation pump J460-02-1PMP-601 - Status | J460-02-2SS-601_ChlWtrCirPmpSts | J460-02-2SS-601_ChlWtrCirPmpSts | STOP | RUN | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 516 | J270-06-1PNL-001 | J460-02-1PMP-601 | Alarm | J460-02-1PMP-601 - Chilled Water Circulation Pump - Fail to Start Alarm | J460-02-1PMP-601_FailToStartAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1PMP-601_FailToStartAlm | 1 | M | - | bar: State 2 to State 64
1.0 | 517 | J270-06-1PNL-001 | J460-02-1PMP-601 | Alarm | J460-02-1PMP-601 - Chilled Water Circulation Pump - Fail to Stop Alarm | J460-02-1PMP-601_FailToStopAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1PMP-601_FailToStopAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 518 | J270-06-1PNL-001 | J460-02-1PMP-601 | Measurement | J460-02-2HSI-601 - Chilled water Circulation pump J460-02-1PMP-601 - Maintenance Switch | J460-02-2HSI-601_ChlWtrCirPmpMS | J460-02-2HSI-601_ChlWtrCirPmpMS | OFF | ON | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 519 | J270-06-1PNL-001 | J460-02-2PT-902 | Measurement | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure | J460-02-2PT-902_ExhFanPress | J460-02-2PT-902_ExhFanPress | 0 | 1000 | [11 empty] | - | - | - | - | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 520 | J270-06-1PNL-001 | J460-02-2PT-902 | Measurement | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure Field | J460-02-2PT-902_ExhFanPress_Field | J460-02-2PT-902_ExhFanPress_Field | 0 | 1000 | [11 empty] | - | - | - | - | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 521 | J270-06-1PNL-001 | J460-02-2PT-902 | Alarm | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure High Alarm | J460-02-2PT-902_ExhFanPressHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2PT-902_ExhFanPressHiAlm | 2 | Y | - | bar: State 2 to State 64
2.1 | 522 | J270-06-1PNL-001 | J460-02-2PT-902 | Setting | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure | J460-02-2PT-902_ExhFanPress_HASP | J460-02-2PT-902_ExhFanPress_HASP | - | 350 | [11 empty] | - | - | - | - | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 523 | J270-06-1PNL-001 | J460-02-2PT-902 | Alarm | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure Low Alarm | J460-02-2PT-902_ExhFanPressLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2PT-902_ExhFanPressLoAlm | 2 | Y | - | bar: State 2 to State 64
2.1 | 524 | J270-06-1PNL-001 | J460-02-2PT-902 | Setting | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure | J460-02-2PT-902_ExhFanPress_LASP | J460-02-2PT-902_ExhFanPress_LASP | 250 | - | [11 empty] | - | - | - | - | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 525 | J270-06-1PNL-001 | J460-02-2PT-902 | Setting | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure Calibration Mode Selection | J460-02-2PT-902_ExhFanPressCalModeSel | J460-02-2PT-902_ExhFanPressCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 526 | J270-06-1PNL-001 | J460-02-2PT-902 | Alarm | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure Calibration Still Active Alarm | J460-02-2PT-902_ExhFanPressCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2PT-902_ExhFanPressCalModeAlm | 2 | Y | - | bar: State 2 to State 64
2.1 | 527 | J270-06-1PNL-001 | J460-02-2PT-902 | Setting | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure Setpoint | J460-02-2PT-902_ExhFanPressSetpoint | J460-02-2PT-902_ExhFanPressSetpoint | 300 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 528 | J270-06-1PNL-001 | J460-02-2PT-902 | Setting | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure Proportional Band | J460-02-2PT-902_ExhFanPress_Set_P | J460-02-2PT-902_ExhFanPress_Set_P | 1900 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 529 | J270-06-1PNL-001 | J460-02-2PT-902 | Setting | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure Integral Time | J460-02-2PT-902_ExhFanPress_Set_I | J460-02-2PT-902_ExhFanPress_Set_I | 200 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 530 | J270-06-1PNL-001 | J460-02-2PT-902 | Setting | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure Derivative Time | J460-02-2PT-902_ExhFanPress_Set_D | J460-02-2PT-902_ExhFanPress_Set_D | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 531 | J270-06-1PNL-001 | J460-02-1B-902 | Measurement | J460-02-2XC-902 - Exhaust Fan J460-02-1B-902 - Control Signal | J460-02-2XC-902_ExhFanCntr | J460-02-2XC-902_ExhFanCntr | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 532 | J270-06-1PNL-001 | J460-02-1B-902 | Measurement | J460-02-2XA-902 - Exhaust Fan J460-02-1B-902 - Alarm | J460-02-2XA-902_ExhFanAlm | J460-02-2XA-902_ExhFanAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 533 | J270-06-1PNL-001 | J460-02-1B-902 | Alarm | J460-02-2XA-902 - Exhaust Fan J460-02-1B-902 - Alarm | J460-02-2XA-902_ExhFanAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2XA-902_ExhFanAlm_Alm | 2 | M | - | bar: State 2 to State 64
1.0 | 534 | J270-06-1PNL-001 | J460-02-1B-902 | Measurement | J460-02-2HSI-902 - Exhaust Fan J460-02-1B-902 - Maintenance Switch | J460-01-2HSI-902_ExhFanMS | J460-01-2HSI-902_ExhFanMS | OFF | ON | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 535 | J270-06-1PNL-001 | J460-01-2TC-601 | Alarm | J460-01-2TC-601 - Room J6.02 - Room Controller - Communication Failure Alarm | J460-01-2TC-601_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TC-601_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 536 | J460-01-1CP-601 | J460-01-2TT-601 | Measurement | J460-01-2TT-601 - Room J6.02 - Temperature | J460-01-2TT-601_RmTemp | J460-01-2TT-601_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 537 | J460-01-1CP-601 | J460-01-2TT-601 | Alarm | J460-01-2TT-601 - Room J6.02 - Temperature High Alarm | J460-01-2TT-601_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-601_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 538 | J460-01-1CP-601 | J460-01-2TT-601 | Setting | J460-01-2TT-601 - Room J6.02 - Temperature | J460-01-2TT-601_RmTemp_HASP | J460-01-2TT-601_RmTemp_HASP | - | 28 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 539 | J460-01-1CP-601 | J460-01-2TT-601 | Alarm | J460-01-2TT-601 - Room J6.02 - Temperature Low Alarm | J460-01-2TT-601_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-601_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 540 | J460-01-1CP-601 | J460-01-2TT-601 | Calculated | J460-01-2TT-601 - Room J6.02 - Temperature | J460-01-2TT-601_RmTemp_LASP | J460-01-2TT-601_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 541 | J460-01-1CP-601 | J460-01-2TT-601 | Calculated | J460-01-2TT-601 - Room J6.02 - Temperature Effective Setpoint | J460-01-2TT-601_RmTempEffSetpoint | J460-01-2TT-601_RmTempEffSetpoint | Calculated | Calculated | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 542 | J460-01-1CP-601 | J460-01-2TT-601 | Setting | J460-01-2TT-601 - Room J6.02 - Temperature Setpoint CPA | J460-01-2TT-601_RmTempSetpointCPA | J460-01-2TT-601_RmTempSetpointCPA | -3 | 3 | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 543 | J460-01-1CP-601 | J460-01-2TT-601 | Setting | J460-01-2TT-601 - Room J6.02 - Temperature Proportional Band | J460-01-2TT-601_RmTemp_Set_P | J460-01-2TT-601_RmTemp_Set_P | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 544 | J460-01-1CP-601 | J460-01-2TT-601 | Setting | J460-01-2TT-601 - Room J6.02 - Temperature Integral Time | J460-01-2TT-601_RmTemp_Set_I | J460-01-2TT-601_RmTemp_Set_I | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 545 | J460-01-1CP-601 | J460-01-2TT-601 | Setting | J460-01-2TT-601 - Room J6.02 - Temperature Derivative Time | J460-01-2TT-601_RmTemp_Set_D | J460-01-2TT-601_RmTemp_Set_D | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 546 | J460-01-1CP-601 | J460-01-2MT-601 | Measurement | J460-01-2MT-601 - Room J6.02 - Humidity | J460-01-2MT-601_RmHum | J460-01-2MT-601_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 547 | J460-01-1CP-601 | J460-01-2MT-601 | Alarm | J460-01-2MT-601 - Room J6.02 - Humidity High Alarm | J460-01-2MT-601_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-601_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 548 | J460-01-1CP-601 | J460-01-2MT-601 | Setting | J460-01-2MT-601 - Room J6.02 - Humidity | J460-01-2MT-601_RmHum_HASP | J460-01-2MT-601_RmHum_HASP | - | 60 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 549 | J460-01-1CP-601 | J460-01-2MT-601 | Alarm | J460-01-2MT-601 - Room J6.02 - Humidity Low Alarm | J460-01-2MT-601_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-601_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 550 | J460-01-1CP-601 | J460-01-2MT-601 | Setting | J460-01-2MT-601 - Room J6.02 - Humidity | J460-01-2MT-601_RmHum_LASP | J460-01-2MT-601_RmHum_LASP | 30 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 551 | J460-01-1CP-601 | J460-01-2XT-612 | Measurement | J460-01-2XT-612 - Room J6.02 - Occupied | J460-01-2XT-612_RmOcc | J460-01-2XT-612_RmOcc | UNOCC | OCC | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 552 | J270-06-1PNL-001 | J460-01-2FCV-601 | Alarm | J460-01-2FCV-601 - Room J6.02 - Reheater Valve Control - Communication Failure Alarm | J460-01-2FCV-601_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-601_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 553 | J270-06-1PNL-001 | J460-01-2FCV-601 | Measurement | J460-01-2FCV-601 - Room J6.02 - Reheater Valve Control Forced Position | J460-01-2FCV-601_ForcePos | J460-01-2FCV-601_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 554 | J270-06-1PNL-001 | J460-01-2FCV-601 | Setting | J460-01-2FCV-601 - Room J6.02 - Reheater Valve Control Forced Calibration | J460-01-2FCV-601_ForceCal | J460-01-2FCV-601_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 555 | J270-06-1PNL-001 | J460-01-2FCV-601 | Measurement | J460-01-2FCV-601 - Room J6.02 - Reheater Valve Control Status | J460-01-2FCV-601_MotState | J460-01-2FCV-601_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 556 | J270-06-1PNL-001 | J460-01-2FCV-601 | Measurement | J460-01-2FCV-601 - Room J6.02 - Reheater Valve Control Actual SP | J460-01-2FCV-601_ActSP | J460-01-2FCV-601_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 557 | J270-06-1PNL-001 | J460-01-2FCV-601 | Setting | J460-01-2FCV-601 - Room J6.02 - Reheater Valve Control SP | J460-01-2FCV-601_SP | J460-01-2FCV-601_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 558 | J270-06-1PNL-001 | J460-01-2FCV-601 | Alarm | J460-01-2FCV-601 - Room J6.02 - Reheater Valve Control Fail to Open Alarm | J460-01-2FCV-601_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-601_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 559 | J270-06-1PNL-001 | J460-01-2FCV-601 | Alarm | J460-01-2FCV-601 - Room J6.02 - Reheater Valve Control Fail to Close Alarm | J460-01-2FCV-601_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-601_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 560 | J270-06-1PNL-001 | J460-01-2FCV-601 | Measurement | J460-01-2FCV-601 - Room J6.02 - Reheater Valve Control Error Code | J460-01-2FCV-601_Err | J460-01-2FCV-601_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 561 | J270-06-1PNL-001 | J460-01-2TC-602 | Alarm | J460-01-2TC-602 - Room J6.03 - Room Controller - Communication Failure Alarm | J460-01-2TC-602_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TC-602_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 562 | J460-01-1CP-602 | J460-01-2TT-602 | Measurement | J460-01-2TT-602 - Room J6.03 - Temperature | J460-01-2TT-602_RmTemp | J460-01-2TT-602_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 563 | J460-01-1CP-602 | J460-01-2TT-602 | Alarm | J460-01-2TT-602 - Room J6.03 - Temperature High Alarm | J460-01-2TT-602_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-602_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 564 | J460-01-1CP-602 | J460-01-2TT-602 | Setting | J460-01-2TT-602 - Room J6.03 - Temperature | J460-01-2TT-602_RmTemp_HASP | J460-01-2TT-602_RmTemp_HASP | - | 28 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 565 | J460-01-1CP-602 | J460-01-2TT-602 | Alarm | J460-01-2TT-602 - Room J6.03 - Temperature Low Alarm | J460-01-2TT-602_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-602_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 566 | J460-01-1CP-602 | J460-01-2TT-602 | Calculated | J460-01-2TT-602 - Room J6.03 - Temperature | J460-01-2TT-602_RmTemp_LASP | J460-01-2TT-602_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 567 | J460-01-1CP-602 | J460-01-2TT-602 | Calculated | J460-01-2TT-602 - Room J6.03 - Temperature Effective Setpoint | J460-01-2TT-602_RmTempEffSetpoint | J460-01-2TT-602_RmTempEffSetpoint | Calculated | Calculated | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 568 | J460-01-1CP-602 | J460-01-2TT-602 | Setting | J460-01-2TT-602 - Room J6.03 - Temperature Setpoint CPA | J460-01-2TT-602_RmTempSetpointCPA | J460-01-2TT-602_RmTempSetpointCPA | -3 | 3 | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 569 | J460-01-1CP-602 | J460-01-2TT-602 | Setting | J460-01-2TT-602 - Room J6.03 - Temperature Proportional Band | J460-01-2TT-602_RmTemp_Set_P | J460-01-2TT-602_RmTemp_Set_P | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 570 | J460-01-1CP-602 | J460-01-2TT-602 | Setting | J460-01-2TT-602 - Room J6.03 - Temperature Integral Time | J460-01-2TT-602_RmTemp_Set_I | J460-01-2TT-602_RmTemp_Set_I | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 571 | J460-01-1CP-602 | J460-01-2TT-602 | Setting | J460-01-2TT-602 - Room J6.03 - Temperature Derivative Time | J460-01-2TT-602_RmTemp_Set_D | J460-01-2TT-602_RmTemp_Set_D | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 572 | J460-01-1CP-602 | J460-01-2MT-602 | Measurement | J460-01-2MT-602 - Room J6.03 - Humidity | J460-01-2MT-602_RmHum | J460-01-2MT-602_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 573 | J460-01-1CP-602 | J460-01-2MT-602 | Alarm | J460-01-2MT-602 - Room J6.03 - Humidity High Alarm | J460-01-2MT-602_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-602_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 574 | J460-01-1CP-602 | J460-01-2MT-602 | Setting | J460-01-2MT-602 - Room J6.03 - Humidity | J460-01-2MT-602_RmHum_HASP | J460-01-2MT-602_RmHum_HASP | - | 60 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 575 | J460-01-1CP-602 | J460-01-2MT-602 | Alarm | J460-01-2MT-602 - Room J6.03 - Humidity Low Alarm | J460-01-2MT-602_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-602_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 576 | J460-01-1CP-602 | J460-01-2MT-602 | Setting | J460-01-2MT-602 - Room J6.03 - Humidity | J460-01-2MT-602_RmHum_LASP | J460-01-2MT-602_RmHum_LASP | 30 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 577 | J460-01-1CP-602 | J460-01-2XT-613 | Measurement | J460-01-2XT-613 - Room J6.03 - Occupied | J460-01-2XT-613_RmOcc | J460-01-2XT-613_RmOcc | UNOCC | OCC | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 578 | J270-06-1PNL-001 | J460-01-2FCV-602 | Alarm | J460-01-2FCV-602 - Room J6.03 - Reheater Valve Control - Communication Failure Alarm | J460-01-2FCV-602_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-602_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 579 | J270-06-1PNL-001 | J460-01-2FCV-602 | Measurement | J460-01-2FCV-602 - Room J6.03 - Reheater Valve Control Forced Position | J460-01-2FCV-602_ForcePos | J460-01-2FCV-602_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 580 | J270-06-1PNL-001 | J460-01-2FCV-602 | Setting | J460-01-2FCV-602 - Room J6.03 - Reheater Valve Control Forced Calibration | J460-01-2FCV-602_ForceCal | J460-01-2FCV-602_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 581 | J270-06-1PNL-001 | J460-01-2FCV-602 | Measurement | J460-01-2FCV-602 - Room J6.03 - Reheater Valve Control Status | J460-01-2FCV-602_MotState | J460-01-2FCV-602_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 582 | J270-06-1PNL-001 | J460-01-2FCV-602 | Measurement | J460-01-2FCV-602 - Room J6.03 - Reheater Valve Control Actual SP | J460-01-2FCV-602_ActSP | J460-01-2FCV-602_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 583 | J270-06-1PNL-001 | J460-01-2FCV-602 | Setting | J460-01-2FCV-602 - Room J6.03 - Reheater Valve Control SP | J460-01-2FCV-602_SP | J460-01-2FCV-602_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 584 | J270-06-1PNL-001 | J460-01-2FCV-602 | Alarm | J460-01-2FCV-602 - Room J6.03 - Reheater Valve Control Fail to Open Alarm | J460-01-2FCV-602_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-602_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 585 | J270-06-1PNL-001 | J460-01-2FCV-602 | Alarm | J460-01-2FCV-602 - Room J6.03 - Reheater Valve Control Fail to Close Alarm | J460-01-2FCV-602_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-602_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 586 | J270-06-1PNL-001 | J460-01-2FCV-602 | Measurement | J460-01-2FCV-602 - Room J6.03 - Reheater Valve Control Error Code | J460-01-2FCV-602_Err | J460-01-2FCV-602_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 587 | J270-06-1PNL-001 | J460-01-2TC-603 | Alarm | J460-01-2TC-603 - Room J6.06 - Room Controller - Communication Failure Alarm | J460-01-2TC-603_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TC-603_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 588 | J460-01-1CP-603 | J460-01-2TT-603 | Measurement | J460-01-2TT-603 - Room J6.06 - Temperature | J460-01-2TT-603_RmTemp | J460-01-2TT-603_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 589 | J460-01-1CP-603 | J460-01-2TT-603 | Alarm | J460-01-2TT-603 - Room J6.06 - Temperature High Alarm | J460-01-2TT-603_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-603_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 590 | J460-01-1CP-603 | J460-01-2TT-603 | Calculated | J460-01-2TT-603 - Room J6.06 - Temperature | J460-01-2TT-603_RmTemp_HASP | J460-01-2TT-603_RmTemp_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 591 | J460-01-1CP-603 | J460-01-2TT-603 | Alarm | J460-01-2TT-603 - Room J6.06 - Temperature Low Alarm | J460-01-2TT-603_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-603_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 592 | J460-01-1CP-603 | J460-01-2TT-603 | Calculated | J460-01-2TT-603 - Room J6.06 - Temperature | J460-01-2TT-603_RmTemp_LASP | J460-01-2TT-603_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 593 | J460-01-1CP-603 | J460-01-2TT-603 | Calculated | J460-01-2TT-603 - Room J6.06 - Temperature Effective Setpoint | J460-01-2TT-603_RmTempEffSetpoint | J460-01-2TT-603_RmTempEffSetpoint | Calculated | Calculated | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 594 | J460-01-1CP-603 | J460-01-2TT-603 | Setting | J460-01-2TT-603 - Room J6.06 - Temperature Setpoint CPA | J460-01-2TT-603_RmTempSetpointCPA | J460-01-2TT-603_RmTempSetpointCPA | -3 | 3 | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 595 | J460-01-1CP-603 | J460-01-2TT-603 | Setting | J460-01-2TT-603 - Room J6.06 - Temperature Proportional Band | J460-01-2TT-603_RmTemp_Set_P_Heat | J460-01-2TT-603_RmTemp_Set_P_Heat | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 596 | J460-01-1CP-603 | J460-01-2TT-603 | Setting | J460-01-2TT-603 - Room J6.06 - Temperature Integral Time | J460-01-2TT-603_RmTemp_Set_I_Heat | J460-01-2TT-603_RmTemp_Set_I_Heat | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 597 | J460-01-1CP-603 | J460-01-2TT-603 | Setting | J460-01-2TT-603 - Room J6.06 - Temperature Derivative Time | J460-01-2TT-603_RmTemp_Set_D_Heat | J460-01-2TT-603_RmTemp_Set_D_Heat | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 598 | J460-01-1CP-603 | J460-01-2TT-603 | Setting | J460-01-2TT-603 - Room J6.06 - Temperature Proportional Band | J460-01-2TT-603_RmTemp_Set_P_Cool | J460-01-2TT-603_RmTemp_Set_P_Cool | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 599 | J460-01-1CP-603 | J460-01-2TT-603 | Setting | J460-01-2TT-603 - Room J6.06 - Temperature Integral Time | J460-01-2TT-603_RmTemp_Set_I_Cool | J460-01-2TT-603_RmTemp_Set_I_Cool | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 600 | J460-01-1CP-603 | J460-01-2TT-603 | Setting | J460-01-2TT-603 - Room J6.06 - Temperature Derivative Time | J460-01-2TT-603_RmTemp_Set_D_Cool | J460-01-2TT-603_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 601 | J460-01-1CP-603 | J460-01-2MT-603 | Measurement | J460-01-2MT-603 - Room J6.06 - Humidity | J460-01-2MT-603_RmHum | J460-01-2MT-603_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 602 | J460-01-1CP-603 | J460-01-2MT-603 | Alarm | J460-01-2MT-603 - Room J6.06 - Humidity High Alarm | J460-01-2MT-603_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-603_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 603 | J460-01-1CP-603 | J460-01-2MT-603 | Setting | J460-01-2MT-603 - Room J6.06 - Humidity | J460-01-2MT-603_RmHum_HASP | J460-01-2MT-603_RmHum_HASP | - | 60 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 604 | J460-01-1CP-603 | J460-01-2MT-603 | Alarm | J460-01-2MT-603 - Room J6.06 - Humidity Low Alarm | J460-01-2MT-603_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-603_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 605 | J460-01-1CP-603 | J460-01-2MT-603 | Setting | J460-01-2MT-603 - Room J6.06 - Humidity | J460-01-2MT-603_RmHum_LASP | J460-01-2MT-603_RmHum_LASP | 30 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 606 | J460-01-1CP-603 | J460-01-2XT-603 | Measurement | J460-01-2XT-603 - Room J6.06 - CO2 Concentration | J460-01-2XT-603_RmCO2 | J460-01-2XT-603_RmCO2 | 0 | 2000 | [11 empty] | - | - | - | - | - | - | 200 | - | ppm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 607 | J460-01-1CP-603 | J460-01-2XT-603 | Alarm | J460-01-2XT-603 - Room J6.06 - CO2 Concentration High Alarm | J460-01-2XT-603_RmCO2HiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2XT-603_RmCO2HiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 608 | J460-01-1CP-603 | J460-01-2XT-603 | Setting | J460-01-2XT-603 - Room J6.06 - CO2 Concentration | J460-01-2XT-603_RmCO2_HASP | J460-01-2XT-603_RmCO2_HASP | - | 1500 | [11 empty] | - | - | - | - | - | - | 200 | - | ppm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 609 | J460-01-1CP-603 | J460-01-2XT-603 | Setting | J460-01-2XT-603 - Room J6.06 - CO2 Concentration Setpoint | J460-01-2XT-603_RmCO2Setpoint | J460-01-2XT-603_RmCO2Setpoint | - | 800 | [11 empty] | - | - | - | - | - | - | 220 | - | ppm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 610 | J460-01-1CP-603 | J460-01-2XT-603 | Setting | J460-01-2XT-603 - Room J6.06 - CO2 Concentration Proportional Band | J460-01-2XT-603_RmCO2_Set_P | J460-01-2XT-603_RmCO2_Set_P | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 611 | J460-01-1CP-603 | J460-01-2XT-603 | Setting | J460-01-2XT-603 - Room J6.06 - CO2 Concentration Integral Time | J460-01-2XT-603_RmCO2_Set_I | J460-01-2XT-603_RmCO2_Set_I | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 612 | J460-01-1CP-603 | J460-01-2XT-603 | Setting | J460-01-2XT-603 - Room J6.06 - CO2 Concentration Derivative Time | J460-01-2XT-603_RmCO2_Set_D | J460-01-2XT-603_RmCO2_Set_D | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 613 | J460-01-1CP-603 | J460-01-2XT-614 | Measurement | J460-01-2XT-614 - Room J6.06 - Occupied | J460-01-2XT-614_RmOcc | J460-01-2XT-614_RmOcc | UNOCC | OCC | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 614 | J270-06-1PNL-001 | J460-01-2FCV-603 | Alarm | J460-01-2FCV-603 - Room J6.06 - J460-01-1ACU-601 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-603_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-603_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 615 | J270-06-1PNL-001 | J460-01-2FCV-603 | Measurement | J460-01-2FCV-603 - Room J6.06 - J460-01-1ACU-601 Heating Valve Control Forced Position | J460-01-2FCV-603_ForcePos | J460-01-2FCV-603_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 616 | J270-06-1PNL-001 | J460-01-2FCV-603 | Setting | J460-01-2FCV-603 - Room J6.06 - J460-01-1ACU-601 Heating Valve Control Forced Calibration | J460-01-2FCV-603_ForceCal | J460-01-2FCV-603_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 617 | J270-06-1PNL-001 | J460-01-2FCV-603 | Measurement | J460-01-2FCV-603 - Room J6.06 - J460-01-1ACU-601 Heating Valve Control Status | J460-01-2FCV-603_MotState | J460-01-2FCV-603_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 618 | J270-06-1PNL-001 | J460-01-2FCV-603 | Measurement | J460-01-2FCV-603 - Room J6.06 - J460-01-1ACU-601 Heating Valve Control Actual SP | J460-01-2FCV-603_ActSP | J460-01-2FCV-603_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 619 | J270-06-1PNL-001 | J460-01-2FCV-603 | Setting | J460-01-2FCV-603 - Room J6.06 - J460-01-1ACU-601 Heating Valve Control SP | J460-01-2FCV-603_SP | J460-01-2FCV-603_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 620 | J270-06-1PNL-001 | J460-01-2FCV-603 | Alarm | J460-01-2FCV-603 - Room J6.06 - J460-01-1ACU-601 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-603_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-603_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 621 | J270-06-1PNL-001 | J460-01-2FCV-603 | Alarm | J460-01-2FCV-603 - Room J6.06 - J460-01-1ACU-601 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-603_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-603_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 622 | J270-06-1PNL-001 | J460-01-2FCV-603 | Measurement | J460-01-2FCV-603 - Room J6.06 - J460-01-1ACU-601 Heating Valve Control Error Code | J460-01-2FCV-603_Err | J460-01-2FCV-603_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 623 | J270-06-1PNL-001 | J460-01-2FCV-604 | Alarm | J460-01-2FCV-604 - Room J6.06 - J460-01-1ACU-602 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-604_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-604_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.1 | 624 | J270-06-1PNL-001 | J460-01-2FCV-604 | Measurement | J460-01-2FCV-604 - Room J6.06 - J460-01-1ACU-602 Heating Valve Control Forced Position | J460-01-2FCV-604_ForcePos | J460-01-2FCV-604_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 625 | J270-06-1PNL-001 | J460-01-2FCV-604 | Setting | J460-01-2FCV-604 - Room J6.06 - J460-01-1ACU-602 Heating Valve Control Forced Calibration | J460-01-2FCV-604_ForceCal | J460-01-2FCV-604_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 626 | J270-06-1PNL-001 | J460-01-2FCV-604 | Measurement | J460-01-2FCV-604 - Room J6.06 - J460-01-1ACU-602 Heating Valve Control Status | J460-01-2FCV-604_MotState | J460-01-2FCV-604_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.1 | 627 | J270-06-1PNL-001 | J460-01-2FCV-604 | Measurement | J460-01-2FCV-604 - Room J6.06 - J460-01-1ACU-602 Heating Valve Control Actual SP | J460-01-2FCV-604_ActSP | J460-01-2FCV-604_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 628 | J270-06-1PNL-001 | J460-01-2FCV-604 | Setting | J460-01-2FCV-604 - Room J6.06 - J460-01-1ACU-602 Heating Valve Control SP | J460-01-2FCV-604_SP | J460-01-2FCV-604_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 629 | J270-06-1PNL-001 | J460-01-2FCV-604 | Alarm | J460-01-2FCV-604 - Room J6.06 - J460-01-1ACU-602 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-604_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-604_FTOAlm | 2 | M | - | bar: State 2 to State 64
2.1 | 630 | J270-06-1PNL-001 | J460-01-2FCV-604 | Alarm | J460-01-2FCV-604 - Room J6.06 - J460-01-1ACU-602 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-604_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-604_FTCAlm | 2 | M | - | bar: State 2 to State 64
2.1 | 631 | J270-06-1PNL-001 | J460-01-2FCV-604 | Measurement | J460-01-2FCV-604 - Room J6.06 - J460-01-1ACU-602 Heating Valve Control Error Code | J460-01-2FCV-604_Err | J460-01-2FCV-604_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 632 | J270-06-1PNL-001 | J460-01-2FCV-605 | Alarm | J460-01-2FCV-605 - Room J6.06 - J460-01-1ACU-603 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-605_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-605_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 633 | J270-06-1PNL-001 | J460-01-2FCV-605 | Measurement | J460-01-2FCV-605 - Room J6.06 - J460-01-1ACU-603 Heating Valve Control Forced Position | J460-01-2FCV-605_ForcePos | J460-01-2FCV-605_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 634 | J270-06-1PNL-001 | J460-01-2FCV-605 | Setting | J460-01-2FCV-605 - Room J6.06 - J460-01-1ACU-603 Heating Valve Control Forced Calibration | J460-01-2FCV-605_ForceCal | J460-01-2FCV-605_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 635 | J270-06-1PNL-001 | J460-01-2FCV-605 | Measurement | J460-01-2FCV-605 - Room J6.06 - J460-01-1ACU-603 Heating Valve Control Status | J460-01-2FCV-605_MotState | J460-01-2FCV-605_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 636 | J270-06-1PNL-001 | J460-01-2FCV-605 | Measurement | J460-01-2FCV-605 - Room J6.06 - J460-01-1ACU-603 Heating Valve Control Actual SP | J460-01-2FCV-605_ActSP | J460-01-2FCV-605_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 637 | J270-06-1PNL-001 | J460-01-2FCV-605 | Setting | J460-01-2FCV-605 - Room J6.06 - J460-01-1ACU-603 Heating Valve Control SP | J460-01-2FCV-605_SP | J460-01-2FCV-605_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 638 | J270-06-1PNL-001 | J460-01-2FCV-605 | Alarm | J460-01-2FCV-605 - Room J6.06 - J460-01-1ACU-603 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-605_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-605_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 639 | J270-06-1PNL-001 | J460-01-2FCV-605 | Alarm | J460-01-2FCV-605 - Room J6.06 - J460-01-1ACU-603 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-605_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-605_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 640 | J270-06-1PNL-001 | J460-01-2FCV-605 | Measurement | J460-01-2FCV-605 - Room J6.06 - J460-01-1ACU-603 Heating Valve Control Error Code | J460-01-2FCV-605_Err | J460-01-2FCV-605_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 641 | J270-06-1PNL-001 | J460-01-2FCV-606 | Alarm | J460-01-2FCV-606 - Room J6.06 - J460-01-1ACU-604 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-606_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-606_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 642 | J270-06-1PNL-001 | J460-01-2FCV-606 | Measurement | J460-01-2FCV-606 - Room J6.06 - J460-01-1ACU-604 Heating Valve Control Forced Position | J460-01-2FCV-606_ForcePos | J460-01-2FCV-606_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 643 | J270-06-1PNL-001 | J460-01-2FCV-606 | Setting | J460-01-2FCV-606 - Room J6.06 - J460-01-1ACU-604 Heating Valve Control Forced Calibration | J460-01-2FCV-606_ForceCal | J460-01-2FCV-606_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 644 | J270-06-1PNL-001 | J460-01-2FCV-606 | Measurement | J460-01-2FCV-606 - Room J6.06 - J460-01-1ACU-604 Heating Valve Control Status | J460-01-2FCV-606_MotState | J460-01-2FCV-606_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 645 | J270-06-1PNL-001 | J460-01-2FCV-606 | Measurement | J460-01-2FCV-606 - Room J6.06 - J460-01-1ACU-604 Heating Valve Control Actual SP | J460-01-2FCV-606_ActSP | J460-01-2FCV-606_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 646 | J270-06-1PNL-001 | J460-01-2FCV-606 | Setting | J460-01-2FCV-606 - Room J6.06 - J460-01-1ACU-604 Heating Valve Control SP | J460-01-2FCV-606_SP | J460-01-2FCV-606_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 647 | J270-06-1PNL-001 | J460-01-2FCV-606 | Alarm | J460-01-2FCV-606 - Room J6.06 - J460-01-1ACU-604 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-606_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-606_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 648 | J270-06-1PNL-001 | J460-01-2FCV-606 | Alarm | J460-01-2FCV-606 - Room J6.06 - J460-01-1ACU-604 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-606_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-606_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 649 | J270-06-1PNL-001 | J460-01-2FCV-606 | Measurement | J460-01-2FCV-606 - Room J6.06 - J460-01-1ACU-604 Heating Valve Control Error Code | J460-01-2FCV-606_Err | J460-01-2FCV-606_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 650 | J270-06-1PNL-001 | J460-01-2FCV-607 | Alarm | J460-01-2FCV-607 - Room J6.06 - J460-01-1ACU-601 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-607_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-607_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 651 | J270-06-1PNL-001 | J460-01-2FCV-607 | Measurement | J460-01-2FCV-607 - Room J6.06 - J460-01-1ACU-601 Cooling Valve Control Forced Position | J460-01-2FCV-607_ForcePos | J460-01-2FCV-607_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 652 | J270-06-1PNL-001 | J460-01-2FCV-607 | Setting | J460-01-2FCV-607 - Room J6.06 - J460-01-1ACU-601 Cooling Valve Control Forced Calibration | J460-01-2FCV-607_ForceCal | J460-01-2FCV-607_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 653 | J270-06-1PNL-001 | J460-01-2FCV-607 | Measurement | J460-01-2FCV-607 - Room J6.06 - J460-01-1ACU-601 Cooling Valve Control Status | J460-01-2FCV-607_MotState | J460-01-2FCV-607_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 654 | J270-06-1PNL-001 | J460-01-2FCV-607 | Measurement | J460-01-2FCV-607 - Room J6.06 - J460-01-1ACU-601 Cooling Valve Control Actual SP | J460-01-2FCV-607_ActSP | J460-01-2FCV-607_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 655 | J270-06-1PNL-001 | J460-01-2FCV-607 | Setting | J460-01-2FCV-607 - Room J6.06 - J460-01-1ACU-601 Cooling Valve Control SP | J460-01-2FCV-607_SP | J460-01-2FCV-607_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 656 | J270-06-1PNL-001 | J460-01-2FCV-607 | Alarm | J460-01-2FCV-607 - Room J6.06 - J460-01-1ACU-601 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-607_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-607_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 657 | J270-06-1PNL-001 | J460-01-2FCV-607 | Alarm | J460-01-2FCV-607 - Room J6.06 - J460-01-1ACU-601 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-607_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-607_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 658 | J270-06-1PNL-001 | J460-01-2FCV-607 | Measurement | J460-01-2FCV-607 - Room J6.06 - J460-01-1ACU-601 Cooling Valve Control Error Code | J460-01-2FCV-607_Err | J460-01-2FCV-607_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 659 | J270-06-1PNL-001 | J460-01-2FCV-608 | Alarm | J460-01-2FCV-608 - Room J6.06 - J460-01-1ACU-602 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-608_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-608_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.1 | 660 | J270-06-1PNL-001 | J460-01-2FCV-608 | Measurement | J460-01-2FCV-608 - Room J6.06 - J460-01-1ACU-602 Cooling Valve Control Forced Position | J460-01-2FCV-608_ForcePos | J460-01-2FCV-608_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 661 | J270-06-1PNL-001 | J460-01-2FCV-608 | Setting | J460-01-2FCV-608 - Room J6.06 - J460-01-1ACU-602 Cooling Valve Control Forced Calibration | J460-01-2FCV-608_ForceCal | J460-01-2FCV-608_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 662 | J270-06-1PNL-001 | J460-01-2FCV-608 | Measurement | J460-01-2FCV-608 - Room J6.06 - J460-01-1ACU-602 Cooling Valve Control Status | J460-01-2FCV-608_MotState | J460-01-2FCV-608_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.1 | 663 | J270-06-1PNL-001 | J460-01-2FCV-608 | Measurement | J460-01-2FCV-608 - Room J6.06 - J460-01-1ACU-602 Cooling Valve Control Actual SP | J460-01-2FCV-608_ActSP | J460-01-2FCV-608_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 664 | J270-06-1PNL-001 | J460-01-2FCV-608 | Setting | J460-01-2FCV-608 - Room J6.06 - J460-01-1ACU-602 Cooling Valve Control SP | J460-01-2FCV-608_SP | J460-01-2FCV-608_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 665 | J270-06-1PNL-001 | J460-01-2FCV-608 | Alarm | J460-01-2FCV-608 - Room J6.06 - J460-01-1ACU-602 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-608_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-608_FTOAlm | 2 | M | - | bar: State 2 to State 64
2.1 | 666 | J270-06-1PNL-001 | J460-01-2FCV-608 | Alarm | J460-01-2FCV-608 - Room J6.06 - J460-01-1ACU-602 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-608_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-608_FTCAlm | 2 | M | - | bar: State 2 to State 64
2.1 | 667 | J270-06-1PNL-001 | J460-01-2FCV-608 | Measurement | J460-01-2FCV-608 - Room J6.06 - J460-01-1ACU-602 Cooling Valve Control Error Code | J460-01-2FCV-608_Err | J460-01-2FCV-608_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 668 | J270-06-1PNL-001 | J460-01-2FCV-609 | Alarm | J460-01-2FCV-609 - Room J6.06 - J460-01-1ACU-603 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-609_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-609_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 669 | J270-06-1PNL-001 | J460-01-2FCV-609 | Measurement | J460-01-2FCV-609 - Room J6.06 - J460-01-1ACU-603 Cooling Valve Control Forced Position | J460-01-2FCV-609_ForcePos | J460-01-2FCV-609_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 670 | J270-06-1PNL-001 | J460-01-2FCV-609 | Setting | J460-01-2FCV-609 - Room J6.06 - J460-01-1ACU-603 Cooling Valve Control Forced Calibration | J460-01-2FCV-609_ForceCal | J460-01-2FCV-609_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 671 | J270-06-1PNL-001 | J460-01-2FCV-609 | Measurement | J460-01-2FCV-609 - Room J6.06 - J460-01-1ACU-603 Cooling Valve Control Status | J460-01-2FCV-609_MotState | J460-01-2FCV-609_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 672 | J270-06-1PNL-001 | J460-01-2FCV-609 | Measurement | J460-01-2FCV-609 - Room J6.06 - J460-01-1ACU-603 Cooling Valve Control Actual SP | J460-01-2FCV-609_ActSP | J460-01-2FCV-609_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 673 | J270-06-1PNL-001 | J460-01-2FCV-609 | Setting | J460-01-2FCV-609 - Room J6.06 - J460-01-1ACU-603 Cooling Valve Control SP | J460-01-2FCV-609_SP | J460-01-2FCV-609_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 674 | J270-06-1PNL-001 | J460-01-2FCV-609 | Alarm | J460-01-2FCV-609 - Room J6.06 - J460-01-1ACU-603 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-609_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-609_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 675 | J270-06-1PNL-001 | J460-01-2FCV-609 | Alarm | J460-01-2FCV-609 - Room J6.06 - J460-01-1ACU-603 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-609_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-609_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 676 | J270-06-1PNL-001 | J460-01-2FCV-609 | Measurement | J460-01-2FCV-609 - Room J6.06 - J460-01-1ACU-603 Cooling Valve Control Error Code | J460-01-2FCV-609_Err | J460-01-2FCV-609_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 677 | J270-06-1PNL-001 | J460-01-2FCV-610 | Alarm | J460-01-2FCV-610 - Room J6.06 - J460-01-1ACU-604 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-610_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-610_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 678 | J270-06-1PNL-001 | J460-01-2FCV-610 | Measurement | J460-01-2FCV-610 - Room J6.06 - J460-01-1ACU-604 Cooling Valve Control Forced Position | J460-01-2FCV-610_ForcePos | J460-01-2FCV-610_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 679 | J270-06-1PNL-001 | J460-01-2FCV-610 | Setting | J460-01-2FCV-610 - Room J6.06 - J460-01-1ACU-604 Cooling Valve Control Forced Calibration | J460-01-2FCV-610_ForceCal | J460-01-2FCV-610_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 680 | J270-06-1PNL-001 | J460-01-2FCV-610 | Measurement | J460-01-2FCV-610 - Room J6.06 - J460-01-1ACU-604 Cooling Valve Control Status | J460-01-2FCV-610_MotState | J460-01-2FCV-610_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 681 | J270-06-1PNL-001 | J460-01-2FCV-610 | Measurement | J460-01-2FCV-610 - Room J6.06 - J460-01-1ACU-604 Cooling Valve Control Actual SP | J460-01-2FCV-610_ActSP | J460-01-2FCV-610_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 682 | J270-06-1PNL-001 | J460-01-2FCV-610 | Setting | J460-01-2FCV-610 - Room J6.06 - J460-01-1ACU-604 Cooling Valve Control SP | J460-01-2FCV-610_SP | J460-01-2FCV-610_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 683 | J270-06-1PNL-001 | J460-01-2FCV-610 | Alarm | J460-01-2FCV-610 - Room J6.06 - J460-01-1ACU-604 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-610_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-610_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 684 | J270-06-1PNL-001 | J460-01-2FCV-610 | Alarm | J460-01-2FCV-610 - Room J6.06 - J460-01-1ACU-604 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-610_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-610_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 685 | J270-06-1PNL-001 | J460-01-2FCV-610 | Measurement | J460-01-2FCV-610 - Room J6.06 - J460-01-1ACU-604 Cooling Valve Control Error Code | J460-01-2FCV-610_Err | J460-01-2FCV-610_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 686 | J270-06-1PNL-001 | J460-01-1VAV-601 | Alarm | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control - Communication Failure Alarm | J460-01-1VAV-601_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-601_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 687 | J270-06-1PNL-001 | J460-01-1VAV-601 | Setting | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Flow Setpoint | J460-01-1VAV-601_SpRel | J460-01-1VAV-601_SpRel | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 688 | J270-06-1PNL-001 | J460-01-1VAV-601 | Measurement | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Relative Position | J460-01-1VAV-601_RelPos | J460-01-1VAV-601_RelPos | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 689 | J270-06-1PNL-001 | J460-01-1VAV-601 | Measurement | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Absolute Flow | J460-01-1VAV-601_AbsFlw | J460-01-1VAV-601_AbsFlw | 0 | 300 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 690 | J270-06-1PNL-001 | J460-01-1VAV-601 | Alarm | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-601_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-601_AbsFlwHiAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 691 | J270-06-1PNL-001 | J460-01-1VAV-601 | Setting | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Absolute Flow | J460-01-1VAV-601_AbsFlw_HASP | J460-01-1VAV-601_AbsFlw_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 692 | J270-06-1PNL-001 | J460-01-1VAV-601 | Alarm | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-601_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-601_AbsFlwLoAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 693 | J270-06-1PNL-001 | J460-01-1VAV-601 | Setting | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Absolute Flow | J460-01-1VAV-601_AbsFlw_LASP | J460-01-1VAV-601_AbsFlw_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 694 | J270-06-1PNL-001 | J460-01-1VAV-601 | Measurement | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Minimum Flow | J460-01-1VAV-601_Vmin | J460-01-1VAV-601_Vmin | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 695 | J270-06-1PNL-001 | J460-01-1VAV-601 | Measurement | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Maximum Flow | J460-01-1VAV-601_Vmax | J460-01-1VAV-601_Vmax | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 696 | J270-06-1PNL-001 | J460-01-1VAV-601 | Measurement | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Nominal Flow | J460-01-1VAV-601_Vnom | J460-01-1VAV-601_Vnom | 0 | 300 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 697 | J270-06-1PNL-001 | J460-01-1VAV-601 | Measurement | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Summary Status | J460-01-1VAV-601_SumSts | J460-01-1VAV-601_SumSts | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 698 | J270-06-1PNL-001 | J460-01-1VAV-601 | Alarm | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Summary Status Alarm | J460-01-1VAV-601_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-601_SumSts_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 699 | J270-06-1PNL-001 | J460-01-1VAV-601 | Measurement | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Actuator Status | J460-01-1VAV-601_ActSts | J460-01-1VAV-601_ActSts | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 700 | J270-06-1PNL-001 | J460-01-1VAV-601 | Measurement | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Device Status | J460-01-1VAV-601_DevSts | J460-01-1VAV-601_DevSts | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 701 | J270-06-1PNL-001 | J460-01-1VAV-601 | Setting | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Device Override | J460-01-1VAV-601_Override | J460-01-1VAV-601_Override | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 702 | J270-06-1PNL-001 | J460-01-1VAV-602 | Alarm | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control - Communication Failure Alarm | J460-01-1VAV-602_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-602_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 703 | J270-06-1PNL-001 | J460-01-1VAV-602 | Setting | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Flow Setpoint | J460-01-1VAV-602_SpRel | J460-01-1VAV-602_SpRel | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 704 | J270-06-1PNL-001 | J460-01-1VAV-602 | Measurement | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Relative Position | J460-01-1VAV-602_RelPos | J460-01-1VAV-602_RelPos | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 705 | J270-06-1PNL-001 | J460-01-1VAV-602 | Measurement | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Absolute Flow | J460-01-1VAV-602_AbsFlw | J460-01-1VAV-602_AbsFlw | 0 | 300 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 706 | J270-06-1PNL-001 | J460-01-1VAV-602 | Alarm | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-602_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-602_AbsFlwHiAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 707 | J270-06-1PNL-001 | J460-01-1VAV-602 | Setting | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Absolute Flow | J460-01-1VAV-602_AbsFlw_HASP | J460-01-1VAV-602_AbsFlw_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 708 | J270-06-1PNL-001 | J460-01-1VAV-602 | Alarm | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-602_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-602_AbsFlwLoAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 709 | J270-06-1PNL-001 | J460-01-1VAV-602 | Setting | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Absolute Flow | J460-01-1VAV-602_AbsFlw_LASP | J460-01-1VAV-602_AbsFlw_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 710 | J270-06-1PNL-001 | J460-01-1VAV-602 | Measurement | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Minimum Flow | J460-01-1VAV-602_Vmin | J460-01-1VAV-602_Vmin | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 711 | J270-06-1PNL-001 | J460-01-1VAV-602 | Measurement | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Maximum Flow | J460-01-1VAV-602_Vmax | J460-01-1VAV-602_Vmax | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 712 | J270-06-1PNL-001 | J460-01-1VAV-602 | Measurement | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Nominal Flow | J460-01-1VAV-602_Vnom | J460-01-1VAV-602_Vnom | 0 | 300 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 713 | J270-06-1PNL-001 | J460-01-1VAV-602 | Measurement | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Summary Status | J460-01-1VAV-602_SumSts | J460-01-1VAV-602_SumSts | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 714 | J270-06-1PNL-001 | J460-01-1VAV-602 | Alarm | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Summary Status Alarm | J460-01-1VAV-602_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-602_SumSts_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 715 | J270-06-1PNL-001 | J460-01-1VAV-602 | Measurement | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Actuator Status | J460-01-1VAV-602_ActSts | J460-01-1VAV-602_ActSts | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 716 | J270-06-1PNL-001 | J460-01-1VAV-602 | Measurement | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Device Status | J460-01-1VAV-602_DevSts | J460-01-1VAV-602_DevSts | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 717 | J270-06-1PNL-001 | J460-01-1VAV-602 | Setting | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Device Override | J460-01-1VAV-602_Override | J460-01-1VAV-602_Override | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 718 | J270-06-1PNL-001 | J460-01-1VAV-603 | Alarm | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control - Communication Failure Alarm | J460-01-1VAV-603_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-603_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 719 | J270-06-1PNL-001 | J460-01-1VAV-603 | Setting | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Flow Setpoint | J460-01-1VAV-603_SpRel | J460-01-1VAV-603_SpRel | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 720 | J270-06-1PNL-001 | J460-01-1VAV-603 | Measurement | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Relative Position | J460-01-1VAV-603_RelPos | J460-01-1VAV-603_RelPos | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 721 | J270-06-1PNL-001 | J460-01-1VAV-603 | Measurement | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-603_AbsFlw | J460-01-1VAV-603_AbsFlw | 0 | 400 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 722 | J270-06-1PNL-001 | J460-01-1VAV-603 | Alarm | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-603_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-603_AbsFlwHiAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 723 | J270-06-1PNL-001 | J460-01-1VAV-603 | Setting | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-603_AbsFlw_HASP | J460-01-1VAV-603_AbsFlw_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 724 | J270-06-1PNL-001 | J460-01-1VAV-603 | Alarm | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-603_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-603_AbsFlwLoAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 725 | J270-06-1PNL-001 | J460-01-1VAV-603 | Setting | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-603_AbsFlw_LASP | J460-01-1VAV-603_AbsFlw_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 726 | J270-06-1PNL-001 | J460-01-1VAV-603 | Measurement | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-603_Vmin | J460-01-1VAV-603_Vmin | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 727 | J270-06-1PNL-001 | J460-01-1VAV-603 | Measurement | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Maximum Flow | J460-01-1VAV-603_Vmax | J460-01-1VAV-603_Vmax | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 728 | J270-06-1PNL-001 | J460-01-1VAV-603 | Measurement | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-603_Vnom | J460-01-1VAV-603_Vnom | 0 | 400 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 729 | J270-06-1PNL-001 | J460-01-1VAV-603 | Measurement | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Summary Status | J460-01-1VAV-603_SumSts | J460-01-1VAV-603_SumSts | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 730 | J270-06-1PNL-001 | J460-01-1VAV-603 | Alarm | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Summary Status Alarm | J460-01-1VAV-603_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-603_SumSts_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 731 | J270-06-1PNL-001 | J460-01-1VAV-603 | Measurement | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Actuator Status | J460-01-1VAV-603_ActSts | J460-01-1VAV-603_ActSts | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 732 | J270-06-1PNL-001 | J460-01-1VAV-603 | Measurement | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Device Status | J460-01-1VAV-603_DevSts | J460-01-1VAV-603_DevSts | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 733 | J270-06-1PNL-001 | J460-01-1VAV-603 | Setting | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Device Override | J460-01-1VAV-603_Override | J460-01-1VAV-603_Override | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 734 | J270-06-1PNL-001 | J460-01-1VAV-604 | Alarm | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control - Communication Failure Alarm | J460-01-1VAV-604_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-604_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 735 | J270-06-1PNL-001 | J460-01-1VAV-604 | Setting | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Flow Setpoint | J460-01-1VAV-604_SpRel | J460-01-1VAV-604_SpRel | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 736 | J270-06-1PNL-001 | J460-01-1VAV-604 | Measurement | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Relative Position | J460-01-1VAV-604_RelPos | J460-01-1VAV-604_RelPos | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 737 | J270-06-1PNL-001 | J460-01-1VAV-604 | Measurement | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Absolute Flow | J460-01-1VAV-604_AbsFlw | J460-01-1VAV-604_AbsFlw | 0 | 200 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 738 | J270-06-1PNL-001 | J460-01-1VAV-604 | Alarm | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-604_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-604_AbsFlwHiAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 739 | J270-06-1PNL-001 | J460-01-1VAV-604 | Setting | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Absolute Flow | J460-01-1VAV-604_AbsFlw_HASP | J460-01-1VAV-604_AbsFlw_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 740 | J270-06-1PNL-001 | J460-01-1VAV-604 | Alarm | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-604_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-604_AbsFlwLoAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 741 | J270-06-1PNL-001 | J460-01-1VAV-604 | Setting | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Absolute Flow | J460-01-1VAV-604_AbsFlw_LASP | J460-01-1VAV-604_AbsFlw_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 742 | J270-06-1PNL-001 | J460-01-1VAV-604 | Measurement | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Minimum Flow | J460-01-1VAV-604_Vmin | J460-01-1VAV-604_Vmin | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 743 | J270-06-1PNL-001 | J460-01-1VAV-604 | Measurement | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Maximum Flow | J460-01-1VAV-604_Vmax | J460-01-1VAV-604_Vmax | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 744 | J270-06-1PNL-001 | J460-01-1VAV-604 | Measurement | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Nominal Flow | J460-01-1VAV-604_Vnom | J460-01-1VAV-604_Vnom | 0 | 200 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 745 | J270-06-1PNL-001 | J460-01-1VAV-604 | Measurement | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Summary Status | J460-01-1VAV-604_SumSts | J460-01-1VAV-604_SumSts | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 746 | J270-06-1PNL-001 | J460-01-1VAV-604 | Alarm | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Summary Status Alarm | J460-01-1VAV-604_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-604_SumSts_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 747 | J270-06-1PNL-001 | J460-01-1VAV-604 | Measurement | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Actuator Status | J460-01-1VAV-604_ActSts | J460-01-1VAV-604_ActSts | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 748 | J270-06-1PNL-001 | J460-01-1VAV-604 | Measurement | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Device Status | J460-01-1VAV-604_DevSts | J460-01-1VAV-604_DevSts | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 749 | J270-06-1PNL-001 | J460-01-1VAV-604 | Setting | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Device Override | J460-01-1VAV-604_Override | J460-01-1VAV-604_Override | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1.0 | 750 | J270-06-1PNL-001 | J460-01-2TC-612 | Alarm | J460-01-2TC-612 - Room J6.04 - MDF Room Controller - Communication Failure Alarm | J460-01-2TC-612_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TC-612_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 751 | J460-01-1CP-612 | J460-01-2TT-615 | Measurement | J460-01-2TT-615 - Room J6.04 - Temperature | J460-01-2TT-615_RmTemp | J460-01-2TT-615_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 752 | J460-01-1CP-612 | J460-01-2TT-615 | Alarm | J460-01-2TT-615 - Room J6.04 - Temperature High Alarm | J460-01-2TT-615_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-615_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
2.1 | 753 | J460-01-1CP-612 | J460-01-2TT-615 | Setting | J460-01-2TT-615 - Room J6.04 - Temperature | J460-01-2TT-615_RmTemp_HASP | J460-01-2TT-615_RmTemp_HASP | - | 30 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 754 | J460-01-1CP-612 | J460-01-2TT-615 | Alarm | J460-01-2TT-615 - Room J6.04 - Temperature Low Alarm | J460-01-2TT-615_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-615_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 755 | J460-01-1CP-612 | J460-01-2TT-615 | Setting | J460-01-2TT-615 - Room J6.04 - Temperature | J460-01-2TT-615_RmTemp_LASP | J460-01-2TT-615_RmTemp_LASP | 15 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 756 | J460-01-1CP-612 | J460-01-2MT-615 | Measurement | J460-01-2MT-615 - Room J6.04 - Humidity | J460-01-2MT-615_RmHum | J460-01-2MT-615_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 757 | J460-01-1CP-612 | J460-01-2MT-615 | Alarm | J460-01-2MT-615 - Room J6.04 - Humidity High Alarm | J460-01-2MT-615_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-615_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 758 | J460-01-1CP-612 | J460-01-2MT-615 | Setting | J460-01-2MT-615 - Room J6.04 - Humidity | J460-01-2MT-615_RmHum_HASP | J460-01-2MT-615_RmHum_HASP | - | 80 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 759 | J460-01-1CP-612 | J460-01-2MT-615 | Alarm | J460-01-2MT-615 - Room J6.04 - Humidity Low Alarm | J460-01-2MT-615_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-615_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 760 | J460-01-1CP-612 | J460-01-2MT-615 | Setting | J460-01-2MT-615 - Room J6.04 - Humidity | J460-01-2MT-615_RmHum_LASP | J460-01-2MT-615_RmHum_LASP | 20 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 761 | J460-01-1CP-612 | J460-01-2LA-601 | Measurement | J460-01-2LA-601 - Room J6.04 - Water Leakage Detection | J460-01-2LA-601_RmWtrLeakAlm | J460-01-2LA-601_RmWtrLeakAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 762 | J460-01-1CP-612 | J460-01-2LA-601 | Alarm | J460-01-2LA-601 - Room J6.04 - Water Leakage Detection Alarm | J460-01-2LA-601_RmWtrLeakAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2LA-601_RmWtrLeakAlm_Alm | 2 | Y | - | bar: State 2 to State 64
1.0 | 763 | J270-06-1PNL-001 | J460-01-1ACU-618 | Alarm | J460-01-1ACU-618 - Room J6.04 - Fan Coil Unit Control - Communication Failure Alarm | J460-01-1ACU-618_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1ACU-618_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 764 | J270-06-1PNL-001 | J460-01-1ACU-618 | Measurement | J460-01-1ACU-618 - Room J6.04 - Fan Coil Unit Control On/Off Status | J460-01-1ACU-618_OnOffSts | J460-01-1ACU-618_OnOffSts | OFF | ON | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 765 | J270-06-1PNL-001 | J460-01-1ACU-618 | Measurement | J460-01-1ACU-618 - Room J6.04 - Fan Coil Unit Control Runtime Hour | J460-01-1ACU-618_FCURunTimeHr | J460-01-1ACU-618_FCURunTimeHr | Calculated | Calculated | [11 empty] | - | - | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 766 | J270-06-1PNL-001 | J460-01-1ACU-618 | Measurement | J460-01-1ACU-618 - Room J6.04 - Fan Coil Unit Control Runtime Reset | J460-01-1ACU-618_FCURunTimeReset | J460-01-1ACU-618_FCURunTimeReset | OFF | ON | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 767 | J270-06-1PNL-001 | J460-01-1ACU-618 | Setting | J460-01-1ACU-618 - Room J6.04 - Fan Coil Unit Control On/Off Command | J460-01-1ACU-618_OnOffStsCmd | J460-01-1ACU-618_OnOffStsCmd | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 768 | J270-06-1PNL-001 | J460-01-1ACU-618 | Alarm | J460-01-1ACU-618 - Room J6.04 - Fan Coil Unit Control Fail to Start Alarm | J460-01-1ACU-618_FailToStartAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1ACU-618_FailToStartAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 769 | J270-06-1PNL-001 | J460-01-1ACU-618 | Alarm | J460-01-1ACU-618 - Room J6.04 - Fan Coil Unit Control Fail to Stop Alarm | J460-01-1ACU-618_FailToStopAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1ACU-618_FailToStopAlm | 4 | M | - | bar: State 2 to State 64
1.0 | 770 | J270-06-1PNL-001 | J460-01-1ACU-618 | Measurement | J460-01-1ACU-618 - Room J6.04 - Fan Coil Unit Control Mode Status | J460-01-1ACU-618_ModeSts | J460-01-1ACU-618_ModeSts | - | HEAT | COOL | FAN | DRY | AUTO | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 771 | J270-06-1PNL-001 | J460-01-1ACU-618 | Setting | J460-01-1ACU-618 - Room J6.04 - Fan Coil Unit Control Mode Command | J460-01-1ACU-618_ModeCmd | J460-01-1ACU-618_ModeCmd | - | HEAT | COOL | FAN | DRY | AUTO | - | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1.0 | 772 | J270-06-1PNL-001 | J460-01-1ACU-618 | Measurement | J460-01-1ACU-618 - Room J6.04 - Fan Coil Unit Control SP Status | J460-01-1ACU-618_SpSts | J460-01-1ACU-618_SpSts | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 773 | J270-06-1PNL-001 | J460-01-1ACU-618 | Setting | J460-01-1ACU-618 - Room J6.04 - Fan Coil Unit Control SP | J460-01-1ACU-618_Sp | J460-01-1ACU-618_Sp | - | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 774 | J270-06-1PNL-001 | J460-01-1ACU-618 | Measurement | J460-01-1ACU-618 - Room J6.04 - Fan Coil Unit Control Fan Speed Status | J460-01-1ACU-618_FanSpdSts | J460-01-1ACU-618_FanSpdSts | - | AUTO | FANSPD1 | FANSPD2 | FANSPD3 | FANSPD4 | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 775 | J270-06-1PNL-001 | J460-01-1ACU-618 | Setting | J460-01-1ACU-618 - Room J6.04 - Fan Coil Unit Control Fan Speed Command | J460-01-1ACU-618_FanSpdCmd | J460-01-1ACU-618_FanSpdCmd | - | AUTO | FANSPD1 | FANSPD2 | FANSPD3 | FANSPD4 | - | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1.0 | 776 | J270-06-1PNL-001 | J460-01-1ACU-618 | Measurement | J460-01-1ACU-618 - Room J6.04 - Fan Coil Unit Control Room Temperature | J460-01-1ACU-618_RmTemp | J460-01-1ACU-618_RmTemp | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 777 | J270-06-1PNL-001 | J460-01-1ACU-618 | Setting | J460-01-1ACU-618 - Room J6.04 - Fan Coil Unit Control Room Temperature SP | J460-01-1ACU-618_RmTempSP | J460-01-1ACU-618_RmTempSP | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 778 | J270-06-1PNL-001 | J460-01-1ACU-618 | Measurement | J460-01-1ACU-618 - Room J6.04 - Fan Coil Unit Control Alarm | J460-01-1ACU-618_Alm | J460-01-1ACU-618_Alm | NO | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 779 | J270-06-1PNL-001 | J460-01-1ACU-618 | Alarm | J460-01-1ACU-618 - Room J6.04 - Fan Coil Unit Control Alarm | J460-01-1ACU-618_Alm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1ACU-618_Alm_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 780 | J270-06-1PNL-001 | J460-01-1ACU-618 | Measurement | J460-01-1ACU-618 - Room J6.04 - Fan Coil Unit Control Occupied | J460-01-1ACU-618_OccSts | J460-01-1ACU-618_OccSts | - | OCC | UNOCC | DISABLED | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1.0 | 781 | J270-06-1PNL-001 | J460-01-1ACU-618 | Setting | J460-01-1ACU-618 - Room J6.04 - Fan Coil Unit Control Occupied Cooling SP | J460-01-1ACU-618_OccClgSP | J460-01-1ACU-618_OccClgSP | - | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 782 | J270-06-1PNL-001 | J460-01-1ACU-618 | Setting | J460-01-1ACU-618 - Room J6.04 - Fan Coil Unit Control Occupied Heating SP | J460-01-1ACU-618_OccHtgSP | J460-01-1ACU-618_OccHtgSP | - | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 783 | J270-06-1PNL-001 | J460-01-1ACU-618 | Setting | J460-01-1ACU-618 - Room J6.04 - Fan Coil Unit Control UnOccupied Cooling SP | J460-01-1ACU-618_UnOccClgSP | J460-01-1ACU-618_UnOccClgSP | - | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 784 | J270-06-1PNL-001 | J460-01-1ACU-618 | Setting | J460-01-1ACU-618 - Room J6.04 - Fan Coil Unit Control UnOccupied Heating SP | J460-01-1ACU-618_UnOccHtgSP | J460-01-1ACU-618_UnOccHtgSP | - | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 785 | J270-06-1PNL-001 | J460-01-1ACU-619 | Alarm | J460-01-1ACU-619 - Room J6.04 - Fan Coil Unit Control - Communication Failure Alarm | J460-01-1ACU-619_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1ACU-619_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 786 | J270-06-1PNL-001 | J460-01-1ACU-619 | Measurement | J460-01-1ACU-619 - Room J6.04 - Fan Coil Unit Control On/Off Status | J460-01-1ACU-619_OnOffSts | J460-01-1ACU-619_OnOffSts | OFF | ON | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 787 | J270-06-1PNL-001 | J460-01-1ACU-619 | Measurement | J460-01-1ACU-619 - Room J6.04 - Fan Coil Unit Control Runtime Hour | J460-01-1ACU-619_FCURunTimeHr | J460-01-1ACU-619_FCURunTimeHr | Calculated | Calculated | [11 empty] | - | - | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 788 | J270-06-1PNL-001 | J460-01-1ACU-619 | Measurement | J460-01-1ACU-619 - Room J6.04 - Fan Coil Unit Control Runtime Reset | J460-01-1ACU-619_FCURunTimeReset | J460-01-1ACU-619_FCURunTimeReset | OFF | ON | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 789 | J270-06-1PNL-001 | J460-01-1ACU-619 | Setting | J460-01-1ACU-619 - Room J6.04 - Fan Coil Unit Control On/Off Command | J460-01-1ACU-619_OnOffStsCmd | J460-01-1ACU-619_OnOffStsCmd | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 790 | J270-06-1PNL-001 | J460-01-1ACU-619 | Alarm | J460-01-1ACU-619 - Room J6.04 - Fan Coil Unit Control Fail to Start Alarm | J460-01-1ACU-619_FailToStartAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1ACU-619_FailToStartAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 791 | J270-06-1PNL-001 | J460-01-1ACU-619 | Alarm | J460-01-1ACU-619 - Room J6.04 - Fan Coil Unit Control Fail to Stop Alarm | J460-01-1ACU-619_FailToStopAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1ACU-619_FailToStopAlm | 4 | M | - | bar: State 2 to State 64
1.0 | 792 | J270-06-1PNL-001 | J460-01-1ACU-619 | Measurement | J460-01-1ACU-619 - Room J6.04 - Fan Coil Unit Control Mode Status | J460-01-1ACU-619_ModeSts | J460-01-1ACU-619_ModeSts | - | HEAT | COOL | FAN | DRY | AUTO | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 793 | J270-06-1PNL-001 | J460-01-1ACU-619 | Setting | J460-01-1ACU-619 - Room J6.04 - Fan Coil Unit Control Mode Command | J460-01-1ACU-619_ModeCmd | J460-01-1ACU-619_ModeCmd | - | HEAT | COOL | FAN | DRY | AUTO | - | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1.0 | 794 | J270-06-1PNL-001 | J460-01-1ACU-619 | Measurement | J460-01-1ACU-619 - Room J6.04 - Fan Coil Unit Control SP Status | J460-01-1ACU-619_SpSts | J460-01-1ACU-619_SpSts | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 795 | J270-06-1PNL-001 | J460-01-1ACU-619 | Setting | J460-01-1ACU-619 - Room J6.04 - Fan Coil Unit Control SP | J460-01-1ACU-619_Sp | J460-01-1ACU-619_Sp | - | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 796 | J270-06-1PNL-001 | J460-01-1ACU-619 | Measurement | J460-01-1ACU-619 - Room J6.04 - Fan Coil Unit Control Fan Speed Status | J460-01-1ACU-619_FanSpdSts | J460-01-1ACU-619_FanSpdSts | - | AUTO | FANSPD1 | FANSPD2 | FANSPD3 | FANSPD4 | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 797 | J270-06-1PNL-001 | J460-01-1ACU-619 | Setting | J460-01-1ACU-619 - Room J6.04 - Fan Coil Unit Control Fan Speed Command | J460-01-1ACU-619_FanSpdCmd | J460-01-1ACU-619_FanSpdCmd | - | AUTO | FANSPD1 | FANSPD2 | FANSPD3 | FANSPD4 | - | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1.0 | 798 | J270-06-1PNL-001 | J460-01-1ACU-619 | Measurement | J460-01-1ACU-619 - Room J6.04 - Fan Coil Unit Control Room Temperature | J460-01-1ACU-619_RmTemp | J460-01-1ACU-619_RmTemp | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 799 | J270-06-1PNL-001 | J460-01-1ACU-619 | Setting | J460-01-1ACU-619 - Room J6.04 - Fan Coil Unit Control Room Temperature SP | J460-01-1ACU-619_RmTempSP | J460-01-1ACU-619_RmTempSP | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 800 | J270-06-1PNL-001 | J460-01-1ACU-619 | Measurement | J460-01-1ACU-619 - Room J6.04 - Fan Coil Unit Control Alarm | J460-01-1ACU-619_Alm | J460-01-1ACU-619_Alm | NO | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 801 | J270-06-1PNL-001 | J460-01-1ACU-619 | Alarm | J460-01-1ACU-619 - Room J6.04 - Fan Coil Unit Control Alarm | J460-01-1ACU-619_Alm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1ACU-619_Alm_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 802 | J270-06-1PNL-001 | J460-01-1ACU-619 | Measurement | J460-01-1ACU-619 - Room J6.04 - Fan Coil Unit Control Occupied | J460-01-1ACU-619_OccSts | J460-01-1ACU-619_OccSts | - | OCC | UNOCC | DISABLED | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.1 | 803 | J270-06-1PNL-001 | J460-01-1ACU-619 | Setting | J460-01-1ACU-619 - Room J6.04 - Fan Coil Unit Control Occupied Cooling SP | J460-01-1ACU-619_OccClgSP | J460-01-1ACU-619_OccClgSP | 20 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 804 | J270-06-1PNL-001 | J460-01-1ACU-619 | Setting | J460-01-1ACU-619 - Room J6.04 - Fan Coil Unit Control Occupied Heating SP | J460-01-1ACU-619_OccHtgSP | J460-01-1ACU-619_OccHtgSP | 20 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 805 | J270-06-1PNL-001 | J460-01-1ACU-619 | Setting | J460-01-1ACU-619 - Room J6.04 - Fan Coil Unit Control UnOccupied Cooling SP | J460-01-1ACU-619_UnOccClgSP | J460-01-1ACU-619_UnOccClgSP | 20 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 806 | J270-06-1PNL-001 | J460-01-1ACU-619 | Setting | J460-01-1ACU-619 - Room J6.04 - Fan Coil Unit Control UnOccupied Heating SP | J460-01-1ACU-619_UnOccHtgSP | J460-01-1ACU-619_UnOccHtgSP | 20 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 807 | J270-06-1PNL-001 | N/A | Setting | J460-01-1ACU-618_619 - Room J6.04 - Fan Coil Unit Control Duty Selection | J460-01-1ACU-618_619_FCUDutySel | J460-01-1ACU-618_619_FCUDutySel | FCU618 | FCU619 | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 808 | J270-06-1PNL-001 | N/A | Setting | J460-01-1ACU-618_619 - Room J6.04 - Fan Coil Unit Control Run Hours Reset Start Minute | J460-01-1ACU-618_619_FCURstMin | J460-01-1ACU-618_619_FCURstMin | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 809 | J270-06-1PNL-001 | N/A | Setting | J460-01-1ACU-618_619 - Room J6.04 - Fan Coil Unit Control Run Hours Reset Start Hour | J460-01-1ACU-618_619_FCURstHr | J460-01-1ACU-618_619_FCURstHr | 2 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Hrs | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 810 | J270-06-1PNL-001 | N/A | Setting | J460-01-1ACU-618_619 - Room J6.04 - Fan Coil Unit Control Run Hours Reset Start Day | J460-01-1ACU-618_619_FCURstDay | J460-01-1ACU-618_619_FCURstDay | SUNDAY | MONDAY | TUESDAY | WEDNESDAY | THURSDAY | FRIDAY | SATURDAY | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1.0 | 811 | J270-06-1PNL-001 | J460-01-2TC-604 | Alarm | J460-01-2TC-604 - Room J6.07 - Room Controller - Communication Failure Alarm | J460-01-2TC-604_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TC-604_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 812 | J460-01-1CP-604 | J460-01-2TT-604 | Measurement | J460-01-2TT-604 - Room J6.07 - Temperature | J460-01-2TT-604_RmTemp | J460-01-2TT-604_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 813 | J460-01-1CP-604 | J460-01-2TT-604 | Alarm | J460-01-2TT-604 - Room J6.07 - Temperature High Alarm | J460-01-2TT-604_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-604_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 814 | J460-01-1CP-604 | J460-01-2TT-604 | Calculated | J460-01-2TT-604 - Room J6.07 - Temperature | J460-01-2TT-604_RmTemp_HASP | J460-01-2TT-604_RmTemp_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 815 | J460-01-1CP-604 | J460-01-2TT-604 | Alarm | J460-01-2TT-604 - Room J6.07 - Temperature Low Alarm | J460-01-2TT-604_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-604_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 816 | J460-01-1CP-604 | J460-01-2TT-604 | Calculated | J460-01-2TT-604 - Room J6.07 - Temperature | J460-01-2TT-604_RmTemp_LASP | J460-01-2TT-604_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 817 | J460-01-1CP-604 | J460-01-2TT-604 | Calculated | J460-01-2TT-604 - Room J6.07 - Temperature Effective Setpoint | J460-01-2TT-604_RmTempEffSetpoint | J460-01-2TT-604_RmTempEffSetpoint | Calculated | Calculated | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 818 | J460-01-1CP-604 | J460-01-2TT-604 | Setting | J460-01-2TT-604 - Room J6.07 - Temperature Setpoint CPA | J460-01-2TT-604_RmTempSetpointCPA | J460-01-2TT-604_RmTempSetpointCPA | -3 | 3 | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 819 | J460-01-1CP-604 | J460-01-2TT-604 | Setting | J460-01-2TT-604 - Room J6.07 - Temperature Proportional Band | J460-01-2TT-604_RmTemp_Set_P_Heat | J460-01-2TT-604_RmTemp_Set_P_Heat | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 820 | J460-01-1CP-604 | J460-01-2TT-604 | Setting | J460-01-2TT-604 - Room J6.07 - Temperature Integral Time | J460-01-2TT-604_RmTemp_Set_I_Heat | J460-01-2TT-604_RmTemp_Set_I_Heat | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 821 | J460-01-1CP-604 | J460-01-2TT-604 | Setting | J460-01-2TT-604 - Room J6.07 - Temperature Derivative Time | J460-01-2TT-604_RmTemp_Set_D_Heat | J460-01-2TT-604_RmTemp_Set_D_Heat | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 822 | J460-01-1CP-604 | J460-01-2TT-604 | Setting | J460-01-2TT-604 - Room J6.07 - Temperature Proportional Band | J460-01-2TT-604_RmTemp_Set_P_Cool | J460-01-2TT-604_RmTemp_Set_P_Cool | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 823 | J460-01-1CP-604 | J460-01-2TT-604 | Setting | J460-01-2TT-604 - Room J6.07 - Temperature Integral Time | J460-01-2TT-604_RmTemp_Set_I_Cool | J460-01-2TT-604_RmTemp_Set_I_Cool | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 824 | J460-01-1CP-604 | J460-01-2TT-604 | Setting | J460-01-2TT-604 - Room J6.07 - Temperature Derivative Time | J460-01-2TT-604_RmTemp_Set_D_Cool | J460-01-2TT-604_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 825 | J460-01-1CP-604 | J460-01-2MT-604 | Measurement | J460-01-2MT-604 - Room J6.07 - Humidity | J460-01-2MT-604_RmHum | J460-01-2MT-604_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 826 | J460-01-1CP-604 | J460-01-2MT-604 | Alarm | J460-01-2MT-604 - Room J6.07 - Humidity High Alarm | J460-01-2MT-604_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-604_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 827 | J460-01-1CP-604 | J460-01-2MT-604 | Setting | J460-01-2MT-604 - Room J6.07 - Humidity | J460-01-2MT-604_RmHum_HASP | J460-01-2MT-604_RmHum_HASP | - | 60 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 828 | J460-01-1CP-604 | J460-01-2MT-604 | Alarm | J460-01-2MT-604 - Room J6.07 - Humidity Low Alarm | J460-01-2MT-604_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-604_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 829 | J460-01-1CP-604 | J460-01-2MT-604 | Setting | J460-01-2MT-604 - Room J6.07 - Humidity | J460-01-2MT-604_RmHum_LASP | J460-01-2MT-604_RmHum_LASP | 30 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 830 | J460-01-1CP-604 | J460-01-2XT-604 | Measurement | J460-01-2XT-604 - Room J6.07 - CO2 Concentration | J460-01-2XT-604_RmCO2 | J460-01-2XT-604_RmCO2 | 0 | 2000 | [11 empty] | - | - | - | - | - | - | 200 | - | ppm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 831 | J460-01-1CP-604 | J460-01-2XT-604 | Alarm | J460-01-2XT-604 - Room J6.07 - CO2 Concentration High Alarm | J460-01-2XT-604_RmCO2HiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2XT-604_RmCO2HiAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 832 | J460-01-1CP-604 | J460-01-2XT-604 | Setting | J460-01-2XT-604 - Room J6.07 - CO2 Concentration | J460-01-2XT-604_RmCO2_HASP | J460-01-2XT-604_RmCO2_HASP | - | 1500 | [11 empty] | - | - | - | - | - | - | 200 | - | ppm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 833 | J460-01-1CP-604 | J460-01-2XT-604 | Setting | J460-01-2XT-604 - Room J6.07 - CO2 Concentration Setpoint | J460-01-2XT-604_RmCO2Setpoint | J460-01-2XT-604_RmCO2Setpoint | - | 800 | [11 empty] | - | - | - | - | - | - | 220 | - | ppm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 834 | J460-01-1CP-604 | J460-01-2XT-604 | Setting | J460-01-2XT-604 - Room J6.07 - CO2 Concentration Proportional Band | J460-01-2XT-604_RmCO2_Set_P | J460-01-2XT-604_RmCO2_Set_P | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 835 | J460-01-1CP-604 | J460-01-2XT-604 | Setting | J460-01-2XT-604 - Room J6.07 - CO2 Concentration Integral Time | J460-01-2XT-604_RmCO2_Set_I | J460-01-2XT-604_RmCO2_Set_I | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 836 | J460-01-1CP-604 | J460-01-2XT-604 | Setting | J460-01-2XT-604 - Room J6.07 - CO2 Concentration Derivative Time | J460-01-2XT-604_RmCO2_Set_D | J460-01-2XT-604_RmCO2_Set_D | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 837 | J460-01-1CP-604 | J460-01-2XT-615 | Measurement | J460-01-2XT-615 - Room J6.07 - Occupied | J460-01-2XT-615_RmOcc | J460-01-2XT-615_RmOcc | UNOCC | OCC | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 838 | J270-06-1PNL-001 | J460-01-2FCV-611 | Alarm | J460-01-2FCV-611 - Room J6.07 - Reheater Valve Control - Communication Failure Alarm | J460-01-2FCV-611_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-611_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 839 | J270-06-1PNL-001 | J460-01-2FCV-611 | Measurement | J460-01-2FCV-611 - Room J6.07 - Reheater Valve Control Forced Position | J460-01-2FCV-611_ForcePos | J460-01-2FCV-611_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 840 | J270-06-1PNL-001 | J460-01-2FCV-611 | Setting | J460-01-2FCV-611 - Room J6.07 - Reheater Valve Control Forced Calibration | J460-01-2FCV-611_ForceCal | J460-01-2FCV-611_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 841 | J270-06-1PNL-001 | J460-01-2FCV-611 | Measurement | J460-01-2FCV-611 - Room J6.07 - Reheater Valve Control Status | J460-01-2FCV-611_MotState | J460-01-2FCV-611_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 842 | J270-06-1PNL-001 | J460-01-2FCV-611 | Measurement | J460-01-2FCV-611 - Room J6.07 - Reheater Valve Control Actual SP | J460-01-2FCV-611_ActSP | J460-01-2FCV-611_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 843 | J270-06-1PNL-001 | J460-01-2FCV-611 | Setting | J460-01-2FCV-611 - Room J6.07 - Reheater Valve Control SP | J460-01-2FCV-611_SP | J460-01-2FCV-611_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 844 | J270-06-1PNL-001 | J460-01-2FCV-611 | Alarm | J460-01-2FCV-611 - Room J6.07 - Reheater Valve Control Fail to Open Alarm | J460-01-2FCV-611_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-611_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 845 | J270-06-1PNL-001 | J460-01-2FCV-611 | Alarm | J460-01-2FCV-611 - Room J6.07 - Reheater Valve Control Fail to Close Alarm | J460-01-2FCV-611_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-611_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 846 | J270-06-1PNL-001 | J460-01-2FCV-611 | Measurement | J460-01-2FCV-611 - Room J6.07 - Reheater Valve Control Error Code | J460-01-2FCV-611_Err | J460-01-2FCV-611_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 847 | J270-06-1PNL-001 | J460-01-1VAV-605 | Alarm | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control - Communication Failure Alarm | J460-01-1VAV-605_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-605_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 848 | J270-06-1PNL-001 | J460-01-1VAV-605 | Setting | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Flow Setpoint | J460-01-1VAV-605_SpRel | J460-01-1VAV-605_SpRel | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 849 | J270-06-1PNL-001 | J460-01-1VAV-605 | Measurement | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Relative Position | J460-01-1VAV-605_RelPos | J460-01-1VAV-605_RelPos | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 850 | J270-06-1PNL-001 | J460-01-1VAV-605 | Measurement | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-605_AbsFlw | J460-01-1VAV-605_AbsFlw | 0 | 350 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 851 | J270-06-1PNL-001 | J460-01-1VAV-605 | Alarm | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-605_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-605_AbsFlwHiAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 852 | J270-06-1PNL-001 | J460-01-1VAV-605 | Setting | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-605_AbsFlw_HASP | J460-01-1VAV-605_AbsFlw_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 853 | J270-06-1PNL-001 | J460-01-1VAV-605 | Alarm | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-605_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-605_AbsFlwLoAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 854 | J270-06-1PNL-001 | J460-01-1VAV-605 | Setting | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-605_AbsFlw_LASP | J460-01-1VAV-605_AbsFlw_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 855 | J270-06-1PNL-001 | J460-01-1VAV-605 | Measurement | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-605_Vmin | J460-01-1VAV-605_Vmin | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 856 | J270-06-1PNL-001 | J460-01-1VAV-605 | Measurement | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Maximum Flow | J460-01-1VAV-605_Vmax | J460-01-1VAV-605_Vmax | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 857 | J270-06-1PNL-001 | J460-01-1VAV-605 | Measurement | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-605_Vnom | J460-01-1VAV-605_Vnom | 0 | 350 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 858 | J270-06-1PNL-001 | J460-01-1VAV-605 | Measurement | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Summary Status | J460-01-1VAV-605_SumSts | J460-01-1VAV-605_SumSts | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 859 | J270-06-1PNL-001 | J460-01-1VAV-605 | Alarm | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Summary Status Alarm | J460-01-1VAV-605_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-605_SumSts_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 860 | J270-06-1PNL-001 | J460-01-1VAV-605 | Measurement | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Actuator Status | J460-01-1VAV-605_ActSts | J460-01-1VAV-605_ActSts | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 861 | J270-06-1PNL-001 | J460-01-1VAV-605 | Measurement | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Device Status | J460-01-1VAV-605_DevSts | J460-01-1VAV-605_DevSts | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 862 | J270-06-1PNL-001 | J460-01-1VAV-605 | Setting | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Device Override | J460-01-1VAV-605_Override | J460-01-1VAV-605_Override | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 863 | J270-06-1PNL-001 | J460-01-1VAV-606 | Alarm | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control - Communication Failure Alarm | J460-01-1VAV-606_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-606_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 864 | J270-06-1PNL-001 | J460-01-1VAV-606 | Setting | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Flow Setpoint | J460-01-1VAV-606_SpRel | J460-01-1VAV-606_SpRel | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 865 | J270-06-1PNL-001 | J460-01-1VAV-606 | Measurement | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Relative Position | J460-01-1VAV-606_RelPos | J460-01-1VAV-606_RelPos | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 866 | J270-06-1PNL-001 | J460-01-1VAV-606 | Measurement | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-606_AbsFlw | J460-01-1VAV-606_AbsFlw | 0 | 350 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 867 | J270-06-1PNL-001 | J460-01-1VAV-606 | Alarm | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-606_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-606_AbsFlwHiAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 868 | J270-06-1PNL-001 | J460-01-1VAV-606 | Setting | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-606_AbsFlw_HASP | J460-01-1VAV-606_AbsFlw_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 869 | J270-06-1PNL-001 | J460-01-1VAV-606 | Alarm | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-606_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-606_AbsFlwLoAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 870 | J270-06-1PNL-001 | J460-01-1VAV-606 | Setting | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-606_AbsFlw_LASP | J460-01-1VAV-606_AbsFlw_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 871 | J270-06-1PNL-001 | J460-01-1VAV-606 | Measurement | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-606_Vmin | J460-01-1VAV-606_Vmin | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 872 | J270-06-1PNL-001 | J460-01-1VAV-606 | Measurement | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Maximum Flow | J460-01-1VAV-606_Vmax | J460-01-1VAV-606_Vmax | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 873 | J270-06-1PNL-001 | J460-01-1VAV-606 | Measurement | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-606_Vnom | J460-01-1VAV-606_Vnom | 0 | 350 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 874 | J270-06-1PNL-001 | J460-01-1VAV-606 | Measurement | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Summary Status | J460-01-1VAV-606_SumSts | J460-01-1VAV-606_SumSts | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 875 | J270-06-1PNL-001 | J460-01-1VAV-606 | Alarm | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Summary Status Alarm | J460-01-1VAV-606_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-606_SumSts_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 876 | J270-06-1PNL-001 | J460-01-1VAV-606 | Measurement | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Actuator Status | J460-01-1VAV-606_ActSts | J460-01-1VAV-606_ActSts | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 877 | J270-06-1PNL-001 | J460-01-1VAV-606 | Measurement | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Device Status | J460-01-1VAV-606_DevSts | J460-01-1VAV-606_DevSts | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 878 | J270-06-1PNL-001 | J460-01-1VAV-606 | Setting | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Device Override | J460-01-1VAV-606_Override | J460-01-1VAV-606_Override | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1.0 | 879 | J270-06-1PNL-001 | J460-01-2FCV-612 | Alarm | J460-01-2FCV-612 - Room J6.06 - J460-01-1ACU-605 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-612_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-612_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 880 | J270-06-1PNL-001 | J460-01-2FCV-612 | Measurement | J460-01-2FCV-612 - Room J6.06 - J460-01-1ACU-605 Heating Valve Control Forced Position | J460-01-2FCV-612_ForcePos | J460-01-2FCV-612_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 881 | J270-06-1PNL-001 | J460-01-2FCV-612 | Setting | J460-01-2FCV-612 - Room J6.06 - J460-01-1ACU-605 Heating Valve Control Forced Calibration | J460-01-2FCV-612_ForceCal | J460-01-2FCV-612_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 882 | J270-06-1PNL-001 | J460-01-2FCV-612 | Measurement | J460-01-2FCV-612 - Room J6.06 - J460-01-1ACU-605 Heating Valve Control Status | J460-01-2FCV-612_MotState | J460-01-2FCV-612_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 883 | J270-06-1PNL-001 | J460-01-2FCV-612 | Measurement | J460-01-2FCV-612 - Room J6.06 - J460-01-1ACU-605 Heating Valve Control Actual SP | J460-01-2FCV-612_ActSP | J460-01-2FCV-612_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 884 | J270-06-1PNL-001 | J460-01-2FCV-612 | Setting | J460-01-2FCV-612 - Room J6.06 - J460-01-1ACU-605 Heating Valve Control SP | J460-01-2FCV-612_SP | J460-01-2FCV-612_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 885 | J270-06-1PNL-001 | J460-01-2FCV-612 | Alarm | J460-01-2FCV-612 - Room J6.06 - J460-01-1ACU-605 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-612_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-612_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 886 | J270-06-1PNL-001 | J460-01-2FCV-612 | Alarm | J460-01-2FCV-612 - Room J6.06 - J460-01-1ACU-605 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-612_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-612_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 887 | J270-06-1PNL-001 | J460-01-2FCV-612 | Measurement | J460-01-2FCV-612 - Room J6.06 - J460-01-1ACU-605 Heating Valve Control Error Code | J460-01-2FCV-612_Err | J460-01-2FCV-612_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 888 | J270-06-1PNL-001 | J460-01-2FCV-613 | Alarm | J460-01-2FCV-613 - Room J6.06 - J460-01-1ACU-606 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-613_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-613_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 889 | J270-06-1PNL-001 | J460-01-2FCV-613 | Measurement | J460-01-2FCV-613 - Room J6.06 - J460-01-1ACU-606 Heating Valve Control Forced Position | J460-01-2FCV-613_ForcePos | J460-01-2FCV-613_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 890 | J270-06-1PNL-001 | J460-01-2FCV-613 | Setting | J460-01-2FCV-613 - Room J6.06 - J460-01-1ACU-606 Heating Valve Control Forced Calibration | J460-01-2FCV-613_ForceCal | J460-01-2FCV-613_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 891 | J270-06-1PNL-001 | J460-01-2FCV-613 | Measurement | J460-01-2FCV-613 - Room J6.06 - J460-01-1ACU-606 Heating Valve Control Status | J460-01-2FCV-613_MotState | J460-01-2FCV-613_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 892 | J270-06-1PNL-001 | J460-01-2FCV-613 | Measurement | J460-01-2FCV-613 - Room J6.06 - J460-01-1ACU-606 Heating Valve Control Actual SP | J460-01-2FCV-613_ActSP | J460-01-2FCV-613_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 893 | J270-06-1PNL-001 | J460-01-2FCV-613 | Setting | J460-01-2FCV-613 - Room J6.06 - J460-01-1ACU-606 Heating Valve Control SP | J460-01-2FCV-613_SP | J460-01-2FCV-613_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 894 | J270-06-1PNL-001 | J460-01-2FCV-613 | Alarm | J460-01-2FCV-613 - Room J6.06 - J460-01-1ACU-606 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-613_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-613_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 895 | J270-06-1PNL-001 | J460-01-2FCV-613 | Alarm | J460-01-2FCV-613 - Room J6.06 - J460-01-1ACU-606 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-613_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-613_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 896 | J270-06-1PNL-001 | J460-01-2FCV-613 | Measurement | J460-01-2FCV-613 - Room J6.06 - J460-01-1ACU-606 Heating Valve Control Error Code | J460-01-2FCV-613_Err | J460-01-2FCV-613_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 897 | J270-06-1PNL-001 | J460-01-2FCV-614 | Alarm | J460-01-2FCV-614 - Room J6.06 - J460-01-1ACU-607 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-614_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-614_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 898 | J270-06-1PNL-001 | J460-01-2FCV-614 | Measurement | J460-01-2FCV-614 - Room J6.06 - J460-01-1ACU-607 Heating Valve Control Forced Position | J460-01-2FCV-614_ForcePos | J460-01-2FCV-614_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 899 | J270-06-1PNL-001 | J460-01-2FCV-614 | Setting | J460-01-2FCV-614 - Room J6.06 - J460-01-1ACU-607 Heating Valve Control Forced Calibration | J460-01-2FCV-614_ForceCal | J460-01-2FCV-614_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 900 | J270-06-1PNL-001 | J460-01-2FCV-614 | Measurement | J460-01-2FCV-614 - Room J6.06 - J460-01-1ACU-607 Heating Valve Control Status | J460-01-2FCV-614_MotState | J460-01-2FCV-614_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 901 | J270-06-1PNL-001 | J460-01-2FCV-614 | Measurement | J460-01-2FCV-614 - Room J6.06 - J460-01-1ACU-607 Heating Valve Control Actual SP | J460-01-2FCV-614_ActSP | J460-01-2FCV-614_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 902 | J270-06-1PNL-001 | J460-01-2FCV-614 | Setting | J460-01-2FCV-614 - Room J6.06 - J460-01-1ACU-607 Heating Valve Control SP | J460-01-2FCV-614_SP | J460-01-2FCV-614_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 903 | J270-06-1PNL-001 | J460-01-2FCV-614 | Alarm | J460-01-2FCV-614 - Room J6.06 - J460-01-1ACU-607 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-614_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-614_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 904 | J270-06-1PNL-001 | J460-01-2FCV-614 | Alarm | J460-01-2FCV-614 - Room J6.06 - J460-01-1ACU-607 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-614_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-614_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 905 | J270-06-1PNL-001 | J460-01-2FCV-614 | Measurement | J460-01-2FCV-614 - Room J6.06 - J460-01-1ACU-607 Heating Valve Control Error Code | J460-01-2FCV-614_Err | J460-01-2FCV-614_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 906 | J270-06-1PNL-001 | J460-01-2FCV-615 | Alarm | J460-01-2FCV-615 - Room J6.06 - J460-01-1ACU-608 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-615_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-615_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 907 | J270-06-1PNL-001 | J460-01-2FCV-615 | Measurement | J460-01-2FCV-615 - Room J6.06 - J460-01-1ACU-608 Heating Valve Control Forced Position | J460-01-2FCV-615_ForcePos | J460-01-2FCV-615_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 908 | J270-06-1PNL-001 | J460-01-2FCV-615 | Setting | J460-01-2FCV-615 - Room J6.06 - J460-01-1ACU-608 Heating Valve Control Forced Calibration | J460-01-2FCV-615_ForceCal | J460-01-2FCV-615_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 909 | J270-06-1PNL-001 | J460-01-2FCV-615 | Measurement | J460-01-2FCV-615 - Room J6.06 - J460-01-1ACU-608 Heating Valve Control Status | J460-01-2FCV-615_MotState | J460-01-2FCV-615_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 910 | J270-06-1PNL-001 | J460-01-2FCV-615 | Measurement | J460-01-2FCV-615 - Room J6.06 - J460-01-1ACU-608 Heating Valve Control Actual SP | J460-01-2FCV-615_ActSP | J460-01-2FCV-615_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 911 | J270-06-1PNL-001 | J460-01-2FCV-615 | Setting | J460-01-2FCV-615 - Room J6.06 - J460-01-1ACU-608 Heating Valve Control SP | J460-01-2FCV-615_SP | J460-01-2FCV-615_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 912 | J270-06-1PNL-001 | J460-01-2FCV-615 | Alarm | J460-01-2FCV-615 - Room J6.06 - J460-01-1ACU-608 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-615_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-615_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 913 | J270-06-1PNL-001 | J460-01-2FCV-615 | Alarm | J460-01-2FCV-615 - Room J6.06 - J460-01-1ACU-608 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-615_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-615_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 914 | J270-06-1PNL-001 | J460-01-2FCV-615 | Measurement | J460-01-2FCV-615 - Room J6.06 - J460-01-1ACU-608 Heating Valve Control Error Code | J460-01-2FCV-615_Err | J460-01-2FCV-615_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 915 | J270-06-1PNL-001 | J460-01-2FCV-616 | Alarm | J460-01-2FCV-616 - Room J6.06 - J460-01-1ACU-605 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-616_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-616_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 916 | J270-06-1PNL-001 | J460-01-2FCV-616 | Measurement | J460-01-2FCV-616 - Room J6.06 - J460-01-1ACU-605 Cooling Valve Control Forced Position | J460-01-2FCV-616_ForcePos | J460-01-2FCV-616_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 917 | J270-06-1PNL-001 | J460-01-2FCV-616 | Setting | J460-01-2FCV-616 - Room J6.06 - J460-01-1ACU-605 Cooling Valve Control Forced Calibration | J460-01-2FCV-616_ForceCal | J460-01-2FCV-616_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 918 | J270-06-1PNL-001 | J460-01-2FCV-616 | Measurement | J460-01-2FCV-616 - Room J6.06 - J460-01-1ACU-605 Cooling Valve Control Status | J460-01-2FCV-616_MotState | J460-01-2FCV-616_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 919 | J270-06-1PNL-001 | J460-01-2FCV-616 | Measurement | J460-01-2FCV-616 - Room J6.06 - J460-01-1ACU-605 Cooling Valve Control Actual SP | J460-01-2FCV-616_ActSP | J460-01-2FCV-616_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 920 | J270-06-1PNL-001 | J460-01-2FCV-616 | Setting | J460-01-2FCV-616 - Room J6.06 - J460-01-1ACU-605 Cooling Valve Control SP | J460-01-2FCV-616_SP | J460-01-2FCV-616_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 921 | J270-06-1PNL-001 | J460-01-2FCV-616 | Alarm | J460-01-2FCV-616 - Room J6.06 - J460-01-1ACU-605 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-616_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-616_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 922 | J270-06-1PNL-001 | J460-01-2FCV-616 | Alarm | J460-01-2FCV-616 - Room J6.06 - J460-01-1ACU-605 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-616_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-616_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 923 | J270-06-1PNL-001 | J460-01-2FCV-616 | Measurement | J460-01-2FCV-616 - Room J6.06 - J460-01-1ACU-605 Cooling Valve Control Error Code | J460-01-2FCV-616_Err | J460-01-2FCV-616_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 924 | J270-06-1PNL-001 | J460-01-2FCV-617 | Alarm | J460-01-2FCV-617 - Room J6.06 - J460-01-1ACU-606 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-617_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-617_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 925 | J270-06-1PNL-001 | J460-01-2FCV-617 | Measurement | J460-01-2FCV-617 - Room J6.06 - J460-01-1ACU-606 Cooling Valve Control Forced Position | J460-01-2FCV-617_ForcePos | J460-01-2FCV-617_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 926 | J270-06-1PNL-001 | J460-01-2FCV-617 | Setting | J460-01-2FCV-617 - Room J6.06 - J460-01-1ACU-606 Cooling Valve Control Forced Calibration | J460-01-2FCV-617_ForceCal | J460-01-2FCV-617_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 927 | J270-06-1PNL-001 | J460-01-2FCV-617 | Measurement | J460-01-2FCV-617 - Room J6.06 - J460-01-1ACU-606 Cooling Valve Control Status | J460-01-2FCV-617_MotState | J460-01-2FCV-617_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 928 | J270-06-1PNL-001 | J460-01-2FCV-617 | Measurement | J460-01-2FCV-617 - Room J6.06 - J460-01-1ACU-606 Cooling Valve Control Actual SP | J460-01-2FCV-617_ActSP | J460-01-2FCV-617_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 929 | J270-06-1PNL-001 | J460-01-2FCV-617 | Setting | J460-01-2FCV-617 - Room J6.06 - J460-01-1ACU-606 Cooling Valve Control SP | J460-01-2FCV-617_SP | J460-01-2FCV-617_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 930 | J270-06-1PNL-001 | J460-01-2FCV-617 | Alarm | J460-01-2FCV-617 - Room J6.06 - J460-01-1ACU-606 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-617_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-617_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 931 | J270-06-1PNL-001 | J460-01-2FCV-617 | Alarm | J460-01-2FCV-617 - Room J6.06 - J460-01-1ACU-606 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-617_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-617_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 932 | J270-06-1PNL-001 | J460-01-2FCV-617 | Measurement | J460-01-2FCV-617 - Room J6.06 - J460-01-1ACU-606 Cooling Valve Control Error Code | J460-01-2FCV-617_Err | J460-01-2FCV-617_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 933 | J270-06-1PNL-001 | J460-01-2FCV-618 | Alarm | J460-01-2FCV-618 - Room J6.06 - J460-01-1ACU-607 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-618_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-618_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 934 | J270-06-1PNL-001 | J460-01-2FCV-618 | Measurement | J460-01-2FCV-618 - Room J6.06 - J460-01-1ACU-607 Cooling Valve Control Forced Position | J460-01-2FCV-618_ForcePos | J460-01-2FCV-618_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 935 | J270-06-1PNL-001 | J460-01-2FCV-618 | Setting | J460-01-2FCV-618 - Room J6.06 - J460-01-1ACU-607 Cooling Valve Control Forced Calibration | J460-01-2FCV-618_ForceCal | J460-01-2FCV-618_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 936 | J270-06-1PNL-001 | J460-01-2FCV-618 | Measurement | J460-01-2FCV-618 - Room J6.06 - J460-01-1ACU-607 Cooling Valve Control Status | J460-01-2FCV-618_MotState | J460-01-2FCV-618_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 937 | J270-06-1PNL-001 | J460-01-2FCV-618 | Measurement | J460-01-2FCV-618 - Room J6.06 - J460-01-1ACU-607 Cooling Valve Control Actual SP | J460-01-2FCV-618_ActSP | J460-01-2FCV-618_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 938 | J270-06-1PNL-001 | J460-01-2FCV-618 | Setting | J460-01-2FCV-618 - Room J6.06 - J460-01-1ACU-607 Cooling Valve Control SP | J460-01-2FCV-618_SP | J460-01-2FCV-618_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 939 | J270-06-1PNL-001 | J460-01-2FCV-618 | Alarm | J460-01-2FCV-618 - Room J6.06 - J460-01-1ACU-607 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-618_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-618_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 940 | J270-06-1PNL-001 | J460-01-2FCV-618 | Alarm | J460-01-2FCV-618 - Room J6.06 - J460-01-1ACU-607 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-618_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-618_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 941 | J270-06-1PNL-001 | J460-01-2FCV-618 | Measurement | J460-01-2FCV-618 - Room J6.06 - J460-01-1ACU-607 Cooling Valve Control Error Code | J460-01-2FCV-618_Err | J460-01-2FCV-618_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 942 | J270-06-1PNL-001 | J460-01-2FCV-619 | Alarm | J460-01-2FCV-619 - Room J6.06 - J460-01-1ACU-608 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-619_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-619_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 943 | J270-06-1PNL-001 | J460-01-2FCV-619 | Measurement | J460-01-2FCV-619 - Room J6.06 - J460-01-1ACU-608 Cooling Valve Control Forced Position | J460-01-2FCV-619_ForcePos | J460-01-2FCV-619_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 944 | J270-06-1PNL-001 | J460-01-2FCV-619 | Setting | J460-01-2FCV-619 - Room J6.06 - J460-01-1ACU-608 Cooling Valve Control Forced Calibration | J460-01-2FCV-619_ForceCal | J460-01-2FCV-619_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 945 | J270-06-1PNL-001 | J460-01-2FCV-619 | Measurement | J460-01-2FCV-619 - Room J6.06 - J460-01-1ACU-608 Cooling Valve Control Status | J460-01-2FCV-619_MotState | J460-01-2FCV-619_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 946 | J270-06-1PNL-001 | J460-01-2FCV-619 | Measurement | J460-01-2FCV-619 - Room J6.06 - J460-01-1ACU-608 Cooling Valve Control Actual SP | J460-01-2FCV-619_ActSP | J460-01-2FCV-619_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 947 | J270-06-1PNL-001 | J460-01-2FCV-619 | Setting | J460-01-2FCV-619 - Room J6.06 - J460-01-1ACU-608 Cooling Valve Control SP | J460-01-2FCV-619_SP | J460-01-2FCV-619_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 948 | J270-06-1PNL-001 | J460-01-2FCV-619 | Alarm | J460-01-2FCV-619 - Room J6.06 - J460-01-1ACU-608 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-619_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-619_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 949 | J270-06-1PNL-001 | J460-01-2FCV-619 | Alarm | J460-01-2FCV-619 - Room J6.06 - J460-01-1ACU-608 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-619_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-619_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 950 | J270-06-1PNL-001 | J460-01-2FCV-619 | Measurement | J460-01-2FCV-619 - Room J6.06 - J460-01-1ACU-608 Cooling Valve Control Error Code | J460-01-2FCV-619_Err | J460-01-2FCV-619_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 951 | J270-06-1PNL-001 | J460-01-1VAV-608 | Alarm | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control - Communication Failure Alarm | J460-01-1VAV-608_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-608_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 952 | J270-06-1PNL-001 | J460-01-1VAV-608 | Setting | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Flow Setpoint | J460-01-1VAV-608_SpRel | J460-01-1VAV-608_SpRel | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 953 | J270-06-1PNL-001 | J460-01-1VAV-608 | Measurement | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Relative Position | J460-01-1VAV-608_RelPos | J460-01-1VAV-608_RelPos | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 954 | J270-06-1PNL-001 | J460-01-1VAV-608 | Measurement | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-608_AbsFlw | J460-01-1VAV-608_AbsFlw | 0 | 400 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 955 | J270-06-1PNL-001 | J460-01-1VAV-608 | Alarm | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-608_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-608_AbsFlwHiAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 956 | J270-06-1PNL-001 | J460-01-1VAV-608 | Setting | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-608_AbsFlw_HASP | J460-01-1VAV-608_AbsFlw_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 957 | J270-06-1PNL-001 | J460-01-1VAV-608 | Alarm | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-608_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-608_AbsFlwLoAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 958 | J270-06-1PNL-001 | J460-01-1VAV-608 | Setting | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-608_AbsFlw_LASP | J460-01-1VAV-608_AbsFlw_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 959 | J270-06-1PNL-001 | J460-01-1VAV-608 | Measurement | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-608_Vmin | J460-01-1VAV-608_Vmin | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 960 | J270-06-1PNL-001 | J460-01-1VAV-608 | Measurement | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Maximum Flow | J460-01-1VAV-608_Vmax | J460-01-1VAV-608_Vmax | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 961 | J270-06-1PNL-001 | J460-01-1VAV-608 | Measurement | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-608_Vnom | J460-01-1VAV-608_Vnom | 0 | 400 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 962 | J270-06-1PNL-001 | J460-01-1VAV-608 | Measurement | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Summary Status | J460-01-1VAV-608_SumSts | J460-01-1VAV-608_SumSts | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 963 | J270-06-1PNL-001 | J460-01-1VAV-608 | Alarm | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Summary Status Alarm | J460-01-1VAV-608_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-608_SumSts_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 964 | J270-06-1PNL-001 | J460-01-1VAV-608 | Measurement | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Actuator Status | J460-01-1VAV-608_ActSts | J460-01-1VAV-608_ActSts | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 965 | J270-06-1PNL-001 | J460-01-1VAV-608 | Measurement | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Device Status | J460-01-1VAV-608_DevSts | J460-01-1VAV-608_DevSts | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 966 | J270-06-1PNL-001 | J460-01-1VAV-608 | Setting | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Device Override | J460-01-1VAV-608_Override | J460-01-1VAV-608_Override | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 967 | J270-06-1PNL-001 | J460-01-1VAV-607 | Alarm | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control - Communication Failure Alarm | J460-01-1VAV-607_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-607_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 968 | J270-06-1PNL-001 | J460-01-1VAV-607 | Setting | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Flow Setpoint | J460-01-1VAV-607_SpRel | J460-01-1VAV-607_SpRel | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 969 | J270-06-1PNL-001 | J460-01-1VAV-607 | Measurement | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Relative Position | J460-01-1VAV-607_RelPos | J460-01-1VAV-607_RelPos | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 970 | J270-06-1PNL-001 | J460-01-1VAV-607 | Measurement | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Absolute Flow | J460-01-1VAV-607_AbsFlw | J460-01-1VAV-607_AbsFlw | 0 | 200 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 971 | J270-06-1PNL-001 | J460-01-1VAV-607 | Alarm | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-607_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-607_AbsFlwHiAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 972 | J270-06-1PNL-001 | J460-01-1VAV-607 | Setting | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Absolute Flow | J460-01-1VAV-607_AbsFlw_HASP | J460-01-1VAV-607_AbsFlw_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 973 | J270-06-1PNL-001 | J460-01-1VAV-607 | Alarm | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-607_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-607_AbsFlwLoAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 974 | J270-06-1PNL-001 | J460-01-1VAV-607 | Setting | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Absolute Flow | J460-01-1VAV-607_AbsFlw_LASP | J460-01-1VAV-607_AbsFlw_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 975 | J270-06-1PNL-001 | J460-01-1VAV-607 | Measurement | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Minimum Flow | J460-01-1VAV-607_Vmin | J460-01-1VAV-607_Vmin | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 976 | J270-06-1PNL-001 | J460-01-1VAV-607 | Measurement | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Maximum Flow | J460-01-1VAV-607_Vmax | J460-01-1VAV-607_Vmax | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 977 | J270-06-1PNL-001 | J460-01-1VAV-607 | Measurement | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Nominal Flow | J460-01-1VAV-607_Vnom | J460-01-1VAV-607_Vnom | 0 | 200 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 978 | J270-06-1PNL-001 | J460-01-1VAV-607 | Measurement | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Summary Status | J460-01-1VAV-607_SumSts | J460-01-1VAV-607_SumSts | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 979 | J270-06-1PNL-001 | J460-01-1VAV-607 | Alarm | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Summary Status Alarm | J460-01-1VAV-607_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-607_SumSts_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 980 | J270-06-1PNL-001 | J460-01-1VAV-607 | Measurement | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Actuator Status | J460-01-1VAV-607_ActSts | J460-01-1VAV-607_ActSts | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 981 | J270-06-1PNL-001 | J460-01-1VAV-607 | Measurement | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Device Status | J460-01-1VAV-607_DevSts | J460-01-1VAV-607_DevSts | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 982 | J270-06-1PNL-001 | J460-01-1VAV-607 | Setting | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Device Override | J460-01-1VAV-607_Override | J460-01-1VAV-607_Override | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1.0 | 983 | J270-06-1PNL-001 | J460-01-2TC-605 | Alarm | J460-01-2TC-605 - Room J6.05 - Room Controller - Communication Failure Alarm | J460-01-2TC-605_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TC-605_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 984 | J460-01-1CP-605 | J460-01-2TT-605 | Measurement | J460-01-2TT-605 - Room J6.05 - Temperature | J460-01-2TT-605_RmTemp | J460-01-2TT-605_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 985 | J460-01-1CP-605 | J460-01-2TT-605 | Alarm | J460-01-2TT-605 - Room J6.05 - Temperature High Alarm | J460-01-2TT-605_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-605_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 986 | J460-01-1CP-605 | J460-01-2TT-605 | Calculated | J460-01-2TT-605 - Room J6.05 - Temperature | J460-01-2TT-605_RmTemp_HASP | J460-01-2TT-605_RmTemp_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 987 | J460-01-1CP-605 | J460-01-2TT-605 | Alarm | J460-01-2TT-605 - Room J6.05 - Temperature Low Alarm | J460-01-2TT-605_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-605_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 988 | J460-01-1CP-605 | J460-01-2TT-605 | Calculated | J460-01-2TT-605 - Room J6.05 - Temperature | J460-01-2TT-605_RmTemp_LASP | J460-01-2TT-605_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 989 | J460-01-1CP-605 | J460-01-2TT-605 | Calculated | J460-01-2TT-605 - Room J6.05 - Temperature Effective Setpoint | J460-01-2TT-605_RmTempEffSetpoint | J460-01-2TT-605_RmTempEffSetpoint | Calculated | Calculated | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 990 | J460-01-1CP-605 | J460-01-2TT-605 | Setting | J460-01-2TT-605 - Room J6.05 - Temperature Setpoint CPA | J460-01-2TT-605_RmTempSetpointCPA | J460-01-2TT-605_RmTempSetpointCPA | -3 | 3 | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 991 | J460-01-1CP-605 | J460-01-2TT-605 | Setting | J460-01-2TT-605 - Room J6.05 - Temperature Proportional Band | J460-01-2TT-605_RmTemp_Set_P_Heat | J460-01-2TT-605_RmTemp_Set_P_Heat | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 992 | J460-01-1CP-605 | J460-01-2TT-605 | Setting | J460-01-2TT-605 - Room J6.05 - Temperature Integral Time | J460-01-2TT-605_RmTemp_Set_I_Heat | J460-01-2TT-605_RmTemp_Set_I_Heat | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 993 | J460-01-1CP-605 | J460-01-2TT-605 | Setting | J460-01-2TT-605 - Room J6.05 - Temperature Derivative Time | J460-01-2TT-605_RmTemp_Set_D_Heat | J460-01-2TT-605_RmTemp_Set_D_Heat | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 994 | J460-01-1CP-605 | J460-01-2TT-605 | Setting | J460-01-2TT-605 - Room J6.05 - Temperature Proportional Band | J460-01-2TT-605_RmTemp_Set_P_Cool | J460-01-2TT-605_RmTemp_Set_P_Cool | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 995 | J460-01-1CP-605 | J460-01-2TT-605 | Setting | J460-01-2TT-605 - Room J6.05 - Temperature Integral Time | J460-01-2TT-605_RmTemp_Set_I_Cool | J460-01-2TT-605_RmTemp_Set_I_Cool | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 996 | J460-01-1CP-605 | J460-01-2TT-605 | Setting | J460-01-2TT-605 - Room J6.05 - Temperature Derivative Time | J460-01-2TT-605_RmTemp_Set_D_Cool | J460-01-2TT-605_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 997 | J460-01-1CP-605 | J460-01-2MT-605 | Measurement | J460-01-2MT-605 - Room J6.05 - Humidity | J460-01-2MT-605_RmHum | J460-01-2MT-605_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 998 | J460-01-1CP-605 | J460-01-2MT-605 | Alarm | J460-01-2MT-605 - Room J6.05 - Humidity High Alarm | J460-01-2MT-605_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-605_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 999 | J460-01-1CP-605 | J460-01-2MT-605 | Setting | J460-01-2MT-605 - Room J6.05 - Humidity | J460-01-2MT-605_RmHum_HASP | J460-01-2MT-605_RmHum_HASP | - | 60 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1000 | J460-01-1CP-605 | J460-01-2MT-605 | Alarm | J460-01-2MT-605 - Room J6.05 - Humidity Low Alarm | J460-01-2MT-605_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-605_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1001 | J460-01-1CP-605 | J460-01-2MT-605 | Setting | J460-01-2MT-605 - Room J6.05 - Humidity | J460-01-2MT-605_RmHum_LASP | J460-01-2MT-605_RmHum_LASP | 30 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1002 | J460-01-1CP-605 | J460-01-2XT-605 | Measurement | J460-01-2XT-605 - Room J6.05 - CO2 Concentration | J460-01-2XT-605_RmCO2 | J460-01-2XT-605_RmCO2 | 0 | 2000 | [11 empty] | - | - | - | - | - | - | 200 | - | ppm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1003 | J460-01-1CP-605 | J460-01-2XT-605 | Alarm | J460-01-2XT-605 - Room J6.05 - CO2 Concentration High Alarm | J460-01-2XT-605_RmCO2HiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2XT-605_RmCO2HiAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1004 | J460-01-1CP-605 | J460-01-2XT-605 | Setting | J460-01-2XT-605 - Room J6.05 - CO2 Concentration | J460-01-2XT-605_RmCO2_HASP | J460-01-2XT-605_RmCO2_HASP | - | 1500 | [11 empty] | - | - | - | - | - | - | 200 | - | ppm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1005 | J460-01-1CP-605 | J460-01-2XT-605 | Setting | J460-01-2XT-605 - Room J6.05 - CO2 Concentration Setpoint | J460-01-2XT-605_RmCO2Setpoint | J460-01-2XT-605_RmCO2Setpoint | - | 800 | [11 empty] | - | - | - | - | - | - | 220 | - | ppm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1006 | J460-01-1CP-605 | J460-01-2XT-605 | Setting | J460-01-2XT-605 - Room J6.05 - CO2 Concentration Proportional Band | J460-01-2XT-605_RmCO2_Set_P | J460-01-2XT-605_RmCO2_Set_P | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1007 | J460-01-1CP-605 | J460-01-2XT-605 | Setting | J460-01-2XT-605 - Room J6.05 - CO2 Concentration Integral Time | J460-01-2XT-605_RmCO2_Set_I | J460-01-2XT-605_RmCO2_Set_I | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1008 | J460-01-1CP-605 | J460-01-2XT-605 | Setting | J460-01-2XT-605 - Room J6.05 - CO2 Concentration Derivative Time | J460-01-2XT-605_RmCO2_Set_D | J460-01-2XT-605_RmCO2_Set_D | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1009 | J460-01-1CP-605 | J460-01-2XT-616 | Measurement | J460-01-2XT-616 - Room J6.05 - Occupied | J460-01-2XT-616_RmOcc | J460-01-2XT-616_RmOcc | UNOCC | OCC | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1010 | J270-06-1PNL-001 | J460-01-2FCV-620 | Alarm | J460-01-2FCV-620 - Room J6.05 - Reheater Valve Control - Communication Failure Alarm | J460-01-2FCV-620_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-620_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1011 | J270-06-1PNL-001 | J460-01-2FCV-620 | Measurement | J460-01-2FCV-620 - Room J6.05 - Reheater Valve Control Forced Position | J460-01-2FCV-620_ForcePos | J460-01-2FCV-620_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1012 | J270-06-1PNL-001 | J460-01-2FCV-620 | Setting | J460-01-2FCV-620 - Room J6.05 - Reheater Valve Control Forced Calibration | J460-01-2FCV-620_ForceCal | J460-01-2FCV-620_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1013 | J270-06-1PNL-001 | J460-01-2FCV-620 | Measurement | J460-01-2FCV-620 - Room J6.05 - Reheater Valve Control Status | J460-01-2FCV-620_MotState | J460-01-2FCV-620_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1014 | J270-06-1PNL-001 | J460-01-2FCV-620 | Measurement | J460-01-2FCV-620 - Room J6.05 - Reheater Valve Control Actual SP | J460-01-2FCV-620_ActSP | J460-01-2FCV-620_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1015 | J270-06-1PNL-001 | J460-01-2FCV-620 | Setting | J460-01-2FCV-620 - Room J6.05 - Reheater Valve Control SP | J460-01-2FCV-620_SP | J460-01-2FCV-620_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1016 | J270-06-1PNL-001 | J460-01-2FCV-620 | Alarm | J460-01-2FCV-620 - Room J6.05 - Reheater Valve Control Fail to Open Alarm | J460-01-2FCV-620_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-620_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1017 | J270-06-1PNL-001 | J460-01-2FCV-620 | Alarm | J460-01-2FCV-620 - Room J6.05 - Reheater Valve Control Fail to Close Alarm | J460-01-2FCV-620_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-620_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1018 | J270-06-1PNL-001 | J460-01-2FCV-620 | Measurement | J460-01-2FCV-620 - Room J6.05 - Reheater Valve Control Error Code | J460-01-2FCV-620_Err | J460-01-2FCV-620_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1019 | J270-06-1PNL-001 | J460-01-1VAV-609 | Alarm | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control - Communication Failure Alarm | J460-01-1VAV-609_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-609_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1020 | J270-06-1PNL-001 | J460-01-1VAV-609 | Setting | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Flow Setpoint | J460-01-1VAV-609_SpRel | J460-01-1VAV-609_SpRel | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1021 | J270-06-1PNL-001 | J460-01-1VAV-609 | Measurement | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Relative Position | J460-01-1VAV-609_RelPos | J460-01-1VAV-609_RelPos | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1022 | J270-06-1PNL-001 | J460-01-1VAV-609 | Measurement | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-609_AbsFlw | J460-01-1VAV-609_AbsFlw | 0 | 250 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1023 | J270-06-1PNL-001 | J460-01-1VAV-609 | Alarm | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-609_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-609_AbsFlwHiAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1024 | J270-06-1PNL-001 | J460-01-1VAV-609 | Setting | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-609_AbsFlw_HASP | J460-01-1VAV-609_AbsFlw_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1025 | J270-06-1PNL-001 | J460-01-1VAV-609 | Alarm | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-609_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-609_AbsFlwLoAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1026 | J270-06-1PNL-001 | J460-01-1VAV-609 | Setting | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-609_AbsFlw_LASP | J460-01-1VAV-609_AbsFlw_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1027 | J270-06-1PNL-001 | J460-01-1VAV-609 | Measurement | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-609_Vmin | J460-01-1VAV-609_Vmin | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1028 | J270-06-1PNL-001 | J460-01-1VAV-609 | Measurement | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Maximum Flow | J460-01-1VAV-609_Vmax | J460-01-1VAV-609_Vmax | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1029 | J270-06-1PNL-001 | J460-01-1VAV-609 | Measurement | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-609_Vnom | J460-01-1VAV-609_Vnom | 0 | 250 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1030 | J270-06-1PNL-001 | J460-01-1VAV-609 | Measurement | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Summary Status | J460-01-1VAV-609_SumSts | J460-01-1VAV-609_SumSts | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1031 | J270-06-1PNL-001 | J460-01-1VAV-609 | Alarm | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Summary Status Alarm | J460-01-1VAV-609_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-609_SumSts_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 1032 | J270-06-1PNL-001 | J460-01-1VAV-609 | Measurement | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Actuator Status | J460-01-1VAV-609_ActSts | J460-01-1VAV-609_ActSts | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1033 | J270-06-1PNL-001 | J460-01-1VAV-609 | Measurement | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Device Status | J460-01-1VAV-609_DevSts | J460-01-1VAV-609_DevSts | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1034 | J270-06-1PNL-001 | J460-01-1VAV-609 | Setting | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Device Override | J460-01-1VAV-609_Override | J460-01-1VAV-609_Override | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1035 | J270-06-1PNL-001 | J460-01-1VAV-610 | Alarm | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control - Communication Failure Alarm | J460-01-1VAV-610_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-610_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1036 | J270-06-1PNL-001 | J460-01-1VAV-610 | Setting | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Flow Setpoint | J460-01-1VAV-610_SpRel | J460-01-1VAV-610_SpRel | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1037 | J270-06-1PNL-001 | J460-01-1VAV-610 | Measurement | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Relative Position | J460-01-1VAV-610_RelPos | J460-01-1VAV-610_RelPos | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1038 | J270-06-1PNL-001 | J460-01-1VAV-610 | Measurement | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Absolute Flow | J460-01-1VAV-610_AbsFlw | J460-01-1VAV-610_AbsFlw | 0 | 250 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1039 | J270-06-1PNL-001 | J460-01-1VAV-610 | Alarm | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-610_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-610_AbsFlwHiAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1040 | J270-06-1PNL-001 | J460-01-1VAV-610 | Setting | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Absolute Flow | J460-01-1VAV-610_AbsFlw_HASP | J460-01-1VAV-610_AbsFlw_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1041 | J270-06-1PNL-001 | J460-01-1VAV-610 | Alarm | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-610_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-610_AbsFlwLoAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1042 | J270-06-1PNL-001 | J460-01-1VAV-610 | Setting | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Absolute Flow | J460-01-1VAV-610_AbsFlw_LASP | J460-01-1VAV-610_AbsFlw_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1043 | J270-06-1PNL-001 | J460-01-1VAV-610 | Measurement | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Minimum Flow | J460-01-1VAV-610_Vmin | J460-01-1VAV-610_Vmin | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1044 | J270-06-1PNL-001 | J460-01-1VAV-610 | Measurement | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Maximum Flow | J460-01-1VAV-610_Vmax | J460-01-1VAV-610_Vmax | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1045 | J270-06-1PNL-001 | J460-01-1VAV-610 | Measurement | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Nominal Flow | J460-01-1VAV-610_Vnom | J460-01-1VAV-610_Vnom | 0 | 250 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1046 | J270-06-1PNL-001 | J460-01-1VAV-610 | Measurement | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Summary Status | J460-01-1VAV-610_SumSts | J460-01-1VAV-610_SumSts | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1047 | J270-06-1PNL-001 | J460-01-1VAV-610 | Alarm | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Summary Status Alarm | J460-01-1VAV-610_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-610_SumSts_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 1048 | J270-06-1PNL-001 | J460-01-1VAV-610 | Measurement | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Actuator Status | J460-01-1VAV-610_ActSts | J460-01-1VAV-610_ActSts | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1049 | J270-06-1PNL-001 | J460-01-1VAV-610 | Measurement | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Device Status | J460-01-1VAV-610_DevSts | J460-01-1VAV-610_DevSts | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1050 | J270-06-1PNL-001 | J460-01-1VAV-610 | Setting | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Device Override | J460-01-1VAV-610_Override | J460-01-1VAV-610_Override | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1051 | J270-06-1PNL-001 | J460-01-2FCV-621 | Alarm | J460-01-2FCV-621 - Room J6.06 - J460-01-1ACU-609 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-621_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-621_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1052 | J270-06-1PNL-001 | J460-01-2FCV-621 | Measurement | J460-01-2FCV-621 - Room J6.06 - J460-01-1ACU-609 Heating Valve Control Forced Position | J460-01-2FCV-621_ForcePos | J460-01-2FCV-621_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1053 | J270-06-1PNL-001 | J460-01-2FCV-621 | Setting | J460-01-2FCV-621 - Room J6.06 - J460-01-1ACU-609 Heating Valve Control Forced Calibration | J460-01-2FCV-621_ForceCal | J460-01-2FCV-621_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1054 | J270-06-1PNL-001 | J460-01-2FCV-621 | Measurement | J460-01-2FCV-621 - Room J6.06 - J460-01-1ACU-609 Heating Valve Control Status | J460-01-2FCV-621_MotState | J460-01-2FCV-621_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1055 | J270-06-1PNL-001 | J460-01-2FCV-621 | Measurement | J460-01-2FCV-621 - Room J6.06 - J460-01-1ACU-609 Heating Valve Control Actual SP | J460-01-2FCV-621_ActSP | J460-01-2FCV-621_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1056 | J270-06-1PNL-001 | J460-01-2FCV-621 | Setting | J460-01-2FCV-621 - Room J6.06 - J460-01-1ACU-609 Heating Valve Control SP | J460-01-2FCV-621_SP | J460-01-2FCV-621_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1057 | J270-06-1PNL-001 | J460-01-2FCV-621 | Alarm | J460-01-2FCV-621 - Room J6.06 - J460-01-1ACU-609 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-621_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-621_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1058 | J270-06-1PNL-001 | J460-01-2FCV-621 | Alarm | J460-01-2FCV-621 - Room J6.06 - J460-01-1ACU-609 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-621_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-621_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1059 | J270-06-1PNL-001 | J460-01-2FCV-621 | Measurement | J460-01-2FCV-621 - Room J6.06 - J460-01-1ACU-609 Heating Valve Control Error Code | J460-01-2FCV-621_Err | J460-01-2FCV-621_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1060 | J270-06-1PNL-001 | J460-01-2FCV-622 | Alarm | J460-01-2FCV-622 - Room J6.06 - J460-01-1ACU-609 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-622_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-622_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1061 | J270-06-1PNL-001 | J460-01-2FCV-622 | Measurement | J460-01-2FCV-622 - Room J6.06 - J460-01-1ACU-609 Cooling Valve Control Forced Position | J460-01-2FCV-622_ForcePos | J460-01-2FCV-622_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1062 | J270-06-1PNL-001 | J460-01-2FCV-622 | Setting | J460-01-2FCV-622 - Room J6.06 - J460-01-1ACU-609 Cooling Valve Control Forced Calibration | J460-01-2FCV-622_ForceCal | J460-01-2FCV-622_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1063 | J270-06-1PNL-001 | J460-01-2FCV-622 | Measurement | J460-01-2FCV-622 - Room J6.06 - J460-01-1ACU-609 Cooling Valve Control Status | J460-01-2FCV-622_MotState | J460-01-2FCV-622_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1064 | J270-06-1PNL-001 | J460-01-2FCV-622 | Measurement | J460-01-2FCV-622 - Room J6.06 - J460-01-1ACU-609 Cooling Valve Control Actual SP | J460-01-2FCV-622_ActSP | J460-01-2FCV-622_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1065 | J270-06-1PNL-001 | J460-01-2FCV-622 | Setting | J460-01-2FCV-622 - Room J6.06 - J460-01-1ACU-609 Cooling Valve Control SP | J460-01-2FCV-622_SP | J460-01-2FCV-622_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1066 | J270-06-1PNL-001 | J460-01-2FCV-622 | Alarm | J460-01-2FCV-622 - Room J6.06 - J460-01-1ACU-609 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-622_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-622_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1067 | J270-06-1PNL-001 | J460-01-2FCV-622 | Alarm | J460-01-2FCV-622 - Room J6.06 - J460-01-1ACU-609 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-622_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-622_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1068 | J270-06-1PNL-001 | J460-01-2FCV-622 | Measurement | J460-01-2FCV-622 - Room J6.06 - J460-01-1ACU-609 Cooling Valve Control Error Code | J460-01-2FCV-622_Err | J460-01-2FCV-622_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1069 | J270-06-1PNL-001 | J460-01-1VAV-611 | Alarm | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control - Communication Failure Alarm | J460-01-1VAV-611_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-611_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1070 | J270-06-1PNL-001 | J460-01-1VAV-611 | Setting | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Flow Setpoint | J460-01-1VAV-611_SpRel | J460-01-1VAV-611_SpRel | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1071 | J270-06-1PNL-001 | J460-01-1VAV-611 | Measurement | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Relative Position | J460-01-1VAV-611_RelPos | J460-01-1VAV-611_RelPos | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1072 | J270-06-1PNL-001 | J460-01-1VAV-611 | Measurement | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-611_AbsFlw | J460-01-1VAV-611_AbsFlw | 0 | 200 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1073 | J270-06-1PNL-001 | J460-01-1VAV-611 | Alarm | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-611_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-611_AbsFlwHiAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1074 | J270-06-1PNL-001 | J460-01-1VAV-611 | Setting | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-611_AbsFlw_HASP | J460-01-1VAV-611_AbsFlw_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1075 | J270-06-1PNL-001 | J460-01-1VAV-611 | Alarm | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-611_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-611_AbsFlwLoAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1076 | J270-06-1PNL-001 | J460-01-1VAV-611 | Setting | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-611_AbsFlw_LASP | J460-01-1VAV-611_AbsFlw_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1077 | J270-06-1PNL-001 | J460-01-1VAV-611 | Measurement | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-611_Vmin | J460-01-1VAV-611_Vmin | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1078 | J270-06-1PNL-001 | J460-01-1VAV-611 | Measurement | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Maximum Flow | J460-01-1VAV-611_Vmax | J460-01-1VAV-611_Vmax | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1079 | J270-06-1PNL-001 | J460-01-1VAV-611 | Measurement | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-611_Vnom | J460-01-1VAV-611_Vnom | 0 | 200 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1080 | J270-06-1PNL-001 | J460-01-1VAV-611 | Measurement | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Summary Status | J460-01-1VAV-611_SumSts | J460-01-1VAV-611_SumSts | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1081 | J270-06-1PNL-001 | J460-01-1VAV-611 | Alarm | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Summary Status Alarm | J460-01-1VAV-611_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-611_SumSts_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 1082 | J270-06-1PNL-001 | J460-01-1VAV-611 | Measurement | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Actuator Status | J460-01-1VAV-611_ActSts | J460-01-1VAV-611_ActSts | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1083 | J270-06-1PNL-001 | J460-01-1VAV-611 | Measurement | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Device Status | J460-01-1VAV-611_DevSts | J460-01-1VAV-611_DevSts | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1084 | J270-06-1PNL-001 | J460-01-1VAV-611 | Setting | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Device Override | J460-01-1VAV-611_Override | J460-01-1VAV-611_Override | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1085 | J270-06-1PNL-001 | J460-01-2TC-606 | Alarm | J460-01-2TC-606 - Room J6.08 - Room Controller - Communication Failure Alarm | J460-01-2TC-606_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TC-606_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1086 | J460-01-1CP-606 | J460-01-2TT-606 | Measurement | J460-01-2TT-606 - Room J6.08 - Temperature | J460-01-2TT-606_RmTemp | J460-01-2TT-606_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1087 | J460-01-1CP-606 | J460-01-2TT-606 | Alarm | J460-01-2TT-606 - Room J6.08 - Temperature High Alarm | J460-01-2TT-606_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-606_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1088 | J460-01-1CP-606 | J460-01-2TT-606 | Setting | J460-01-2TT-606 - Room J6.08 - Temperature | J460-01-2TT-606_RmTemp_HASP | J460-01-2TT-606_RmTemp_HASP | - | 28 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1089 | J460-01-1CP-606 | J460-01-2TT-606 | Alarm | J460-01-2TT-606 - Room J6.08 - Temperature Low Alarm | J460-01-2TT-606_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-606_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1090 | J460-01-1CP-606 | J460-01-2TT-606 | Calculated | J460-01-2TT-606 - Room J6.08 - Temperature | J460-01-2TT-606_RmTemp_LASP | J460-01-2TT-606_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1091 | J460-01-1CP-606 | J460-01-2TT-606 | Calculated | J460-01-2TT-606 - Room J6.08 - Temperature Effective Setpoint | J460-01-2TT-606_RmTempEffSetpoint | J460-01-2TT-606_RmTempEffSetpoint | Calculated | Calculated | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1092 | J460-01-1CP-606 | J460-01-2TT-606 | Setting | J460-01-2TT-606 - Room J6.08 - Temperature Setpoint CPA | J460-01-2TT-606_RmTempSetpointCPA | J460-01-2TT-606_RmTempSetpointCPA | -3 | 3 | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1093 | J460-01-1CP-606 | J460-01-2TT-606 | Setting | J460-01-2TT-606 - Room J6.08 - Temperature Proportional Band | J460-01-2TT-606_RmTemp_Set_P | J460-01-2TT-606_RmTemp_Set_P | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1094 | J460-01-1CP-606 | J460-01-2TT-606 | Setting | J460-01-2TT-606 - Room J6.08 - Temperature Integral Time | J460-01-2TT-606_RmTemp_Set_I | J460-01-2TT-606_RmTemp_Set_I | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1095 | J460-01-1CP-606 | J460-01-2TT-606 | Setting | J460-01-2TT-606 - Room J6.08 - Temperature Derivative Time | J460-01-2TT-606_RmTemp_Set_D | J460-01-2TT-606_RmTemp_Set_D | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1096 | J460-01-1CP-606 | J460-01-2MT-606 | Measurement | J460-01-2MT-606 - Room J6.08 - Humidity | J460-01-2MT-606_RmHum | J460-01-2MT-606_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1097 | J460-01-1CP-606 | J460-01-2MT-606 | Alarm | J460-01-2MT-606 - Room J6.08 - Humidity High Alarm | J460-01-2MT-606_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-606_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1098 | J460-01-1CP-606 | J460-01-2MT-606 | Setting | J460-01-2MT-606 - Room J6.08 - Humidity | J460-01-2MT-606_RmHum_HASP | J460-01-2MT-606_RmHum_HASP | - | 60 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1099 | J460-01-1CP-606 | J460-01-2MT-606 | Alarm | J460-01-2MT-606 - Room J6.08 - Humidity Low Alarm | J460-01-2MT-606_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-606_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1100 | J460-01-1CP-606 | J460-01-2MT-606 | Setting | J460-01-2MT-606 - Room J6.08 - Humidity | J460-01-2MT-606_RmHum_LASP | J460-01-2MT-606_RmHum_LASP | 30 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1101 | J460-01-1CP-606 | J460-01-2XT-617 | Measurement | J460-01-2XT-617 - Room J6.08 - Occupied | J460-01-2XT-617_RmOcc | J460-01-2XT-617_RmOcc | UNOCC | OCC | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1102 | J270-06-1PNL-001 | J460-01-2FCV-623 | Alarm | J460-01-2FCV-623 - Room J6.08 - Reheater Valve Control - Communication Failure Alarm | J460-01-2FCV-623_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-623_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1103 | J270-06-1PNL-001 | J460-01-2FCV-623 | Measurement | J460-01-2FCV-623 - Room J6.08 - Reheater Valve Control Forced Position | J460-01-2FCV-623_ForcePos | J460-01-2FCV-623_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1104 | J270-06-1PNL-001 | J460-01-2FCV-623 | Setting | J460-01-2FCV-623 - Room J6.08 - Reheater Valve Control Forced Calibration | J460-01-2FCV-623_ForceCal | J460-01-2FCV-623_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1105 | J270-06-1PNL-001 | J460-01-2FCV-623 | Measurement | J460-01-2FCV-623 - Room J6.08 - Reheater Valve Control Status | J460-01-2FCV-623_MotState | J460-01-2FCV-623_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1106 | J270-06-1PNL-001 | J460-01-2FCV-623 | Measurement | J460-01-2FCV-623 - Room J6.08 - Reheater Valve Control Actual SP | J460-01-2FCV-623_ActSP | J460-01-2FCV-623_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1107 | J270-06-1PNL-001 | J460-01-2FCV-623 | Setting | J460-01-2FCV-623 - Room J6.08 - Reheater Valve Control SP | J460-01-2FCV-623_SP | J460-01-2FCV-623_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1108 | J270-06-1PNL-001 | J460-01-2FCV-623 | Alarm | J460-01-2FCV-623 - Room J6.08 - Reheater Valve Control Fail to Open Alarm | J460-01-2FCV-623_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-623_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1109 | J270-06-1PNL-001 | J460-01-2FCV-623 | Alarm | J460-01-2FCV-623 - Room J6.08 - Reheater Valve Control Fail to Close Alarm | J460-01-2FCV-623_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-623_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1110 | J270-06-1PNL-001 | J460-01-2FCV-623 | Measurement | J460-01-2FCV-623 - Room J6.08 - Reheater Valve Control Error Code | J460-01-2FCV-623_Err | J460-01-2FCV-623_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1111 | J270-06-1PNL-001 | J460-01-2TC-607 | Alarm | J460-01-2TC-607 - Room J6.09 - Room Controller - Communication Failure Alarm | J460-01-2TC-607_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TC-607_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1112 | J460-01-1CP-607 | J460-01-2TT-607 | Measurement | J460-01-2TT-607 - Room J6.09 - Temperature | J460-01-2TT-607_RmTemp | J460-01-2TT-607_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1113 | J460-01-1CP-607 | J460-01-2TT-607 | Alarm | J460-01-2TT-607 - Room J6.09 - Temperature High Alarm | J460-01-2TT-607_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-607_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1114 | J460-01-1CP-607 | J460-01-2TT-607 | Calculated | J460-01-2TT-607 - Room J6.09 - Temperature | J460-01-2TT-607_RmTemp_HASP | J460-01-2TT-607_RmTemp_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1115 | J460-01-1CP-607 | J460-01-2TT-607 | Alarm | J460-01-2TT-607 - Room J6.09 - Temperature Low Alarm | J460-01-2TT-607_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-607_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1116 | J460-01-1CP-607 | J460-01-2TT-607 | Calculated | J460-01-2TT-607 - Room J6.09 - Temperature | J460-01-2TT-607_RmTemp_LASP | J460-01-2TT-607_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1117 | J460-01-1CP-607 | J460-01-2TT-607 | Calculated | J460-01-2TT-607 - Room J6.09 - Temperature Effective Setpoint | J460-01-2TT-607_RmTempEffSetpoint | J460-01-2TT-607_RmTempEffSetpoint | Calculated | Calculated | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1118 | J460-01-1CP-607 | J460-01-2TT-607 | Setting | J460-01-2TT-607 - Room J6.09 - Temperature Setpoint CPA | J460-01-2TT-607_RmTempSetpointCPA | J460-01-2TT-607_RmTempSetpointCPA | -3 | 3 | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1119 | J460-01-1CP-607 | J460-01-2TT-607 | Setting | J460-01-2TT-607 - Room J6.09- Temperature Proportional Band | J460-01-2TT-607_RmTemp_Set_P_Heat | J460-01-2TT-607_RmTemp_Set_P_Heat | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1120 | J460-01-1CP-607 | J460-01-2TT-607 | Setting | J460-01-2TT-607 - Room J6.09- Temperature Integral Time | J460-01-2TT-607_RmTemp_Set_I_Heat | J460-01-2TT-607_RmTemp_Set_I_Heat | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1121 | J460-01-1CP-607 | J460-01-2TT-607 | Setting | J460-01-2TT-607 - Room J6.09- Temperature Derivative Time | J460-01-2TT-607_RmTemp_Set_D_Heat | J460-01-2TT-607_RmTemp_Set_D_Heat | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1122 | J460-01-1CP-607 | J460-01-2TT-607 | Setting | J460-01-2TT-607 - Room J6.09- Temperature Proportional Band | J460-01-2TT-607_RmTemp_Set_P_Cool | J460-01-2TT-607_RmTemp_Set_P_Cool | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1123 | J460-01-1CP-607 | J460-01-2TT-607 | Setting | J460-01-2TT-607 - Room J6.09- Temperature Integral Time | J460-01-2TT-607_RmTemp_Set_I_Cool | J460-01-2TT-607_RmTemp_Set_I_Cool | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1124 | J460-01-1CP-607 | J460-01-2TT-607 | Setting | J460-01-2TT-607 - Room J6.09- Temperature Derivative Time | J460-01-2TT-607_RmTemp_Set_D_Cool | J460-01-2TT-607_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1125 | J460-01-1CP-607 | J460-01-2MT-607 | Measurement | J460-01-2MT-607 - Room J6.09 - Humidity | J460-01-2MT-607_RmHum | J460-01-2MT-607_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1126 | J460-01-1CP-607 | J460-01-2MT-607 | Alarm | J460-01-2MT-607 - Room J6.09 - Humidity High Alarm | J460-01-2MT-607_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-607_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1127 | J460-01-1CP-607 | J460-01-2MT-607 | Setting | J460-01-2MT-607 - Room J6.09 - Humidity | J460-01-2MT-607_RmHum_HASP | J460-01-2MT-607_RmHum_HASP | - | 60 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1128 | J460-01-1CP-607 | J460-01-2MT-607 | Alarm | J460-01-2MT-607 - Room J6.09 - Humidity Low Alarm | J460-01-2MT-607_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-607_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1129 | J460-01-1CP-607 | J460-01-2MT-607 | Setting | J460-01-2MT-607 - Room J6.09 - Humidity | J460-01-2MT-607_RmHum_LASP | J460-01-2MT-607_RmHum_LASP | 30 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1130 | J460-01-1CP-607 | J460-01-2XT-607 | Measurement | J460-01-2XT-607 - Room J6.09 - CO2 Concentration | J460-01-2XT-607_RmCO2 | J460-01-2XT-607_RmCO2 | 0 | 2000 | [11 empty] | - | - | - | - | - | - | 200 | - | ppm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1131 | J460-01-1CP-607 | J460-01-2XT-607 | Alarm | J460-01-2XT-607 - Room J6.09 - CO2 Concentration High Alarm | J460-01-2XT-607_RmCO2HiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2XT-607_RmCO2HiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1132 | J460-01-1CP-607 | J460-01-2XT-607 | Setting | J460-01-2XT-607 - Room J6.09 - CO2 Concentration | J460-01-2XT-607_RmCO2_HASP | J460-01-2XT-607_RmCO2_HASP | - | 1500 | [11 empty] | - | - | - | - | - | - | 200 | - | ppm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1133 | J460-01-1CP-607 | J460-01-2XT-607 | Setting | J460-01-2XT-607 - Room J6.09 - CO2 Concentration Setpoint | J460-01-2XT-607_RmCO2Setpoint | J460-01-2XT-607_RmCO2Setpoint | - | 800 | [11 empty] | - | - | - | - | - | - | 220 | - | ppm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1134 | J460-01-1CP-607 | J460-01-2XT-607 | Setting | J460-01-2XT-607 - Room J6.09 - CO2 Concentration Proportional Band | J460-01-2XT-607_RmCO2_Set_P | J460-01-2XT-607_RmCO2_Set_P | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1135 | J460-01-1CP-607 | J460-01-2XT-607 | Setting | J460-01-2XT-607 - Room J6.09 - CO2 Concentration Integral Time | J460-01-2XT-607_RmCO2_Set_I | J460-01-2XT-607_RmCO2_Set_I | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1136 | J460-01-1CP-607 | J460-01-2XT-607 | Setting | J460-01-2XT-607 - Room J6.09 - CO2 Concentration Derivative Time | J460-01-2XT-607_RmCO2_Set_D | J460-01-2XT-607_RmCO2_Set_D | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1137 | J460-01-1CP-607 | J460-01-2XT-618 | Measurement | J460-01-2XT-618 - Room J6.09 - Occupied | J460-01-2XT-618_RmOcc | J460-01-2XT-618_RmOcc | UNOCC | OCC | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1138 | J270-06-1PNL-001 | J460-01-2FCV-624 | Alarm | J460-01-2FCV-624 - Room J6.09 - J460-01-1ACU-610 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-624_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-624_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1139 | J270-06-1PNL-001 | J460-01-2FCV-624 | Measurement | J460-01-2FCV-624 - Room J6.09 - J460-01-1ACU-610 Heating Valve Control Forced Position | J460-01-2FCV-624_ForcePos | J460-01-2FCV-624_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1140 | J270-06-1PNL-001 | J460-01-2FCV-624 | Setting | J460-01-2FCV-624 - Room J6.09 - J460-01-1ACU-610 Heating Valve Control Forced Calibration | J460-01-2FCV-624_ForceCal | J460-01-2FCV-624_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1141 | J270-06-1PNL-001 | J460-01-2FCV-624 | Measurement | J460-01-2FCV-624 - Room J6.09 - J460-01-1ACU-610 Heating Valve Control Status | J460-01-2FCV-624_MotState | J460-01-2FCV-624_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1142 | J270-06-1PNL-001 | J460-01-2FCV-624 | Measurement | J460-01-2FCV-624 - Room J6.09 - J460-01-1ACU-610 Heating Valve Control Actual SP | J460-01-2FCV-624_ActSP | J460-01-2FCV-624_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1143 | J270-06-1PNL-001 | J460-01-2FCV-624 | Setting | J460-01-2FCV-624 - Room J6.09 - J460-01-1ACU-610 Heating Valve Control SP | J460-01-2FCV-624_SP | J460-01-2FCV-624_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1144 | J270-06-1PNL-001 | J460-01-2FCV-624 | Alarm | J460-01-2FCV-624 - Room J6.09 - J460-01-1ACU-610 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-624_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-624_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1145 | J270-06-1PNL-001 | J460-01-2FCV-624 | Alarm | J460-01-2FCV-624 - Room J6.09 - J460-01-1ACU-610 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-624_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-624_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1146 | J270-06-1PNL-001 | J460-01-2FCV-624 | Measurement | J460-01-2FCV-624 - Room J6.09 - J460-01-1ACU-610 Heating Valve Control Error Code | J460-01-2FCV-624_Err | J460-01-2FCV-624_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1147 | J270-06-1PNL-001 | J460-01-2FCV-625 | Alarm | J460-01-2FCV-625 - Room J6.09 - J460-01-1ACU-611 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-625_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-625_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1148 | J270-06-1PNL-001 | J460-01-2FCV-625 | Measurement | J460-01-2FCV-625 - Room J6.09 - J460-01-1ACU-611 Heating Valve Control Forced Position | J460-01-2FCV-625_ForcePos | J460-01-2FCV-625_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1149 | J270-06-1PNL-001 | J460-01-2FCV-625 | Setting | J460-01-2FCV-625 - Room J6.09 - J460-01-1ACU-611 Heating Valve Control Forced Calibration | J460-01-2FCV-625_ForceCal | J460-01-2FCV-625_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1150 | J270-06-1PNL-001 | J460-01-2FCV-625 | Measurement | J460-01-2FCV-625 - Room J6.09 - J460-01-1ACU-611 Heating Valve Control Status | J460-01-2FCV-625_MotState | J460-01-2FCV-625_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1151 | J270-06-1PNL-001 | J460-01-2FCV-625 | Measurement | J460-01-2FCV-625 - Room J6.09 - J460-01-1ACU-611 Heating Valve Control Actual SP | J460-01-2FCV-625_ActSP | J460-01-2FCV-625_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1152 | J270-06-1PNL-001 | J460-01-2FCV-625 | Setting | J460-01-2FCV-625 - Room J6.09 - J460-01-1ACU-611 Heating Valve Control SP | J460-01-2FCV-625_SP | J460-01-2FCV-625_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1153 | J270-06-1PNL-001 | J460-01-2FCV-625 | Alarm | J460-01-2FCV-625 - Room J6.09 - J460-01-1ACU-611 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-625_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-625_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1154 | J270-06-1PNL-001 | J460-01-2FCV-625 | Alarm | J460-01-2FCV-625 - Room J6.09 - J460-01-1ACU-611 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-625_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-625_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1155 | J270-06-1PNL-001 | J460-01-2FCV-625 | Measurement | J460-01-2FCV-625 - Room J6.09 - J460-01-1ACU-611 Heating Valve Control Error Code | J460-01-2FCV-625_Err | J460-01-2FCV-625_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1156 | J270-06-1PNL-001 | J460-01-2FCV-626 | Alarm | J460-01-2FCV-626 - Room J6.09 - J460-01-1ACU-612 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-626_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-626_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1157 | J270-06-1PNL-001 | J460-01-2FCV-626 | Measurement | J460-01-2FCV-626 - Room J6.09 - J460-01-1ACU-612 Heating Valve Control Forced Position | J460-01-2FCV-626_ForcePos | J460-01-2FCV-626_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1158 | J270-06-1PNL-001 | J460-01-2FCV-626 | Setting | J460-01-2FCV-626 - Room J6.09 - J460-01-1ACU-612 Heating Valve Control Forced Calibration | J460-01-2FCV-626_ForceCal | J460-01-2FCV-626_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1159 | J270-06-1PNL-001 | J460-01-2FCV-626 | Measurement | J460-01-2FCV-626 - Room J6.09 - J460-01-1ACU-612 Heating Valve Control Status | J460-01-2FCV-626_MotState | J460-01-2FCV-626_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1160 | J270-06-1PNL-001 | J460-01-2FCV-626 | Measurement | J460-01-2FCV-626 - Room J6.09 - J460-01-1ACU-612 Heating Valve Control Actual SP | J460-01-2FCV-626_ActSP | J460-01-2FCV-626_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1161 | J270-06-1PNL-001 | J460-01-2FCV-626 | Setting | J460-01-2FCV-626 - Room J6.09 - J460-01-1ACU-612 Heating Valve Control SP | J460-01-2FCV-626_SP | J460-01-2FCV-626_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1162 | J270-06-1PNL-001 | J460-01-2FCV-626 | Alarm | J460-01-2FCV-626 - Room J6.09 - J460-01-1ACU-612 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-626_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-626_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1163 | J270-06-1PNL-001 | J460-01-2FCV-626 | Alarm | J460-01-2FCV-626 - Room J6.09 - J460-01-1ACU-612 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-626_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-626_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1164 | J270-06-1PNL-001 | J460-01-2FCV-626 | Measurement | J460-01-2FCV-626 - Room J6.09 - J460-01-1ACU-612 Heating Valve Control Error Code | J460-01-2FCV-626_Err | J460-01-2FCV-626_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1165 | J270-06-1PNL-001 | J460-01-2FCV-627 | Alarm | J460-01-2FCV-627 - Room J6.09 - J460-01-1ACU-613 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-627_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-627_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1166 | J270-06-1PNL-001 | J460-01-2FCV-627 | Measurement | J460-01-2FCV-627 - Room J6.09 - J460-01-1ACU-613 Heating Valve Control Forced Position | J460-01-2FCV-627_ForcePos | J460-01-2FCV-627_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1167 | J270-06-1PNL-001 | J460-01-2FCV-627 | Setting | J460-01-2FCV-627 - Room J6.09 - J460-01-1ACU-613 Heating Valve Control Forced Calibration | J460-01-2FCV-627_ForceCal | J460-01-2FCV-627_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1168 | J270-06-1PNL-001 | J460-01-2FCV-627 | Measurement | J460-01-2FCV-627 - Room J6.09 - J460-01-1ACU-613 Heating Valve Control Status | J460-01-2FCV-627_MotState | J460-01-2FCV-627_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1169 | J270-06-1PNL-001 | J460-01-2FCV-627 | Measurement | J460-01-2FCV-627 - Room J6.09 - J460-01-1ACU-613 Heating Valve Control Actual SP | J460-01-2FCV-627_ActSP | J460-01-2FCV-627_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1170 | J270-06-1PNL-001 | J460-01-2FCV-627 | Setting | J460-01-2FCV-627 - Room J6.09 - J460-01-1ACU-613 Heating Valve Control SP | J460-01-2FCV-627_SP | J460-01-2FCV-627_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1171 | J270-06-1PNL-001 | J460-01-2FCV-627 | Alarm | J460-01-2FCV-627 - Room J6.09 - J460-01-1ACU-613 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-627_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-627_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1172 | J270-06-1PNL-001 | J460-01-2FCV-627 | Alarm | J460-01-2FCV-627 - Room J6.09 - J460-01-1ACU-613 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-627_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-627_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1173 | J270-06-1PNL-001 | J460-01-2FCV-627 | Measurement | J460-01-2FCV-627 - Room J6.09 - J460-01-1ACU-613 Heating Valve Control Error Code | J460-01-2FCV-627_Err | J460-01-2FCV-627_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1174 | J270-06-1PNL-001 | J460-01-2FCV-628 | Alarm | J460-01-2FCV-628 - Room J6.09 - J460-01-1ACU-610 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-628_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-628_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1175 | J270-06-1PNL-001 | J460-01-2FCV-628 | Measurement | J460-01-2FCV-628 - Room J6.09 - J460-01-1ACU-610 Cooling Valve Control Forced Position | J460-01-2FCV-628_ForcePos | J460-01-2FCV-628_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1176 | J270-06-1PNL-001 | J460-01-2FCV-628 | Setting | J460-01-2FCV-628 - Room J6.09 - J460-01-1ACU-610 Cooling Valve Control Forced Calibration | J460-01-2FCV-628_ForceCal | J460-01-2FCV-628_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1177 | J270-06-1PNL-001 | J460-01-2FCV-628 | Measurement | J460-01-2FCV-628 - Room J6.09 - J460-01-1ACU-610 Cooling Valve Control Status | J460-01-2FCV-628_MotState | J460-01-2FCV-628_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1178 | J270-06-1PNL-001 | J460-01-2FCV-628 | Measurement | J460-01-2FCV-628 - Room J6.09 - J460-01-1ACU-610 Cooling Valve Control Actual SP | J460-01-2FCV-628_ActSP | J460-01-2FCV-628_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1179 | J270-06-1PNL-001 | J460-01-2FCV-628 | Setting | J460-01-2FCV-628 - Room J6.09 - J460-01-1ACU-610 Cooling Valve Control SP | J460-01-2FCV-628_SP | J460-01-2FCV-628_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1180 | J270-06-1PNL-001 | J460-01-2FCV-628 | Alarm | J460-01-2FCV-628 - Room J6.09 - J460-01-1ACU-610 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-628_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-628_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1181 | J270-06-1PNL-001 | J460-01-2FCV-628 | Alarm | J460-01-2FCV-628 - Room J6.09 - J460-01-1ACU-610 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-628_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-628_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1182 | J270-06-1PNL-001 | J460-01-2FCV-628 | Measurement | J460-01-2FCV-628 - Room J6.09 - J460-01-1ACU-610 Cooling Valve Control Error Code | J460-01-2FCV-628_Err | J460-01-2FCV-628_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1183 | J270-06-1PNL-001 | J460-01-2FCV-629 | Alarm | J460-01-2FCV-629 - Room J6.09 - J460-01-1ACU-611 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-629_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-629_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1184 | J270-06-1PNL-001 | J460-01-2FCV-629 | Measurement | J460-01-2FCV-629 - Room J6.09 - J460-01-1ACU-611 Cooling Valve Control Forced Position | J460-01-2FCV-629_ForcePos | J460-01-2FCV-629_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1185 | J270-06-1PNL-001 | J460-01-2FCV-629 | Setting | J460-01-2FCV-629 - Room J6.09 - J460-01-1ACU-611 Cooling Valve Control Forced Calibration | J460-01-2FCV-629_ForceCal | J460-01-2FCV-629_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1186 | J270-06-1PNL-001 | J460-01-2FCV-629 | Measurement | J460-01-2FCV-629 - Room J6.09 - J460-01-1ACU-611 Cooling Valve Control Status | J460-01-2FCV-629_MotState | J460-01-2FCV-629_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1187 | J270-06-1PNL-001 | J460-01-2FCV-629 | Measurement | J460-01-2FCV-629 - Room J6.09 - J460-01-1ACU-611 Cooling Valve Control Actual SP | J460-01-2FCV-629_ActSP | J460-01-2FCV-629_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1188 | J270-06-1PNL-001 | J460-01-2FCV-629 | Setting | J460-01-2FCV-629 - Room J6.09 - J460-01-1ACU-611 Cooling Valve Control SP | J460-01-2FCV-629_SP | J460-01-2FCV-629_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1189 | J270-06-1PNL-001 | J460-01-2FCV-629 | Alarm | J460-01-2FCV-629 - Room J6.09 - J460-01-1ACU-611 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-629_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-629_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1190 | J270-06-1PNL-001 | J460-01-2FCV-629 | Alarm | J460-01-2FCV-629 - Room J6.09 - J460-01-1ACU-611 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-629_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-629_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1191 | J270-06-1PNL-001 | J460-01-2FCV-629 | Measurement | J460-01-2FCV-629 - Room J6.09 - J460-01-1ACU-611 Cooling Valve Control Error Code | J460-01-2FCV-629_Err | J460-01-2FCV-629_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1192 | J270-06-1PNL-001 | J460-01-2FCV-630 | Alarm | J460-01-2FCV-630 - Room J6.09 - J460-01-1ACU-612 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-630_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-630_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1193 | J270-06-1PNL-001 | J460-01-2FCV-630 | Measurement | J460-01-2FCV-630 - Room J6.09 - J460-01-1ACU-612 Cooling Valve Control Forced Position | J460-01-2FCV-630_ForcePos | J460-01-2FCV-630_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1194 | J270-06-1PNL-001 | J460-01-2FCV-630 | Setting | J460-01-2FCV-630 - Room J6.09 - J460-01-1ACU-612 Cooling Valve Control Forced Calibration | J460-01-2FCV-630_ForceCal | J460-01-2FCV-630_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1195 | J270-06-1PNL-001 | J460-01-2FCV-630 | Measurement | J460-01-2FCV-630 - Room J6.09 - J460-01-1ACU-612 Cooling Valve Control Status | J460-01-2FCV-630_MotState | J460-01-2FCV-630_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1196 | J270-06-1PNL-001 | J460-01-2FCV-630 | Measurement | J460-01-2FCV-630 - Room J6.09 - J460-01-1ACU-612 Cooling Valve Control Actual SP | J460-01-2FCV-630_ActSP | J460-01-2FCV-630_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1197 | J270-06-1PNL-001 | J460-01-2FCV-630 | Setting | J460-01-2FCV-630 - Room J6.09 - J460-01-1ACU-612 Cooling Valve Control SP | J460-01-2FCV-630_SP | J460-01-2FCV-630_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1198 | J270-06-1PNL-001 | J460-01-2FCV-630 | Alarm | J460-01-2FCV-630 - Room J6.09 - J460-01-1ACU-612 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-630_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-630_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1199 | J270-06-1PNL-001 | J460-01-2FCV-630 | Alarm | J460-01-2FCV-630 - Room J6.09 - J460-01-1ACU-612 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-630_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-630_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1200 | J270-06-1PNL-001 | J460-01-2FCV-630 | Measurement | J460-01-2FCV-630 - Room J6.09 - J460-01-1ACU-612 Cooling Valve Control Error Code | J460-01-2FCV-630_Err | J460-01-2FCV-630_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1201 | J270-06-1PNL-001 | J460-01-2FCV-631 | Alarm | J460-01-2FCV-631 - Room J6.09 - J460-01-1ACU-613 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-631_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-631_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1202 | J270-06-1PNL-001 | J460-01-2FCV-631 | Measurement | J460-01-2FCV-631 - Room J6.09 - J460-01-1ACU-613 Cooling Valve Control Forced Position | J460-01-2FCV-631_ForcePos | J460-01-2FCV-631_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1203 | J270-06-1PNL-001 | J460-01-2FCV-631 | Setting | J460-01-2FCV-631 - Room J6.09 - J460-01-1ACU-613 Cooling Valve Control Forced Calibration | J460-01-2FCV-631_ForceCal | J460-01-2FCV-631_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1204 | J270-06-1PNL-001 | J460-01-2FCV-631 | Measurement | J460-01-2FCV-631 - Room J6.09 - J460-01-1ACU-613 Cooling Valve Control Status | J460-01-2FCV-631_MotState | J460-01-2FCV-631_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1205 | J270-06-1PNL-001 | J460-01-2FCV-631 | Measurement | J460-01-2FCV-631 - Room J6.09 - J460-01-1ACU-613 Cooling Valve Control Actual SP | J460-01-2FCV-631_ActSP | J460-01-2FCV-631_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1206 | J270-06-1PNL-001 | J460-01-2FCV-631 | Setting | J460-01-2FCV-631 - Room J6.09 - J460-01-1ACU-613 Cooling Valve Control SP | J460-01-2FCV-631_SP | J460-01-2FCV-631_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1207 | J270-06-1PNL-001 | J460-01-2FCV-631 | Alarm | J460-01-2FCV-631 - Room J6.09 - J460-01-1ACU-613 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-631_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-631_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1208 | J270-06-1PNL-001 | J460-01-2FCV-631 | Alarm | J460-01-2FCV-631 - Room J6.09 - J460-01-1ACU-613 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-631_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-631_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1209 | J270-06-1PNL-001 | J460-01-2FCV-631 | Measurement | J460-01-2FCV-631 - Room J6.09 - J460-01-1ACU-613 Cooling Valve Control Error Code | J460-01-2FCV-631_Err | J460-01-2FCV-631_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1210 | J270-06-1PNL-001 | J460-01-1VAV-613 | Alarm | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control - Communication Failure Alarm | J460-01-1VAV-613_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-613_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1211 | J270-06-1PNL-001 | J460-01-1VAV-613 | Setting | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Flow Setpoint | J460-01-1VAV-613_SpRel | J460-01-1VAV-613_SpRel | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1212 | J270-06-1PNL-001 | J460-01-1VAV-613 | Measurement | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Relative Position | J460-01-1VAV-613_RelPos | J460-01-1VAV-613_RelPos | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1213 | J270-06-1PNL-001 | J460-01-1VAV-613 | Measurement | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-613_AbsFlw | J460-01-1VAV-613_AbsFlw | 0 | 400 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1214 | J270-06-1PNL-001 | J460-01-1VAV-613 | Alarm | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-613_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-613_AbsFlwHiAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1215 | J270-06-1PNL-001 | J460-01-1VAV-613 | Setting | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-613_AbsFlw_HASP | J460-01-1VAV-613_AbsFlw_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1216 | J270-06-1PNL-001 | J460-01-1VAV-613 | Alarm | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-613_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-613_AbsFlwLoAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1217 | J270-06-1PNL-001 | J460-01-1VAV-613 | Setting | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-613_AbsFlw_LASP | J460-01-1VAV-613_AbsFlw_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1218 | J270-06-1PNL-001 | J460-01-1VAV-613 | Measurement | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-613_Vmin | J460-01-1VAV-613_Vmin | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1219 | J270-06-1PNL-001 | J460-01-1VAV-613 | Measurement | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Maximum Flow | J460-01-1VAV-613_Vmax | J460-01-1VAV-613_Vmax | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1220 | J270-06-1PNL-001 | J460-01-1VAV-613 | Measurement | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-613_Vnom | J460-01-1VAV-613_Vnom | 0 | 400 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1221 | J270-06-1PNL-001 | J460-01-1VAV-613 | Measurement | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Summary Status | J460-01-1VAV-613_SumSts | J460-01-1VAV-613_SumSts | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1222 | J270-06-1PNL-001 | J460-01-1VAV-613 | Alarm | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Summary Status Alarm | J460-01-1VAV-613_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-613_SumSts_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 1223 | J270-06-1PNL-001 | J460-01-1VAV-613 | Measurement | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Actuator Status | J460-01-1VAV-613_ActSts | J460-01-1VAV-613_ActSts | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1224 | J270-06-1PNL-001 | J460-01-1VAV-613 | Measurement | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Device Status | J460-01-1VAV-613_DevSts | J460-01-1VAV-613_DevSts | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1225 | J270-06-1PNL-001 | J460-01-1VAV-613 | Setting | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Device Override | J460-01-1VAV-613_Override | J460-01-1VAV-613_Override | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1226 | J270-06-1PNL-001 | J460-01-1VAV-612 | Alarm | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control - Communication Failure Alarm | J460-01-1VAV-612_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-612_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1227 | J270-06-1PNL-001 | J460-01-1VAV-612 | Setting | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Flow Setpoint | J460-01-1VAV-612_SpRel | J460-01-1VAV-612_SpRel | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1228 | J270-06-1PNL-001 | J460-01-1VAV-612 | Measurement | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Relative Position | J460-01-1VAV-612_RelPos | J460-01-1VAV-612_RelPos | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1229 | J270-06-1PNL-001 | J460-01-1VAV-612 | Measurement | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Absolute Flow | J460-01-1VAV-612_AbsFlw | J460-01-1VAV-612_AbsFlw | 0 | 400 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1230 | J270-06-1PNL-001 | J460-01-1VAV-612 | Alarm | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-612_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-612_AbsFlwHiAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1231 | J270-06-1PNL-001 | J460-01-1VAV-612 | Setting | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Absolute Flow | J460-01-1VAV-612_AbsFlw_HASP | J460-01-1VAV-612_AbsFlw_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1232 | J270-06-1PNL-001 | J460-01-1VAV-612 | Alarm | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-612_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-612_AbsFlwLoAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1233 | J270-06-1PNL-001 | J460-01-1VAV-612 | Setting | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Absolute Flow | J460-01-1VAV-612_AbsFlw_LASP | J460-01-1VAV-612_AbsFlw_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1234 | J270-06-1PNL-001 | J460-01-1VAV-612 | Measurement | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Minimum Flow | J460-01-1VAV-612_Vmin | J460-01-1VAV-612_Vmin | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1235 | J270-06-1PNL-001 | J460-01-1VAV-612 | Measurement | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Maximum Flow | J460-01-1VAV-612_Vmax | J460-01-1VAV-612_Vmax | 400 | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1236 | J270-06-1PNL-001 | J460-01-1VAV-612 | Measurement | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Nominal Flow | J460-01-1VAV-612_Vnom | J460-01-1VAV-612_Vnom | 0 | 400 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1237 | J270-06-1PNL-001 | J460-01-1VAV-612 | Measurement | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Summary Status | J460-01-1VAV-612_SumSts | J460-01-1VAV-612_SumSts | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1238 | J270-06-1PNL-001 | J460-01-1VAV-612 | Alarm | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Summary Status Alarm | J460-01-1VAV-612_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-612_SumSts_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 1239 | J270-06-1PNL-001 | J460-01-1VAV-612 | Measurement | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Actuator Status | J460-01-1VAV-612_ActSts | J460-01-1VAV-612_ActSts | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1240 | J270-06-1PNL-001 | J460-01-1VAV-612 | Measurement | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Device Status | J460-01-1VAV-612_DevSts | J460-01-1VAV-612_DevSts | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1241 | J270-06-1PNL-001 | J460-01-1VAV-612 | Setting | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Device Override | J460-01-1VAV-612_Override | J460-01-1VAV-612_Override | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1242 | J270-06-1PNL-001 | J460-01-2TC-608 | Alarm | J460-01-2TC-608 - Room J6.10 - Room Controller - Communication Failure Alarm | J460-01-2TC-608_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TC-608_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1243 | J460-01-1CP-608 | J460-01-2TT-608 | Measurement | J460-01-2TT-608 - Room J6.10 - Temperature | J460-01-2TT-608_RmTemp | J460-01-2TT-608_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1244 | J460-01-1CP-608 | J460-01-2TT-608 | Alarm | J460-01-2TT-608 - Room J6.10 - Temperature High Alarm | J460-01-2TT-608_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-608_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1245 | J460-01-1CP-608 | J460-01-2TT-608 | Setting | J460-01-2TT-608 - Room J6.10 - Temperature | J460-01-2TT-608_RmTemp_HASP | J460-01-2TT-608_RmTemp_HASP | - | 28 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1246 | J460-01-1CP-608 | J460-01-2TT-608 | Alarm | J460-01-2TT-608 - Room J6.10 - Temperature Low Alarm | J460-01-2TT-608_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-608_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1247 | J460-01-1CP-608 | J460-01-2TT-608 | Calculated | J460-01-2TT-608 - Room J6.10 - Temperature | J460-01-2TT-608_RmTemp_LASP | J460-01-2TT-608_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1248 | J460-01-1CP-608 | J460-01-2TT-608 | Calculated | J460-01-2TT-608 - Room J6.10 - Temperature Effective Setpoint | J460-01-2TT-608_RmTempEffSetpoint | J460-01-2TT-608_RmTempEffSetpoint | Calculated | Calculated | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1249 | J460-01-1CP-608 | J460-01-2TT-608 | Setting | J460-01-2TT-608 - Room J6.10 - Temperature Setpoint CPA | J460-01-2TT-608_RmTempSetpointCPA | J460-01-2TT-608_RmTempSetpointCPA | -3 | 3 | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1250 | J460-01-1CP-608 | J460-01-2TT-608 | Setting | J460-01-2TT-608 - Room J6.10 - Temperature Proportional Band | J460-01-2TT-608_RmTemp_Set_P | J460-01-2TT-608_RmTemp_Set_P | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1251 | J460-01-1CP-608 | J460-01-2TT-608 | Setting | J460-01-2TT-608 - Room J6.10 - Temperature Integral Time | J460-01-2TT-608_RmTemp_Set_I | J460-01-2TT-608_RmTemp_Set_I | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1252 | J460-01-1CP-608 | J460-01-2TT-608 | Setting | J460-01-2TT-608 - Room J6.10 - Temperature Derivative Time | J460-01-2TT-608_RmTemp_Set_D | J460-01-2TT-608_RmTemp_Set_D | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1253 | J460-01-1CP-608 | J460-01-2MT-608 | Measurement | J460-01-2MT-608 - Room J6.10 - Humidity | J460-01-2MT-608_RmHum | J460-01-2MT-608_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1254 | J460-01-1CP-608 | J460-01-2MT-608 | Alarm | J460-01-2MT-608 - Room J6.10 - Humidity High Alarm | J460-01-2MT-608_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-608_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1255 | J460-01-1CP-608 | J460-01-2MT-608 | Setting | J460-01-2MT-608 - Room J6.10 - Humidity | J460-01-2MT-608_RmHum_HASP | J460-01-2MT-608_RmHum_HASP | - | 60 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1256 | J460-01-1CP-608 | J460-01-2MT-608 | Alarm | J460-01-2MT-608 - Room J6.10 - Humidity Low Alarm | J460-01-2MT-608_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-608_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1257 | J460-01-1CP-608 | J460-01-2MT-608 | Setting | J460-01-2MT-608 - Room J6.10 - Humidity | J460-01-2MT-608_RmHum_LASP | J460-01-2MT-608_RmHum_LASP | 30 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1258 | J460-01-1CP-608 | J460-01-2XT-608 | Measurement | J460-01-2XT-608 - Room J6.10 - CO2 Concentration | J460-01-2XT-608_RmCO2 | J460-01-2XT-608_RmCO2 | 0 | 2000 | [11 empty] | - | - | - | - | - | - | 200 | - | ppm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1259 | J460-01-1CP-608 | J460-01-2XT-608 | Alarm | J460-01-2XT-608 - Room J6.10 - CO2 Concentration High Alarm | J460-01-2XT-608_RmCO2HiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2XT-608_RmCO2HiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1260 | J460-01-1CP-608 | J460-01-2XT-608 | Setting | J460-01-2XT-608 - Room J6.10 - CO2 Concentration | J460-01-2XT-608_RmCO2_HASP | J460-01-2XT-608_RmCO2_HASP | - | 1500 | [11 empty] | - | - | - | - | - | - | 200 | - | ppm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1261 | J460-01-1CP-608 | J460-01-2XT-619 | Measurement | J460-01-2XT-619 - Room J6.10 - Occupied | J460-01-2XT-619_RmOcc | J460-01-2XT-619_RmOcc | UNOCC | OCC | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1262 | J270-06-1PNL-001 | J460-01-2FCV-632 | Alarm | J460-01-2FCV-632 - Room J6.10 - Reheater Valve Control - Communication Failure Alarm | J460-01-2FCV-632_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-632_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1263 | J270-06-1PNL-001 | J460-01-2FCV-632 | Measurement | J460-01-2FCV-632 - Room J6.10 - Reheater Valve Control Forced Position | J460-01-2FCV-632_ForcePos | J460-01-2FCV-632_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1264 | J270-06-1PNL-001 | J460-01-2FCV-632 | Setting | J460-01-2FCV-632 - Room J6.10 - Reheater Valve Control Forced Calibration | J460-01-2FCV-632_ForceCal | J460-01-2FCV-632_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1265 | J270-06-1PNL-001 | J460-01-2FCV-632 | Measurement | J460-01-2FCV-632 - Room J6.10 - Reheater Valve Control Status | J460-01-2FCV-632_MotState | J460-01-2FCV-632_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1266 | J270-06-1PNL-001 | J460-01-2FCV-632 | Measurement | J460-01-2FCV-632 - Room J6.10 - Reheater Valve Control Actual SP | J460-01-2FCV-632_ActSP | J460-01-2FCV-632_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1267 | J270-06-1PNL-001 | J460-01-2FCV-632 | Setting | J460-01-2FCV-632 - Room J6.10 - Reheater Valve Control SP | J460-01-2FCV-632_SP | J460-01-2FCV-632_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1268 | J270-06-1PNL-001 | J460-01-2FCV-632 | Alarm | J460-01-2FCV-632 - Room J6.10 - Reheater Valve Control Fail to Open Alarm | J460-01-2FCV-632_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-632_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1269 | J270-06-1PNL-001 | J460-01-2FCV-632 | Alarm | J460-01-2FCV-632 - Room J6.10 - Reheater Valve Control Fail to Close Alarm | J460-01-2FCV-632_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-632_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1270 | J270-06-1PNL-001 | J460-01-2FCV-632 | Measurement | J460-01-2FCV-632 - Room J6.10 - Reheater Valve Control Error Code | J460-01-2FCV-632_Err | J460-01-2FCV-632_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1271 | J270-06-1PNL-001 | J460-01-2TC-609 | Alarm | J460-01-2TC-609 - Room J6.11 - Room Controller - Communication Failure Alarm | J460-01-2TC-609_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TC-609_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1272 | J460-01-1CP-609 | J460-01-2TT-609 | Measurement | J460-01-2TT-609 - Room J6.11 - Temperature | J460-01-2TT-609_RmTemp | J460-01-2TT-609_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1273 | J460-01-1CP-609 | J460-01-2TT-609 | Alarm | J460-01-2TT-609 - Room J6.11 - Temperature High Alarm | J460-01-2TT-609_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-609_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1274 | J460-01-1CP-609 | J460-01-2TT-609 | Calculated | J460-01-2TT-609 - Room J6.11 - Temperature | J460-01-2TT-609_RmTemp_HASP | J460-01-2TT-609_RmTemp_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1275 | J460-01-1CP-609 | J460-01-2TT-609 | Alarm | J460-01-2TT-609 - Room J6.11 - Temperature Low Alarm | J460-01-2TT-609_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-609_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1276 | J460-01-1CP-609 | J460-01-2TT-609 | Calculated | J460-01-2TT-609 - Room J6.11 - Temperature | J460-01-2TT-609_RmTemp_LASP | J460-01-2TT-609_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1277 | J460-01-1CP-609 | J460-01-2TT-609 | Calculated | J460-01-2TT-609 - Room J6.11 - Temperature Effective Setpoint | J460-01-2TT-609_RmTempEffSetpoint | J460-01-2TT-609_RmTempEffSetpoint | Calculated | Calculated | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1278 | J460-01-1CP-609 | J460-01-2TT-609 | Setting | J460-01-2TT-609 - Room J6.11 - Temperature Setpoint CPA | J460-01-2TT-609_RmTempSetpointCPA | J460-01-2TT-609_RmTempSetpointCPA | -3 | 3 | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1279 | J460-01-1CP-609 | J460-01-2TT-609 | Setting | J460-01-2TT-609 - Room J6.11 - Temperature Proportional Band | J460-01-2TT-609_RmTemp_Set_P_Heat | J460-01-2TT-609_RmTemp_Set_P_Heat | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1280 | J460-01-1CP-609 | J460-01-2TT-609 | Setting | J460-01-2TT-609 - Room J6.11 - Temperature Integral Time | J460-01-2TT-609_RmTemp_Set_I_Heat | J460-01-2TT-609_RmTemp_Set_I_Heat | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1281 | J460-01-1CP-609 | J460-01-2TT-609 | Setting | J460-01-2TT-609 - Room J6.11 - Temperature Derivative Time | J460-01-2TT-609_RmTemp_Set_D_Heat | J460-01-2TT-609_RmTemp_Set_D_Heat | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1282 | J460-01-1CP-609 | J460-01-2TT-609 | Setting | J460-01-2TT-609 - Room J6.11 - Temperature Proportional Band | J460-01-2TT-609_RmTemp_Set_P_Cool | J460-01-2TT-609_RmTemp_Set_P_Cool | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1283 | J460-01-1CP-609 | J460-01-2TT-609 | Setting | J460-01-2TT-609 - Room J6.11 - Temperature Integral Time | J460-01-2TT-609_RmTemp_Set_I_Cool | J460-01-2TT-609_RmTemp_Set_I_Cool | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1284 | J460-01-1CP-609 | J460-01-2TT-609 | Setting | J460-01-2TT-609 - Room J6.11 - Temperature Derivative Time | J460-01-2TT-609_RmTemp_Set_D_Cool | J460-01-2TT-609_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1285 | J460-01-1CP-609 | J460-01-2MT-609 | Measurement | J460-01-2MT-609 - Room J6.11 - Humidity | J460-01-2MT-609_RmHum | J460-01-2MT-609_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1286 | J460-01-1CP-609 | J460-01-2MT-609 | Alarm | J460-01-2MT-609 - Room J6.11 - Humidity High Alarm | J460-01-2MT-609_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-609_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1287 | J460-01-1CP-609 | J460-01-2MT-609 | Setting | J460-01-2MT-609 - Room J6.11 - Humidity | J460-01-2MT-609_RmHum_HASP | J460-01-2MT-609_RmHum_HASP | - | 60 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1288 | J460-01-1CP-609 | J460-01-2MT-609 | Alarm | J460-01-2MT-609 - Room J6.11 - Humidity Low Alarm | J460-01-2MT-609_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-609_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1289 | J460-01-1CP-609 | J460-01-2MT-609 | Setting | J460-01-2MT-609 - Room J6.11 - Humidity | J460-01-2MT-609_RmHum_LASP | J460-01-2MT-609_RmHum_LASP | 30 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1290 | J460-01-1CP-609 | J460-01-2XT-609 | Measurement | J460-01-2XT-609 - Room J6.11 - CO2 Concentration | J460-01-2XT-609_RmCO2 | J460-01-2XT-609_RmCO2 | 0 | 2000 | [11 empty] | - | - | - | - | - | - | 200 | - | ppm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1291 | J460-01-1CP-609 | J460-01-2XT-609 | Alarm | J460-01-2XT-609 - Room J6.11 - CO2 Concentration High Alarm | J460-01-2XT-609_RmCO2HiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2XT-609_RmCO2HiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1292 | J460-01-1CP-609 | J460-01-2XT-609 | Setting | J460-01-2XT-609 - Room J6.11 - CO2 Concentration | J460-01-2XT-609_RmCO2_HASP | J460-01-2XT-609_RmCO2_HASP | - | 1500 | [11 empty] | - | - | - | - | - | - | 200 | - | ppm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1293 | J460-01-1CP-609 | J460-01-2XT-609 | Setting | J460-01-2XT-609 - Room J6.11 - CO2 Concentration Setpoint | J460-01-2XT-609_RmCO2Setpoint | J460-01-2XT-609_RmCO2Setpoint | - | 800 | [11 empty] | - | - | - | - | - | - | 220 | - | ppm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1294 | J460-01-1CP-609 | J460-01-2XT-609 | Setting | J460-01-2XT-609 - Room J6.11 - CO2 Concentration Proportional Band | J460-01-2XT-609_RmCO2_Set_P | J460-01-2XT-609_RmCO2_Set_P | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1295 | J460-01-1CP-609 | J460-01-2XT-609 | Setting | J460-01-2XT-609 - Room J6.11 - CO2 Concentration Integral Time | J460-01-2XT-609_RmCO2_Set_I | J460-01-2XT-609_RmCO2_Set_I | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1296 | J460-01-1CP-609 | J460-01-2XT-609 | Setting | J460-01-2XT-609 - Room J6.11 - CO2 Concentration Derivative Time | J460-01-2XT-609_RmCO2_Set_D | J460-01-2XT-609_RmCO2_Set_D | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1297 | J460-01-1CP-609 | J460-01-2XT-620 | Measurement | J460-01-2XT-620 - Room J6.11 - Occupied | J460-01-2XT-620_RmOcc | J460-01-2XT-620_RmOcc | UNOCC | OCC | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1298 | J270-06-1PNL-001 | J460-01-2FCV-633 | Alarm | J460-01-2FCV-633 - Room J6.11 - J460-01-1ACU-614 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-633_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-633_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1299 | J270-06-1PNL-001 | J460-01-2FCV-633 | Measurement | J460-01-2FCV-633 - Room J6.11 - J460-01-1ACU-614 Heating Valve Control Forced Position | J460-01-2FCV-633_ForcePos | J460-01-2FCV-633_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1300 | J270-06-1PNL-001 | J460-01-2FCV-633 | Setting | J460-01-2FCV-633 - Room J6.11 - J460-01-1ACU-614 Heating Valve Control Forced Calibration | J460-01-2FCV-633_ForceCal | J460-01-2FCV-633_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1301 | J270-06-1PNL-001 | J460-01-2FCV-633 | Measurement | J460-01-2FCV-633 - Room J6.11 - J460-01-1ACU-614 Heating Valve Control Status | J460-01-2FCV-633_MotState | J460-01-2FCV-633_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1302 | J270-06-1PNL-001 | J460-01-2FCV-633 | Measurement | J460-01-2FCV-633 - Room J6.11 - J460-01-1ACU-614 Heating Valve Control Actual SP | J460-01-2FCV-633_ActSP | J460-01-2FCV-633_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1303 | J270-06-1PNL-001 | J460-01-2FCV-633 | Setting | J460-01-2FCV-633 - Room J6.11 - J460-01-1ACU-614 Heating Valve Control SP | J460-01-2FCV-633_SP | J460-01-2FCV-633_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1304 | J270-06-1PNL-001 | J460-01-2FCV-633 | Alarm | J460-01-2FCV-633 - Room J6.11 - J460-01-1ACU-614 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-633_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-633_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1305 | J270-06-1PNL-001 | J460-01-2FCV-633 | Alarm | J460-01-2FCV-633 - Room J6.11 - J460-01-1ACU-614 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-633_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-633_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1306 | J270-06-1PNL-001 | J460-01-2FCV-633 | Measurement | J460-01-2FCV-633 - Room J6.11 - J460-01-1ACU-614 Heating Valve Control Error Code | J460-01-2FCV-633_Err | J460-01-2FCV-633_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1307 | J270-06-1PNL-001 | J460-01-2FCV-634 | Alarm | J460-01-2FCV-634 - Room J6.11 - J460-01-1ACU-615 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-634_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-634_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1308 | J270-06-1PNL-001 | J460-01-2FCV-634 | Measurement | J460-01-2FCV-634 - Room J6.11 - J460-01-1ACU-615 Heating Valve Control Forced Position | J460-01-2FCV-634_ForcePos | J460-01-2FCV-634_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1309 | J270-06-1PNL-001 | J460-01-2FCV-634 | Setting | J460-01-2FCV-634 - Room J6.11 - J460-01-1ACU-615 Heating Valve Control Forced Calibration | J460-01-2FCV-634_ForceCal | J460-01-2FCV-634_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1310 | J270-06-1PNL-001 | J460-01-2FCV-634 | Measurement | J460-01-2FCV-634 - Room J6.11 - J460-01-1ACU-615 Heating Valve Control Status | J460-01-2FCV-634_MotState | J460-01-2FCV-634_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1311 | J270-06-1PNL-001 | J460-01-2FCV-634 | Measurement | J460-01-2FCV-634 - Room J6.11 - J460-01-1ACU-615 Heating Valve Control Actual SP | J460-01-2FCV-634_ActSP | J460-01-2FCV-634_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1312 | J270-06-1PNL-001 | J460-01-2FCV-634 | Setting | J460-01-2FCV-634 - Room J6.11 - J460-01-1ACU-615 Heating Valve Control SP | J460-01-2FCV-634_SP | J460-01-2FCV-634_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1313 | J270-06-1PNL-001 | J460-01-2FCV-634 | Alarm | J460-01-2FCV-634 - Room J6.11 - J460-01-1ACU-615 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-634_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-634_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1314 | J270-06-1PNL-001 | J460-01-2FCV-634 | Alarm | J460-01-2FCV-634 - Room J6.11 - J460-01-1ACU-615 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-634_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-634_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1315 | J270-06-1PNL-001 | J460-01-2FCV-634 | Measurement | J460-01-2FCV-634 - Room J6.11 - J460-01-1ACU-615 Heating Valve Control Error Code | J460-01-2FCV-634_Err | J460-01-2FCV-634_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1316 | J270-06-1PNL-001 | J460-01-2FCV-635 | Alarm | J460-01-2FCV-635 - Room J6.11 - J460-01-1ACU-616 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-635_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-635_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1317 | J270-06-1PNL-001 | J460-01-2FCV-635 | Measurement | J460-01-2FCV-635 - Room J6.11 - J460-01-1ACU-616 Heating Valve Control Forced Position | J460-01-2FCV-635_ForcePos | J460-01-2FCV-635_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1318 | J270-06-1PNL-001 | J460-01-2FCV-635 | Setting | J460-01-2FCV-635 - Room J6.11 - J460-01-1ACU-616 Heating Valve Control Forced Calibration | J460-01-2FCV-635_ForceCal | J460-01-2FCV-635_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1319 | J270-06-1PNL-001 | J460-01-2FCV-635 | Measurement | J460-01-2FCV-635 - Room J6.11 - J460-01-1ACU-616 Heating Valve Control Status | J460-01-2FCV-635_MotState | J460-01-2FCV-635_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1320 | J270-06-1PNL-001 | J460-01-2FCV-635 | Measurement | J460-01-2FCV-635 - Room J6.11 - J460-01-1ACU-616 Heating Valve Control Actual SP | J460-01-2FCV-635_ActSP | J460-01-2FCV-635_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1321 | J270-06-1PNL-001 | J460-01-2FCV-635 | Setting | J460-01-2FCV-635 - Room J6.11 - J460-01-1ACU-616 Heating Valve Control SP | J460-01-2FCV-635_SP | J460-01-2FCV-635_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1322 | J270-06-1PNL-001 | J460-01-2FCV-635 | Alarm | J460-01-2FCV-635 - Room J6.11 - J460-01-1ACU-616 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-635_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-635_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1323 | J270-06-1PNL-001 | J460-01-2FCV-635 | Alarm | J460-01-2FCV-635 - Room J6.11 - J460-01-1ACU-616 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-635_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-635_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1324 | J270-06-1PNL-001 | J460-01-2FCV-635 | Measurement | J460-01-2FCV-635 - Room J6.11 - J460-01-1ACU-616 Heating Valve Control Error Code | J460-01-2FCV-635_Err | J460-01-2FCV-635_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1325 | J270-06-1PNL-001 | J460-01-2FCV-636 | Alarm | J460-01-2FCV-636 - Room J6.11 - J460-01-1ACU-617 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-636_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-636_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1326 | J270-06-1PNL-001 | J460-01-2FCV-636 | Measurement | J460-01-2FCV-636 - Room J6.11 - J460-01-1ACU-617 Heating Valve Control Forced Position | J460-01-2FCV-636_ForcePos | J460-01-2FCV-636_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1327 | J270-06-1PNL-001 | J460-01-2FCV-636 | Setting | J460-01-2FCV-636 - Room J6.11 - J460-01-1ACU-617 Heating Valve Control Forced Calibration | J460-01-2FCV-636_ForceCal | J460-01-2FCV-636_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1328 | J270-06-1PNL-001 | J460-01-2FCV-636 | Measurement | J460-01-2FCV-636 - Room J6.11 - J460-01-1ACU-617 Heating Valve Control Status | J460-01-2FCV-636_MotState | J460-01-2FCV-636_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1329 | J270-06-1PNL-001 | J460-01-2FCV-636 | Measurement | J460-01-2FCV-636 - Room J6.11 - J460-01-1ACU-617 Heating Valve Control Actual SP | J460-01-2FCV-636_ActSP | J460-01-2FCV-636_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1330 | J270-06-1PNL-001 | J460-01-2FCV-636 | Setting | J460-01-2FCV-636 - Room J6.11 - J460-01-1ACU-617 Heating Valve Control SP | J460-01-2FCV-636_SP | J460-01-2FCV-636_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1331 | J270-06-1PNL-001 | J460-01-2FCV-636 | Alarm | J460-01-2FCV-636 - Room J6.11 - J460-01-1ACU-617 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-636_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-636_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1332 | J270-06-1PNL-001 | J460-01-2FCV-636 | Alarm | J460-01-2FCV-636 - Room J6.11 - J460-01-1ACU-617 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-636_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-636_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1333 | J270-06-1PNL-001 | J460-01-2FCV-636 | Measurement | J460-01-2FCV-636 - Room J6.11 - J460-01-1ACU-617 Heating Valve Control Error Code | J460-01-2FCV-636_Err | J460-01-2FCV-636_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1334 | J270-06-1PNL-001 | J460-01-2FCV-637 | Alarm | J460-01-2FCV-637 - Room J6.11 - J460-01-1ACU-614 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-637_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-637_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1335 | J270-06-1PNL-001 | J460-01-2FCV-637 | Measurement | J460-01-2FCV-637 - Room J6.11 - J460-01-1ACU-614 Cooling Valve Control Forced Position | J460-01-2FCV-637_ForcePos | J460-01-2FCV-637_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1336 | J270-06-1PNL-001 | J460-01-2FCV-637 | Setting | J460-01-2FCV-637 - Room J6.11 - J460-01-1ACU-614 Cooling Valve Control Forced Calibration | J460-01-2FCV-637_ForceCal | J460-01-2FCV-637_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1337 | J270-06-1PNL-001 | J460-01-2FCV-637 | Measurement | J460-01-2FCV-637 - Room J6.11 - J460-01-1ACU-614 Cooling Valve Control Status | J460-01-2FCV-637_MotState | J460-01-2FCV-637_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1338 | J270-06-1PNL-001 | J460-01-2FCV-637 | Measurement | J460-01-2FCV-637 - Room J6.11 - J460-01-1ACU-614 Cooling Valve Control Actual SP | J460-01-2FCV-637_ActSP | J460-01-2FCV-637_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1339 | J270-06-1PNL-001 | J460-01-2FCV-637 | Setting | J460-01-2FCV-637 - Room J6.11 - J460-01-1ACU-614 Cooling Valve Control SP | J460-01-2FCV-637_SP | J460-01-2FCV-637_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1340 | J270-06-1PNL-001 | J460-01-2FCV-637 | Alarm | J460-01-2FCV-637 - Room J6.11 - J460-01-1ACU-614 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-637_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-637_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1341 | J270-06-1PNL-001 | J460-01-2FCV-637 | Alarm | J460-01-2FCV-637 - Room J6.11 - J460-01-1ACU-614 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-637_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-637_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1342 | J270-06-1PNL-001 | J460-01-2FCV-637 | Measurement | J460-01-2FCV-637 - Room J6.11 - J460-01-1ACU-614 Cooling Valve Control Error Code | J460-01-2FCV-637_Err | J460-01-2FCV-637_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1343 | J270-06-1PNL-001 | J460-01-2FCV-638 | Alarm | J460-01-2FCV-638 - Room J6.11 - J460-01-1ACU-615 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-638_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-638_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1344 | J270-06-1PNL-001 | J460-01-2FCV-638 | Measurement | J460-01-2FCV-638 - Room J6.11 - J460-01-1ACU-615 Cooling Valve Control Forced Position | J460-01-2FCV-638_ForcePos | J460-01-2FCV-638_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1345 | J270-06-1PNL-001 | J460-01-2FCV-638 | Setting | J460-01-2FCV-638 - Room J6.11 - J460-01-1ACU-615 Cooling Valve Control Forced Calibration | J460-01-2FCV-638_ForceCal | J460-01-2FCV-638_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1346 | J270-06-1PNL-001 | J460-01-2FCV-638 | Measurement | J460-01-2FCV-638 - Room J6.11 - J460-01-1ACU-615 Cooling Valve Control Status | J460-01-2FCV-638_MotState | J460-01-2FCV-638_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1347 | J270-06-1PNL-001 | J460-01-2FCV-638 | Measurement | J460-01-2FCV-638 - Room J6.11 - J460-01-1ACU-615 Cooling Valve Control Actual SP | J460-01-2FCV-638_ActSP | J460-01-2FCV-638_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1348 | J270-06-1PNL-001 | J460-01-2FCV-638 | Setting | J460-01-2FCV-638 - Room J6.11 - J460-01-1ACU-615 Cooling Valve Control SP | J460-01-2FCV-638_SP | J460-01-2FCV-638_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1349 | J270-06-1PNL-001 | J460-01-2FCV-638 | Alarm | J460-01-2FCV-638 - Room J6.11 - J460-01-1ACU-615 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-638_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-638_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1350 | J270-06-1PNL-001 | J460-01-2FCV-638 | Alarm | J460-01-2FCV-638 - Room J6.11 - J460-01-1ACU-615 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-638_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-638_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1351 | J270-06-1PNL-001 | J460-01-2FCV-638 | Measurement | J460-01-2FCV-638 - Room J6.11 - J460-01-1ACU-615 Cooling Valve Control Error Code | J460-01-2FCV-638_Err | J460-01-2FCV-638_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1352 | J270-06-1PNL-001 | J460-01-2FCV-639 | Alarm | J460-01-2FCV-639 - Room J6.11 - J460-01-1ACU-616 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-639_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-639_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1353 | J270-06-1PNL-001 | J460-01-2FCV-639 | Measurement | J460-01-2FCV-639 - Room J6.11 - J460-01-1ACU-616 Cooling Valve Control Forced Position | J460-01-2FCV-639_ForcePos | J460-01-2FCV-639_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1354 | J270-06-1PNL-001 | J460-01-2FCV-639 | Setting | J460-01-2FCV-639 - Room J6.11 - J460-01-1ACU-616 Cooling Valve Control Forced Calibration | J460-01-2FCV-639_ForceCal | J460-01-2FCV-639_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1355 | J270-06-1PNL-001 | J460-01-2FCV-639 | Measurement | J460-01-2FCV-639 - Room J6.11 - J460-01-1ACU-616 Cooling Valve Control Status | J460-01-2FCV-639_MotState | J460-01-2FCV-639_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1356 | J270-06-1PNL-001 | J460-01-2FCV-639 | Measurement | J460-01-2FCV-639 - Room J6.11 - J460-01-1ACU-616 Cooling Valve Control Actual SP | J460-01-2FCV-639_ActSP | J460-01-2FCV-639_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1357 | J270-06-1PNL-001 | J460-01-2FCV-639 | Setting | J460-01-2FCV-639 - Room J6.11 - J460-01-1ACU-616 Cooling Valve Control SP | J460-01-2FCV-639_SP | J460-01-2FCV-639_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1358 | J270-06-1PNL-001 | J460-01-2FCV-639 | Alarm | J460-01-2FCV-639 - Room J6.11 - J460-01-1ACU-616 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-639_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-639_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1359 | J270-06-1PNL-001 | J460-01-2FCV-639 | Alarm | J460-01-2FCV-639 - Room J6.11 - J460-01-1ACU-616 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-639_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-639_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1360 | J270-06-1PNL-001 | J460-01-2FCV-639 | Measurement | J460-01-2FCV-639 - Room J6.11 - J460-01-1ACU-616 Cooling Valve Control Error Code | J460-01-2FCV-639_Err | J460-01-2FCV-639_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1361 | J270-06-1PNL-001 | J460-01-2FCV-640 | Alarm | J460-01-2FCV-640 - Room J6.11 - J460-01-1ACU-617 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-640_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-640_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1362 | J270-06-1PNL-001 | J460-01-2FCV-640 | Measurement | J460-01-2FCV-640 - Room J6.11 - J460-01-1ACU-617 Cooling Valve Control Forced Position | J460-01-2FCV-640_ForcePos | J460-01-2FCV-640_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1363 | J270-06-1PNL-001 | J460-01-2FCV-640 | Setting | J460-01-2FCV-640 - Room J6.11 - J460-01-1ACU-617 Cooling Valve Control Forced Calibration | J460-01-2FCV-640_ForceCal | J460-01-2FCV-640_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1364 | J270-06-1PNL-001 | J460-01-2FCV-640 | Measurement | J460-01-2FCV-640 - Room J6.11 - J460-01-1ACU-617 Cooling Valve Control Status | J460-01-2FCV-640_MotState | J460-01-2FCV-640_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1365 | J270-06-1PNL-001 | J460-01-2FCV-640 | Measurement | J460-01-2FCV-640 - Room J6.11 - J460-01-1ACU-617 Cooling Valve Control Actual SP | J460-01-2FCV-640_ActSP | J460-01-2FCV-640_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1366 | J270-06-1PNL-001 | J460-01-2FCV-640 | Setting | J460-01-2FCV-640 - Room J6.11 - J460-01-1ACU-617 Cooling Valve Control SP | J460-01-2FCV-640_SP | J460-01-2FCV-640_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1367 | J270-06-1PNL-001 | J460-01-2FCV-640 | Alarm | J460-01-2FCV-640 - Room J6.11 - J460-01-1ACU-617 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-640_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-640_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1368 | J270-06-1PNL-001 | J460-01-2FCV-640 | Alarm | J460-01-2FCV-640 - Room J6.11 - J460-01-1ACU-617 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-640_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-640_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1369 | J270-06-1PNL-001 | J460-01-2FCV-640 | Measurement | J460-01-2FCV-640 - Room J6.11 - J460-01-1ACU-617 Cooling Valve Control Error Code | J460-01-2FCV-640_Err | J460-01-2FCV-640_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1370 | J270-06-1PNL-001 | J460-01-1VAV-615 | Alarm | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control - Communication Failure Alarm | J460-01-1VAV-615_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-615_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1371 | J270-06-1PNL-001 | J460-01-1VAV-615 | Setting | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Flow Setpoint | J460-01-1VAV-615_SpRel | J460-01-1VAV-615_SpRel | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1372 | J270-06-1PNL-001 | J460-01-1VAV-615 | Measurement | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Relative Position | J460-01-1VAV-615_RelPos | J460-01-1VAV-615_RelPos | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1373 | J270-06-1PNL-001 | J460-01-1VAV-615 | Measurement | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-615_AbsFlw | J460-01-1VAV-615_AbsFlw | 0 | 500 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1374 | J270-06-1PNL-001 | J460-01-1VAV-615 | Alarm | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-615_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-615_AbsFlwHiAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1375 | J270-06-1PNL-001 | J460-01-1VAV-615 | Setting | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-615_AbsFlw_HASP | J460-01-1VAV-615_AbsFlw_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1376 | J270-06-1PNL-001 | J460-01-1VAV-615 | Alarm | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-615_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-615_AbsFlwLoAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1377 | J270-06-1PNL-001 | J460-01-1VAV-615 | Setting | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-615_AbsFlw_LASP | J460-01-1VAV-615_AbsFlw_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1378 | J270-06-1PNL-001 | J460-01-1VAV-615 | Measurement | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-615_Vmin | J460-01-1VAV-615_Vmin | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1379 | J270-06-1PNL-001 | J460-01-1VAV-615 | Measurement | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Maximum Flow | J460-01-1VAV-615_Vmax | J460-01-1VAV-615_Vmax | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1380 | J270-06-1PNL-001 | J460-01-1VAV-615 | Measurement | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-615_Vnom | J460-01-1VAV-615_Vnom | 0 | 500 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1381 | J270-06-1PNL-001 | J460-01-1VAV-615 | Measurement | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Summary Status | J460-01-1VAV-615_SumSts | J460-01-1VAV-615_SumSts | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1382 | J270-06-1PNL-001 | J460-01-1VAV-615 | Alarm | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Summary Status Alarm | J460-01-1VAV-615_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-615_SumSts_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 1383 | J270-06-1PNL-001 | J460-01-1VAV-615 | Measurement | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Actuator Status | J460-01-1VAV-615_ActSts | J460-01-1VAV-615_ActSts | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1384 | J270-06-1PNL-001 | J460-01-1VAV-615 | Measurement | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Device Status | J460-01-1VAV-615_DevSts | J460-01-1VAV-615_DevSts | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1385 | J270-06-1PNL-001 | J460-01-1VAV-615 | Setting | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Device Override | J460-01-1VAV-615_Override | J460-01-1VAV-615_Override | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1386 | J270-06-1PNL-001 | J460-01-1VAV-614 | Alarm | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control - Communication Failure Alarm | J460-01-1VAV-614_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-614_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1387 | J270-06-1PNL-001 | J460-01-1VAV-614 | Setting | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Flow Setpoint | J460-01-1VAV-614_SpRel | J460-01-1VAV-614_SpRel | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1388 | J270-06-1PNL-001 | J460-01-1VAV-614 | Measurement | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Relative Position | J460-01-1VAV-614_RelPos | J460-01-1VAV-614_RelPos | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1389 | J270-06-1PNL-001 | J460-01-1VAV-614 | Measurement | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Absolute Flow | J460-01-1VAV-614_AbsFlw | J460-01-1VAV-614_AbsFlw | 0 | 500 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1390 | J270-06-1PNL-001 | J460-01-1VAV-614 | Alarm | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-614_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-614_AbsFlwHiAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1391 | J270-06-1PNL-001 | J460-01-1VAV-614 | Setting | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Absolute Flow | J460-01-1VAV-614_AbsFlw_HASP | J460-01-1VAV-614_AbsFlw_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1392 | J270-06-1PNL-001 | J460-01-1VAV-614 | Alarm | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-614_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-614_AbsFlwLoAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1393 | J270-06-1PNL-001 | J460-01-1VAV-614 | Setting | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Absolute Flow | J460-01-1VAV-614_AbsFlw_LASP | J460-01-1VAV-614_AbsFlw_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1394 | J270-06-1PNL-001 | J460-01-1VAV-614 | Measurement | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Minimum Flow | J460-01-1VAV-614_Vmin | J460-01-1VAV-614_Vmin | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1395 | J270-06-1PNL-001 | J460-01-1VAV-614 | Measurement | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Maximum Flow | J460-01-1VAV-614_Vmax | J460-01-1VAV-614_Vmax | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1396 | J270-06-1PNL-001 | J460-01-1VAV-614 | Measurement | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Nominal Flow | J460-01-1VAV-614_Vnom | J460-01-1VAV-614_Vnom | 0 | 500 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1397 | J270-06-1PNL-001 | J460-01-1VAV-614 | Measurement | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Summary Status | J460-01-1VAV-614_SumSts | J460-01-1VAV-614_SumSts | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1398 | J270-06-1PNL-001 | J460-01-1VAV-614 | Alarm | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Summary Status Alarm | J460-01-1VAV-614_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-614_SumSts_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 1399 | J270-06-1PNL-001 | J460-01-1VAV-614 | Measurement | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Actuator Status | J460-01-1VAV-614_ActSts | J460-01-1VAV-614_ActSts | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1400 | J270-06-1PNL-001 | J460-01-1VAV-614 | Measurement | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Device Status | J460-01-1VAV-614_DevSts | J460-01-1VAV-614_DevSts | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1401 | J270-06-1PNL-001 | J460-01-1VAV-614 | Setting | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Device Override | J460-01-1VAV-614_Override | J460-01-1VAV-614_Override | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1402 | J270-06-1PNL-001 | J460-01-2TC-610 | Alarm | J460-01-2TC-610 - Room J6.13 - Room Controller - Communication Failure Alarm | J460-01-2TC-610_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TC-610_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1403 | J460-01-1CP-610 | J460-01-2TT-610 | Measurement | J460-01-2TT-610 - Room J6.13 - Temperature | J460-01-2TT-610_RmTemp | J460-01-2TT-610_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1404 | J460-01-1CP-610 | J460-01-2TT-610 | Alarm | J460-01-2TT-610 - Room J6.13 - Temperature High Alarm | J460-01-2TT-610_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-610_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1405 | J460-01-1CP-610 | J460-01-2TT-610 | Calculated | J460-01-2TT-610 - Room J6.13 - Temperature | J460-01-2TT-610_RmTemp_HASP | J460-01-2TT-610_RmTemp_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1406 | J460-01-1CP-610 | J460-01-2TT-610 | Alarm | J460-01-2TT-610 - Room J6.13 - Temperature Low Alarm | J460-01-2TT-610_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-610_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1407 | J460-01-1CP-610 | J460-01-2TT-610 | Calculated | J460-01-2TT-610 - Room J6.13 - Temperature | J460-01-2TT-610_RmTemp_LASP | J460-01-2TT-610_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1408 | J460-01-1CP-610 | J460-01-2TT-610 | Calculated | J460-01-2TT-610 - Room J6.13 - Temperature Effective Setpoint | J460-01-2TT-610_RmTempEffSetpoint | J460-01-2TT-610_RmTempEffSetpoint | Calculated | Calculated | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1409 | J460-01-1CP-610 | J460-01-2TT-610 | Setting | J460-01-2TT-610 - Room J6.13 - Temperature Setpoint CPA | J460-01-2TT-610_RmTempSetpointCPA | J460-01-2TT-610_RmTempSetpointCPA | -3 | 3 | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1410 | J460-01-1CP-610 | J460-01-2TT-610 | Setting | J460-01-2TT-610 - Room J6.13 - Temperature Proportional Band | J460-01-2TT-610_RmTemp_Set_P_Heat | J460-01-2TT-610_RmTemp_Set_P_Heat | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1411 | J460-01-1CP-610 | J460-01-2TT-610 | Setting | J460-01-2TT-610 - Room J6.13 - Temperature Integral Time | J460-01-2TT-610_RmTemp_Set_I_Heat | J460-01-2TT-610_RmTemp_Set_I_Heat | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1412 | J460-01-1CP-610 | J460-01-2TT-610 | Setting | J460-01-2TT-610 - Room J6.13 - Temperature Derivative Time | J460-01-2TT-610_RmTemp_Set_D_Heat | J460-01-2TT-610_RmTemp_Set_D_Heat | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1413 | J460-01-1CP-610 | J460-01-2TT-610 | Setting | J460-01-2TT-610 - Room J6.13 - Temperature Proportional Band | J460-01-2TT-610_RmTemp_Set_P_Cool | J460-01-2TT-610_RmTemp_Set_P_Cool | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1414 | J460-01-1CP-610 | J460-01-2TT-610 | Setting | J460-01-2TT-610 - Room J6.13 - Temperature Integral Time | J460-01-2TT-610_RmTemp_Set_I_Cool | J460-01-2TT-610_RmTemp_Set_I_Cool | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1415 | J460-01-1CP-610 | J460-01-2TT-610 | Setting | J460-01-2TT-610 - Room J6.13 - Temperature Derivative Time | J460-01-2TT-610_RmTemp_Set_D_Cool | J460-01-2TT-610_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1416 | J460-01-1CP-610 | J460-01-2MT-610 | Measurement | J460-01-2MT-610 - Room J6.13 - Humidity | J460-01-2MT-610_RmHum | J460-01-2MT-610_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1417 | J460-01-1CP-610 | J460-01-2MT-610 | Alarm | J460-01-2MT-610 - Room J6.13 - Humidity High Alarm | J460-01-2MT-610_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-610_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1418 | J460-01-1CP-610 | J460-01-2MT-610 | Setting | J460-01-2MT-610 - Room J6.13 - Humidity | J460-01-2MT-610_RmHum_HASP | J460-01-2MT-610_RmHum_HASP | - | 60 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1419 | J460-01-1CP-610 | J460-01-2MT-610 | Alarm | J460-01-2MT-610 - Room J6.13 - Humidity Low Alarm | J460-01-2MT-610_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-610_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1420 | J460-01-1CP-610 | J460-01-2MT-610 | Setting | J460-01-2MT-610 - Room J6.13 - Humidity | J460-01-2MT-610_RmHum_LASP | J460-01-2MT-610_RmHum_LASP | 30 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1421 | J460-01-1CP-610 | J460-01-2XT-610 | Measurement | J460-01-2XT-610 - Room J6.13 - CO2 Concentration | J460-01-2XT-610_RmCO2 | J460-01-2XT-610_RmCO2 | 0 | 2000 | [11 empty] | - | - | - | - | - | - | 200 | - | ppm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1422 | J460-01-1CP-610 | J460-01-2XT-610 | Alarm | J460-01-2XT-610 - Room J6.13 - CO2 Concentration High Alarm | J460-01-2XT-610_RmCO2HiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2XT-610_RmCO2HiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1423 | J460-01-1CP-610 | J460-01-2XT-610 | Setting | J460-01-2XT-610 - Room J6.13 - CO2 Concentration | J460-01-2XT-610_RmCO2_HASP | J460-01-2XT-610_RmCO2_HASP | - | 1500 | [11 empty] | - | - | - | - | - | - | 200 | - | ppm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1424 | J460-01-1CP-610 | J460-01-2XT-610 | Setting | J460-01-2XT-610 - Room J6.13- CO2 Concentration Setpoint | J460-01-2XT-610_RmCO2Setpoint | J460-01-2XT-610_RmCO2Setpoint | - | 800 | [11 empty] | - | - | - | - | - | - | 220 | - | ppm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1425 | J460-01-1CP-610 | J460-01-2XT-610 | Setting | J460-01-2XT-610 - Room J6.13- CO2 Concentration Proportional Band | J460-01-2XT-610_RmCO2_Set_P | J460-01-2XT-610_RmCO2_Set_P | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1426 | J460-01-1CP-610 | J460-01-2XT-610 | Setting | J460-01-2XT-610 - Room J6.13- CO2 Concentration Integral Time | J460-01-2XT-610_RmCO2_Set_I | J460-01-2XT-610_RmCO2_Set_I | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1427 | J460-01-1CP-610 | J460-01-2XT-610 | Setting | J460-01-2XT-610 - Room J6.13- CO2 Concentration Derivative Time | J460-01-2XT-610_RmCO2_Set_D | J460-01-2XT-610_RmCO2_Set_D | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1428 | J460-01-1CP-610 | J460-01-2XT-621 | Measurement | J460-01-2XT-621 - Room J6.13 - Occupied | J460-01-2XT-621_RmOcc | J460-01-2XT-621_RmOcc | UNOCC | OCC | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1429 | J270-06-1PNL-001 | J460-01-2FCV-641 | Alarm | J460-01-2FCV-641 - Room J6.13 - Reheater Valve Control - Communication Failure Alarm | J460-01-2FCV-641_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-641_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1430 | J270-06-1PNL-001 | J460-01-2FCV-641 | Measurement | J460-01-2FCV-641 - Room J6.13 - Reheater Valve Control Forced Position | J460-01-2FCV-641_ForcePos | J460-01-2FCV-641_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1431 | J270-06-1PNL-001 | J460-01-2FCV-641 | Setting | J460-01-2FCV-641 - Room J6.13 - Reheater Valve Control Forced Calibration | J460-01-2FCV-641_ForceCal | J460-01-2FCV-641_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1432 | J270-06-1PNL-001 | J460-01-2FCV-641 | Measurement | J460-01-2FCV-641 - Room J6.13 - Reheater Valve Control Status | J460-01-2FCV-641_MotState | J460-01-2FCV-641_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1433 | J270-06-1PNL-001 | J460-01-2FCV-641 | Measurement | J460-01-2FCV-641 - Room J6.13 - Reheater Valve Control Actual SP | J460-01-2FCV-641_ActSP | J460-01-2FCV-641_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1434 | J270-06-1PNL-001 | J460-01-2FCV-641 | Setting | J460-01-2FCV-641 - Room J6.13 - Reheater Valve Control SP | J460-01-2FCV-641_SP | J460-01-2FCV-641_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1435 | J270-06-1PNL-001 | J460-01-2FCV-641 | Alarm | J460-01-2FCV-641 - Room J6.13 - Reheater Valve Control Fail to Open Alarm | J460-01-2FCV-641_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-641_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1436 | J270-06-1PNL-001 | J460-01-2FCV-641 | Alarm | J460-01-2FCV-641 - Room J6.13 - Reheater Valve Control Fail to Close Alarm | J460-01-2FCV-641_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-641_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1437 | J270-06-1PNL-001 | J460-01-2FCV-641 | Measurement | J460-01-2FCV-641 - Room J6.13 - Reheater Valve Control Error Code | J460-01-2FCV-641_Err | J460-01-2FCV-641_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1438 | J270-06-1PNL-001 | J460-01-1VAV-616 | Alarm | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control - Communication Failure Alarm | J460-01-1VAV-616_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-616_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1439 | J270-06-1PNL-001 | J460-01-1VAV-616 | Setting | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Flow Setpoint | J460-01-1VAV-616_SpRel | J460-01-1VAV-616_SpRel | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1440 | J270-06-1PNL-001 | J460-01-1VAV-616 | Measurement | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Relative Position | J460-01-1VAV-616_RelPos | J460-01-1VAV-616_RelPos | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1441 | J270-06-1PNL-001 | J460-01-1VAV-616 | Measurement | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-616_AbsFlw | J460-01-1VAV-616_AbsFlw | 0 | 150 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1442 | J270-06-1PNL-001 | J460-01-1VAV-616 | Alarm | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-616_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-614_Vnom_LASP | 2 | Y | - | bar: State 2 to State 64
2.0 | 1443 | J270-06-1PNL-001 | J460-01-1VAV-616 | Setting | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-616_AbsFlw_HASP | J460-01-1VAV-616_AbsFlw_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1444 | J270-06-1PNL-001 | J460-01-1VAV-616 | Alarm | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-616_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-616_AbsFlwLoAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1445 | J270-06-1PNL-001 | J460-01-1VAV-616 | Setting | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-616_AbsFlw_LASP | J460-01-1VAV-616_AbsFlw_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1446 | J270-06-1PNL-001 | J460-01-1VAV-616 | Measurement | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-616_Vmin | J460-01-1VAV-616_Vmin | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1447 | J270-06-1PNL-001 | J460-01-1VAV-616 | Measurement | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Maximum Flow | J460-01-1VAV-616_Vmax | J460-01-1VAV-616_Vmax | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1448 | J270-06-1PNL-001 | J460-01-1VAV-616 | Measurement | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-616_Vnom | J460-01-1VAV-616_Vnom | 0 | 150 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1449 | J270-06-1PNL-001 | J460-01-1VAV-616 | Measurement | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Summary Status | J460-01-1VAV-616_SumSts | J460-01-1VAV-616_SumSts | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1450 | J270-06-1PNL-001 | J460-01-1VAV-616 | Alarm | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Summary Status Alarm | J460-01-1VAV-616_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-616_SumSts_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 1451 | J270-06-1PNL-001 | J460-01-1VAV-616 | Measurement | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Actuator Status | J460-01-1VAV-616_ActSts | J460-01-1VAV-616_ActSts | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1452 | J270-06-1PNL-001 | J460-01-1VAV-616 | Measurement | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Device Status | J460-01-1VAV-616_DevSts | J460-01-1VAV-616_DevSts | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1453 | J270-06-1PNL-001 | J460-01-1VAV-616 | Setting | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Device Override | J460-01-1VAV-616_Override | J460-01-1VAV-616_Override | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1454 | J270-06-1PNL-001 | J460-01-1VAV-617 | Alarm | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control - Communication Failure Alarm | J460-01-1VAV-617_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-617_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1455 | J270-06-1PNL-001 | J460-01-1VAV-617 | Setting | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Flow Setpoint | J460-01-1VAV-617_SpRel | J460-01-1VAV-617_SpRel | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1456 | J270-06-1PNL-001 | J460-01-1VAV-617 | Measurement | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Relative Position | J460-01-1VAV-617_RelPos | J460-01-1VAV-617_RelPos | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1457 | J270-06-1PNL-001 | J460-01-1VAV-617 | Measurement | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Absolute Flow | J460-01-1VAV-617_AbsFlw | J460-01-1VAV-617_AbsFlw | 0 | 125 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1458 | J270-06-1PNL-001 | J460-01-1VAV-617 | Alarm | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-617_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-616_SupAirFlow_Set_D | 2 | Y | - | bar: State 2 to State 64
2.0 | 1459 | J270-06-1PNL-001 | J460-01-1VAV-617 | Setting | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Absolute Flow | J460-01-1VAV-617_AbsFlw_HASP | J460-01-1VAV-617_AbsFlw_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1460 | J270-06-1PNL-001 | J460-01-1VAV-617 | Alarm | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-617_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-617_AbsFlwLoAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1461 | J270-06-1PNL-001 | J460-01-1VAV-617 | Setting | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Absolute Flow | J460-01-1VAV-617_AbsFlw_LASP | J460-01-1VAV-617_AbsFlw_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1462 | J270-06-1PNL-001 | J460-01-1VAV-617 | Measurement | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Minimum Flow | J460-01-1VAV-617_Vmin | J460-01-1VAV-617_Vmin | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1463 | J270-06-1PNL-001 | J460-01-1VAV-617 | Measurement | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Maximum Flow | J460-01-1VAV-617_Vmax | J460-01-1VAV-617_Vmax | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1464 | J270-06-1PNL-001 | J460-01-1VAV-617 | Measurement | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Nominal Flow | J460-01-1VAV-617_Vnom | J460-01-1VAV-617_Vnom | 0 | 125 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1465 | J270-06-1PNL-001 | J460-01-1VAV-617 | Measurement | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Summary Status | J460-01-1VAV-617_SumSts | J460-01-1VAV-617_SumSts | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1466 | J270-06-1PNL-001 | J460-01-1VAV-617 | Alarm | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Summary Status Alarm | J460-01-1VAV-617_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-617_SumSts_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 1467 | J270-06-1PNL-001 | J460-01-1VAV-617 | Measurement | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Actuator Status | J460-01-1VAV-617_ActSts | J460-01-1VAV-617_ActSts | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1468 | J270-06-1PNL-001 | J460-01-1VAV-617 | Measurement | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Device Status | J460-01-1VAV-617_DevSts | J460-01-1VAV-617_DevSts | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1469 | J270-06-1PNL-001 | J460-01-1VAV-617 | Setting | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Device Override | J460-01-1VAV-617_Override | J460-01-1VAV-617_Override | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1470 | J270-06-1PNL-001 | J460-01-2TC-611 | Alarm | J460-01-2TC-611 - Room J6.12 - Room Controller - Communication Failure Alarm | J460-01-2TC-611_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TC-611_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1471 | J460-02-1CP-611 | J460-01-2TT-611 | Measurement | J460-01-2TT-611 - Room J6.12 - Temperature | J460-01-2TT-611_RmTemp | J460-01-2TT-611_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1472 | J460-01-1CP-611 | J460-01-2TT-611 | Alarm | J460-01-2TT-611 - Room J6.12 - Temperature High Alarm | J460-01-2TT-611_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-611_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1473 | J460-01-1CP-611 | J460-01-2TT-611 | Setting | J460-01-2TT-611 - Room J6.12 - Temperature | J460-01-2TT-611_RmTemp_HASP | J460-01-2TT-611_RmTemp_HASP | - | 28 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1474 | J460-01-1CP-611 | J460-01-2TT-611 | Alarm | J460-01-2TT-611 - Room J6.12 - Temperature Low Alarm | J460-01-2TT-611_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-611_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1475 | J460-01-1CP-611 | J460-01-2TT-611 | Calculated | J460-01-2TT-611 - Room J6.12 - Temperature | J460-01-2TT-611_RmTemp_LASP | J460-01-2TT-611_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1476 | J460-01-1CP-611 | J460-01-2TT-611 | Calculated | J460-01-2TT-611 - Room J6.12 - Temperature Effective Setpoint | J460-01-2TT-611_RmTempEffSetpoint | J460-01-2TT-611_RmTempEffSetpoint | Calculated | Calculated | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1477 | J460-01-1CP-611 | J460-01-2TT-611 | Setting | J460-01-2TT-611 - Room J6.12 - Temperature Setpoint CPA | J460-01-2TT-611_RmTempSetpointCPA | J460-01-2TT-611_RmTempSetpointCPA | -3 | 3 | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1478 | J460-01-1CP-611 | J460-01-2TT-611 | Setting | J460-01-2TT-611 - Room J6.12 - Temperature Proportional Band | J460-01-2TT-611_RmTemp_Set_P | J460-01-2TT-611_RmTemp_Set_P | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1479 | J460-01-1CP-611 | J460-01-2TT-611 | Setting | J460-01-2TT-611 - Room J6.12 - Temperature Integral Time | J460-01-2TT-611_RmTemp_Set_I | J460-01-2TT-611_RmTemp_Set_I | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1480 | J460-01-1CP-611 | J460-01-2TT-611 | Setting | J460-01-2TT-611 - Room J6.12 - Temperature Derivative Time | J460-01-2TT-611_RmTemp_Set_D | J460-01-2TT-611_RmTemp_Set_D | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1481 | J460-01-1CP-611 | J460-01-2MT-611 | Measurement | J460-01-2MT-611 - Room J6.12 - Humidity | J460-01-2MT-611_RmHum | J460-01-2MT-611_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1482 | J460-01-1CP-611 | J460-01-2MT-611 | Alarm | J460-01-2MT-611 - Room J6.12 - Humidity High Alarm | J460-01-2MT-611_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-611_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1483 | J460-01-1CP-611 | J460-01-2MT-611 | Setting | J460-01-2MT-611 - Room J6.12 - Humidity | J460-01-2MT-611_RmHum_HASP | J460-01-2MT-611_RmHum_HASP | - | 60 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1484 | J460-01-1CP-611 | J460-01-2MT-611 | Alarm | J460-01-2MT-611 - Room J6.12 - Humidity Low Alarm | J460-01-2MT-611_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-611_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1485 | J460-01-1CP-611 | J460-01-2MT-611 | Setting | J460-01-2MT-611 - Room J6.12 - Humidity | J460-01-2MT-611_RmHum_LASP | J460-01-2MT-611_RmHum_LASP | 30 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1486 | J460-01-1CP-611 | J460-01-2XT-622 | Measurement | J460-01-2XT-622 - Room J6.12 - Occupied | J460-01-2XT-622_RmOcc | J460-01-2XT-622_RmOcc | UNOCC | OCC | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1487 | J270-06-1PNL-001 | J460-01-2FCV-642 | Alarm | J460-01-2FCV-642 - Room J6.12 - Reheater Valve Control - Communication Failure Alarm | J460-01-2FCV-642_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-642_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1488 | J270-06-1PNL-001 | J460-01-2FCV-642 | Measurement | J460-01-2FCV-642 - Room J6.12 - Reheater Valve Control Forced Position | J460-01-2FCV-642_ForcePos | J460-01-2FCV-642_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1489 | J270-06-1PNL-001 | J460-01-2FCV-642 | Setting | J460-01-2FCV-642 - Room J6.12 - Reheater Valve Control Forced Calibration | J460-01-2FCV-642_ForceCal | J460-01-2FCV-642_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1490 | J270-06-1PNL-001 | J460-01-2FCV-642 | Measurement | J460-01-2FCV-642 - Room J6.12 - Reheater Valve Control Status | J460-01-2FCV-642_MotState | J460-01-2FCV-642_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1491 | J270-06-1PNL-001 | J460-01-2FCV-642 | Measurement | J460-01-2FCV-642 - Room J6.12 - Reheater Valve Control Actual SP | J460-01-2FCV-642_ActSP | J460-01-2FCV-642_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1492 | J270-06-1PNL-001 | J460-01-2FCV-642 | Setting | J460-01-2FCV-642 - Room J6.12 - Reheater Valve Control SP | J460-01-2FCV-642_SP | J460-01-2FCV-642_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1493 | J270-06-1PNL-001 | J460-01-2FCV-642 | Alarm | J460-01-2FCV-642 - Room J6.12 - Reheater Valve Control Fail to Open Alarm | J460-01-2FCV-642_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-642_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1494 | J270-06-1PNL-001 | J460-01-2FCV-642 | Alarm | J460-01-2FCV-642 - Room J6.12 - Reheater Valve Control Fail to Close Alarm | J460-01-2FCV-642_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-642_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1495 | J270-06-1PNL-001 | J460-01-2FCV-642 | Measurement | J460-01-2FCV-642 - Room J6.12 - Reheater Valve Control Error Code | J460-01-2FCV-642_Err | J460-01-2FCV-642_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1496 | J270-06-1PNL-001 | J460-02-2TC-601 | Alarm | J460-02-2TC-601 - Room J6.20 - Lab Controller - Communication Failure Alarm | J460-02-2TC-601_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TC-601_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1497 | J460-02-1CP-601 | J460-02-2TT-601 | Measurement | J460-02-2TT-601 - Room J6.20 - Temperature | J460-02-2TT-601_RmTemp | J460-02-2TT-601_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1498 | J460-02-1CP-601 | J460-02-2TT-601 | Alarm | J460-02-2TT-601 - Room J6.20 - Temperature High Alarm | J460-02-2TT-601_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-601_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1499 | J460-02-1CP-601 | J460-02-2TT-601 | Calculated | J460-02-2TT-601 - Room J6.20 - Temperature | J460-02-2TT-601_RmTemp_HASP | J460-02-2TT-601_RmTemp_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1500 | J460-02-1CP-601 | J460-02-2TT-601 | Alarm | J460-02-2TT-601 - Room J6.20 - Temperature Low Alarm | J460-02-2TT-601_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-601_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1501 | J460-02-1CP-601 | J460-02-2TT-601 | Calculated | J460-02-2TT-601 - Room J6.20 - Temperature | J460-02-2TT-601_RmTemp_LASP | J460-02-2TT-601_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1502 | J460-02-1CP-601 | J460-02-2TT-601 | Setting | J460-02-2TT-601 - Room J6.20 - Temperature Setpoint | J460-02-2TT-601_RmTempSetpoint | J460-02-2TT-601_RmTempSetpoint | 20 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1503 | J460-02-1CP-601 | J460-02-2TT-601 | Setting | J460-02-2TT-601 - Room J6.20 - Temperature Proportional Band | J460-02-2TT-601_RmTemp_Set_P_Heat | J460-02-2TT-601_RmTemp_Set_P_Heat | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1504 | J460-02-1CP-601 | J460-02-2TT-601 | Setting | J460-02-2TT-601 - Room J6.20 - Temperature Integral Time | J460-02-2TT-601_RmTemp_Set_I_Heat | J460-02-2TT-601_RmTemp_Set_I_Heat | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1505 | J460-02-1CP-601 | J460-02-2TT-601 | Setting | J460-02-2TT-601 - Room J6.20 - Temperature Derivative Time | J460-02-2TT-601_RmTemp_Set_D_Heat | J460-02-2TT-601_RmTemp_Set_D_Heat | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1506 | J460-02-1CP-601 | J460-02-2TT-601 | Setting | J460-02-2TT-601 - Room J6.20 - Temperature Proportional Band | J460-02-2TT-601_RmTemp_Set_P_Cool | J460-02-2TT-601_RmTemp_Set_P_Cool | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1507 | J460-02-1CP-601 | J460-02-2TT-601 | Setting | J460-02-2TT-601 - Room J6.20 - Temperature Integral Time | J460-02-2TT-601_RmTemp_Set_I_Cool | J460-02-2TT-601_RmTemp_Set_I_Cool | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1508 | J460-02-1CP-601 | J460-02-2TT-601 | Setting | J460-02-2TT-601 - Room J6.20 - Temperature Derivative Time | J460-02-2TT-601_RmTemp_Set_D_Cool | J460-02-2TT-601_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1509 | J460-02-1CP-601 | J460-02-2MT-601 | Measurement | J460-02-2MT-601 - Room J6.20 - Humidity | J460-02-2MT-601_RmHum | J460-02-2MT-601_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1510 | J460-02-1CP-601 | J460-02-2MT-601 | Alarm | J460-02-2MT-601 - Room J6.20 - Humidity High Alarm | J460-02-2MT-601_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-601_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1511 | J460-02-1CP-601 | J460-02-2MT-601 | Setting | J460-02-2MT-601 - Room J6.20 - Humidity | J460-02-2MT-601_RmHum_HASP | J460-02-2MT-601_RmHum_HASP | - | 70 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1512 | J460-02-1CP-601 | J460-02-2MT-601 | Alarm | J460-02-2MT-601 - Room J6.20 - Humidity Low Alarm | J460-02-2MT-601_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-601_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1513 | J460-02-1CP-601 | J460-02-2MT-601 | Setting | J460-02-2MT-601 - Room J6.20 - Humidity | J460-02-2MT-601_RmHum_LASP | J460-02-2MT-601_RmHum_LASP | 40 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1514 | J270-06-1PNL-001 | J460-02-2FCV-601 | Alarm | J460-02-2FCV-601 - Room J6.20 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-601_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-601_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1515 | J270-06-1PNL-001 | J460-02-2FCV-601 | Measurement | J460-02-2FCV-601 - Room J6.20 - Reheater Valve Control Forced Position | J460-02-2FCV-601_ForcePos | J460-02-2FCV-601_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1516 | J270-06-1PNL-001 | J460-02-2FCV-601 | Setting | J460-02-2FCV-601 - Room J6.20 - Reheater Valve Control Forced Calibration | J460-02-2FCV-601_ForceCal | J460-02-2FCV-601_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1517 | J270-06-1PNL-001 | J460-02-2FCV-601 | Measurement | J460-02-2FCV-601 - Room J6.20 - Reheater Valve Control Status | J460-02-2FCV-601_MotState | J460-02-2FCV-601_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1518 | J270-06-1PNL-001 | J460-02-2FCV-601 | Measurement | J460-02-2FCV-601 - Room J6.20 - Reheater Valve Control Actual SP | J460-02-2FCV-601_ActSP | J460-02-2FCV-601_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1519 | J270-06-1PNL-001 | J460-02-2FCV-601 | Setting | J460-02-2FCV-601 - Room J6.20 - Reheater Valve Control SP | J460-02-2FCV-601_SP | J460-02-2FCV-601_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1520 | J270-06-1PNL-001 | J460-02-2FCV-601 | Alarm | J460-02-2FCV-601 - Room J6.20 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-601_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-601_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1521 | J270-06-1PNL-001 | J460-02-2FCV-601 | Alarm | J460-02-2FCV-601 - Room J6.20 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-601_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-601_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1522 | J270-06-1PNL-001 | J460-02-2FCV-601 | Measurement | J460-02-2FCV-601 - Room J6.20 - Reheater Valve Control Error Code | J460-02-2FCV-601_Err | J460-02-2FCV-601_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1523 | J270-06-1PNL-001 | J460-02-2FCV-602 | Alarm | J460-02-2FCV-602 - Room J6.20 - J460-02-1ACU-602 Cooling Valve Control - Communication Failure Alarm | J460-02-2FCV-602_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-602_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1524 | J270-06-1PNL-001 | J460-02-2FCV-602 | Measurement | J460-02-2FCV-602 - Room J6.20 - J460-02-1ACU-602 Cooling Valve Control Forced Position | J460-02-2FCV-602_ForcePos | J460-02-2FCV-602_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1525 | J270-06-1PNL-001 | J460-02-2FCV-602 | Setting | J460-02-2FCV-602 - Room J6.20 - J460-02-1ACU-602 Cooling Valve Control Forced Calibration | J460-02-2FCV-602_ForceCal | J460-02-2FCV-602_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1526 | J270-06-1PNL-001 | J460-02-2FCV-602 | Measurement | J460-02-2FCV-602 - Room J6.20 - J460-02-1ACU-602 Cooling Valve Control Status | J460-02-2FCV-602_MotState | J460-02-2FCV-602_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1527 | J270-06-1PNL-001 | J460-02-2FCV-602 | Measurement | J460-02-2FCV-602 - Room J6.20 - J460-02-1ACU-602 Cooling Valve Control Actual SP | J460-02-2FCV-602_ActSP | J460-02-2FCV-602_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1528 | J270-06-1PNL-001 | J460-02-2FCV-602 | Setting | J460-02-2FCV-602 - Room J6.20 - J460-02-1ACU-602 Cooling Valve Control SP | J460-02-2FCV-602_SP | J460-02-2FCV-602_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1529 | J270-06-1PNL-001 | J460-02-2FCV-602 | Alarm | J460-02-2FCV-602 - Room J6.20 - J460-02-1ACU-602 Cooling Valve Control Fail to Open Alarm | J460-02-2FCV-602_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-602_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1530 | J270-06-1PNL-001 | J460-02-2FCV-602 | Alarm | J460-02-2FCV-602 - Room J6.20 - J460-02-1ACU-602 Cooling Valve Control Fail to Close Alarm | J460-02-2FCV-602_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-602_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1531 | J270-06-1PNL-001 | J460-02-2FCV-602 | Measurement | J460-02-2FCV-602 - Room J6.20 - J460-02-1ACU-602 Cooling Valve Control Error Code | J460-02-2FCV-602_Err | J460-02-2FCV-602_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1532 | J460-02-1CP-601 | J460-02-2TT-618 | Measurement | J460-02-2TT-618 - Room J6.20 - J460-02-1ACU-601 - Supply Temperature | J460-02-2TT-618_SupAirTemp | J460-02-2TT-618_SupAirTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1533 | J460-02-1CP-601 | J460-02-2TT-618 | Measurement | J460-02-2TT-618 - Room J6.20 - J460-02-1ACU-601 - Supply Temperature Field | J460-02-2TT-618_SupAirTemp_Field | J460-02-2TT-618_SupAirTemp_Field | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1534 | J460-02-1CP-601 | J460-02-2TT-618 | Alarm | J460-02-2TT-618 - Room J6.20 - J460-02-1ACU-601 - Supply Temperature High Alarm | J460-02-2TT-618_SupAirTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-618_SupAirTempHiAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 1535 | J460-02-1CP-601 | J460-02-2TT-618 | Setting | J460-02-2TT-618 - Room J6.20 - J460-02-1ACU-601 - Supply Temperature | J460-02-2TT-618_SupAirTemp_HASP | J460-02-2TT-618_SupAirTemp_HASP | - | 22 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1536 | J460-02-1CP-601 | J460-02-2TT-618 | Alarm | J460-02-2TT-618 - Room J6.20 - J460-02-1ACU-601 - Supply Temperature Low Alarm | J460-02-2TT-618_SupAirTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-618_SupAirTempLoAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 1537 | J460-02-1CP-601 | J460-02-2TT-618 | Setting | J460-02-2TT-618 - Room J6.20 - J460-02-1ACU-601 - Supply Temperature | J460-02-2TT-618_SupAirTemp_LASP | J460-02-2TT-618_SupAirTemp_LASP | 18 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1538 | J460-02-1CP-601 | J460-02-2TT-618 | Setting | J460-02-2TT-618 - Room J6.20 - J460-02-1ACU-601 - Supply Temperature Calibration Mode Selection | J460-02-2TT-618_SupAirTempCalModeSel | J460-02-2TT-618_SupAirTempCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1539 | J460-02-1CP-601 | J460-02-2TT-618 | Alarm | J460-02-2TT-618 - Room J6.20 - J460-02-1ACU-601 - Supply Temperature Calibration Still Active Alarm | J460-02-2TT-618_SupAirTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-618_SupAirTempCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1540 | J460-02-1CP-601 | J460-02-1ACU-601 | Measurement | J460-02-2XA-618 - J460-02-1ACU-601 - Alarm | J460-02-2XA-618_FCUAlm | J460-02-2XA-618_FCUAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1541 | J460-02-1CP-601 | J460-02-1ACU-601 | Alarm | J460-02-2XA-618 - J460-02-1ACU-601 - Alarm | J460-02-2XA-618_FCUAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2XA-618_FCUAlm_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 1542 | J460-02-1CP-601 | J460-02-1ACU-601 | Measurement | J460-02-2SC-618 - J460-02-1ACU-601 - Fan Speed | J460-02-2SC-618_FCUSpd | J460-02-2SC-618_FCUSpd | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1543 | J270-06-1PNL-001 | J460-02-1VAV-601 | Alarm | J460-02-1VAV-601 - Room J6.20 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-601_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-601_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1544 | J270-06-1PNL-001 | J460-02-1VAV-601 | Setting | J460-02-1VAV-601 - Room J6.20 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-601_Mode | J460-02-1VAV-601_Mode | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1545 | J270-06-1PNL-001 | J460-02-1VAV-601 | Setting | J460-02-1VAV-601 - Room J6.20 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-601_FlwSPShift | J460-02-1VAV-601_FlwSPShift | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1546 | J270-06-1PNL-001 | J460-02-1VAV-601 | Measurement | J460-02-1VAV-601 - Room J6.20 - Supply Air Flow Control Local Alarm | J460-02-1VAV-601_LocAlm | J460-02-1VAV-601_LocAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1547 | J270-06-1PNL-001 | J460-02-1VAV-601 | Alarm | J460-02-1VAV-601 - Room J6.20 - Supply Air Flow Control Local Alarm | J460-02-1VAV-601_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-601_LocAlm_Alm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1548 | J270-06-1PNL-001 | J460-02-1VAV-601 | Measurement | J460-02-1VAV-601 - Room J6.20 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-601_SumAlm | J460-02-1VAV-601_SumAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1549 | J270-06-1PNL-001 | J460-02-1VAV-601 | Alarm | J460-02-1VAV-601 - Room J6.20 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-601_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-601_SumAlm_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 1550 | J270-06-1PNL-001 | J460-02-1VAV-601 | Measurement | J460-02-1VAV-602-603-604 - Room J6.20 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-602-603-604_RmEaFlw | J460-02-1VAV-602-603-604_RmEaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1551 | J270-06-1PNL-001 | J460-02-1VAV-601 | Measurement | J460-02-1VAV-601 - Room J6.20 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-601_RmSaFlw | J460-02-1VAV-601_RmSaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1552 | J270-06-1PNL-001 | J460-02-2TC-602 | Alarm | J460-02-2TC-602 - Room J6.22 - Lab Controller - Communication Failure Alarm | J460-02-2TC-602_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TC-602_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1553 | J460-02-1CP-602 | J460-02-2TT-602 | Measurement | J460-02-2TT-602 - Room J6.22 - Temperature | J460-02-2TT-602_RmTemp | J460-02-2TT-602_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1554 | J460-02-1CP-602 | J460-02-2TT-602 | Alarm | J460-02-2TT-602 - Room J6.22 - Temperature High Alarm | J460-02-2TT-602_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-602_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1555 | J460-02-1CP-602 | J460-02-2TT-602 | Calculated | J460-02-2TT-602 - Room J6.22 - Temperature | J460-02-2TT-602_RmTemp_HASP | J460-02-2TT-602_RmTemp_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1556 | J460-02-1CP-602 | J460-02-2TT-602 | Alarm | J460-02-2TT-602 - Room J6.22 - Temperature Low Alarm | J460-02-2TT-602_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-602_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1557 | J460-02-1CP-602 | J460-02-2TT-602 | Calculated | J460-02-2TT-602 - Room J6.22 - Temperature | J460-02-2TT-602_RmTemp_LASP | J460-02-2TT-602_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1558 | J460-02-1CP-602 | J460-02-2TT-602 | Setting | J460-02-2TT-602 - Room J6.22- Temperature Setpoint | J460-02-2TT-602_RmTempSetpoint | J460-02-2TT-602_RmTempSetpoint | 20 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1559 | J460-02-1CP-602 | J460-02-2TT-602 | Setting | J460-02-2TT-602 - Room J6.22- Temperature Proportional Band | J460-02-2TT-602_RmTemp_Set_P_Heat | J460-02-2TT-602_RmTemp_Set_P_Heat | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1560 | J460-02-1CP-602 | J460-02-2TT-602 | Setting | J460-02-2TT-602 - Room J6.22- Temperature Integral Time | J460-02-2TT-602_RmTemp_Set_I_Heat | J460-02-2TT-602_RmTemp_Set_I_Heat | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1561 | J460-02-1CP-602 | J460-02-2TT-602 | Setting | J460-02-2TT-602 - Room J6.22- Temperature Derivative Time | J460-02-2TT-602_RmTemp_Set_D_Heat | J460-02-2TT-602_RmTemp_Set_D_Heat | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1562 | J460-02-1CP-602 | J460-02-2TT-602 | Setting | J460-02-2TT-602 - Room J6.22- Temperature Proportional Band | J460-02-2TT-602_RmTemp_Set_P_Cool | J460-02-2TT-602_RmTemp_Set_P_Cool | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1563 | J460-02-1CP-602 | J460-02-2TT-602 | Setting | J460-02-2TT-602 - Room J6.22- Temperature Integral Time | J460-02-2TT-602_RmTemp_Set_I_Cool | J460-02-2TT-602_RmTemp_Set_I_Cool | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1564 | J460-02-1CP-602 | J460-02-2TT-602 | Setting | J460-02-2TT-602 - Room J6.22- Temperature Derivative Time | J460-02-2TT-602_RmTemp_Set_D_Cool | J460-02-2TT-602_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1565 | J460-02-1CP-602 | J460-02-2MT-602 | Measurement | J460-02-2MT-602 - Room J6.22 - Humidity | J460-02-2MT-602_RmHum | J460-02-2MT-602_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1566 | J460-02-1CP-602 | J460-02-2MT-602 | Alarm | J460-02-2MT-602 - Room J6.22 - Humidity High Alarm | J460-02-2MT-602_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-602_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1567 | J460-02-1CP-602 | J460-02-2MT-602 | Setting | J460-02-2MT-602 - Room J6.22 - Humidity | J460-02-2MT-602_RmHum_HASP | J460-02-2MT-602_RmHum_HASP | - | 70 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1568 | J460-02-1CP-602 | J460-02-2MT-602 | Alarm | J460-02-2MT-602 - Room J6.22 - Humidity Low Alarm | J460-02-2MT-602_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-602_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1569 | J460-02-1CP-602 | J460-02-2MT-602 | Setting | J460-02-2MT-602 - Room J6.22 - Humidity | J460-02-2MT-602_RmHum_LASP | J460-02-2MT-602_RmHum_LASP | 40 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1570 | J270-06-1PNL-001 | J460-02-2FCV-603 | Alarm | J460-02-2FCV-603 - Room J6.22 - J460-02-1ACU-601 Cooling Valve Control - Communication Failure Alarm | J460-02-2FCV-603_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-603_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1571 | J270-06-1PNL-001 | J460-02-2FCV-603 | Measurement | J460-02-2FCV-603 - Room J6.22 - J460-02-1ACU-601 Cooling Valve Control Forced Position | J460-02-2FCV-603_ForcePos | J460-02-2FCV-603_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1572 | J270-06-1PNL-001 | J460-02-2FCV-603 | Setting | J460-02-2FCV-603 - Room J6.22 - J460-02-1ACU-601 Cooling Valve Control Forced Calibration | J460-02-2FCV-603_ForceCal | J460-02-2FCV-603_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1573 | J270-06-1PNL-001 | J460-02-2FCV-603 | Measurement | J460-02-2FCV-603 - Room J6.22 - J460-02-1ACU-601 Cooling Valve Control Status | J460-02-2FCV-603_MotState | J460-02-2FCV-603_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1574 | J270-06-1PNL-001 | J460-02-2FCV-603 | Measurement | J460-02-2FCV-603 - Room J6.22 - J460-02-1ACU-601 Cooling Valve Control Actual SP | J460-02-2FCV-603_ActSP | J460-02-2FCV-603_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1575 | J270-06-1PNL-001 | J460-02-2FCV-603 | Setting | J460-02-2FCV-603 - Room J6.22 - J460-02-1ACU-601 Cooling Valve Control SP | J460-02-2FCV-603_SP | J460-02-2FCV-603_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1576 | J270-06-1PNL-001 | J460-02-2FCV-603 | Alarm | J460-02-2FCV-603 - Room J6.22 - J460-02-1ACU-601 Cooling Valve Control Fail to Open Alarm | J460-02-2FCV-603_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-603_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1577 | J270-06-1PNL-001 | J460-02-2FCV-603 | Alarm | J460-02-2FCV-603 - Room J6.22 - J460-02-1ACU-601 Cooling Valve Control Fail to Close Alarm | J460-02-2FCV-603_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-603_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1578 | J270-06-1PNL-001 | J460-02-2FCV-603 | Measurement | J460-02-2FCV-603 - Room J6.22 - J460-02-1ACU-601 Cooling Valve Control Error Code | J460-02-2FCV-603_Err | J460-02-2FCV-603_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1579 | J270-06-1PNL-001 | J460-02-2FCV-604 | Alarm | J460-02-2FCV-604 - Room J6.22 - J460-02-1ACU-601 Heating Valve Control - Communication Failure Alarm | J460-02-2FCV-604_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-604_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1580 | J270-06-1PNL-001 | J460-02-2FCV-604 | Measurement | J460-02-2FCV-604 - Room J6.22 - J460-02-1ACU-601 Heating Valve Control Forced Position | J460-02-2FCV-604_ForcePos | J460-02-2FCV-604_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1581 | J270-06-1PNL-001 | J460-02-2FCV-604 | Setting | J460-02-2FCV-604 - Room J6.22 - J460-02-1ACU-601 Heating Valve Control Forced Calibration | J460-02-2FCV-604_ForceCal | J460-02-2FCV-604_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1582 | J270-06-1PNL-001 | J460-02-2FCV-604 | Measurement | J460-02-2FCV-604 - Room J6.22 - J460-02-1ACU-601 Heating Valve Control Status | J460-02-2FCV-604_MotState | J460-02-2FCV-604_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1583 | J270-06-1PNL-001 | J460-02-2FCV-604 | Measurement | J460-02-2FCV-604 - Room J6.22 - J460-02-1ACU-601 Heating Valve Control Actual SP | J460-02-2FCV-604_ActSP | J460-02-2FCV-604_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1584 | J270-06-1PNL-001 | J460-02-2FCV-604 | Setting | J460-02-2FCV-604 - Room J6.22 - J460-02-1ACU-601 Heating Valve Control SP | J460-02-2FCV-604_SP | J460-02-2FCV-604_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1585 | J270-06-1PNL-001 | J460-02-2FCV-604 | Alarm | J460-02-2FCV-604 - Room J6.22 - J460-02-1ACU-601 Heating Valve Control Fail to Open Alarm | J460-02-2FCV-604_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-604_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1586 | J270-06-1PNL-001 | J460-02-2FCV-604 | Alarm | J460-02-2FCV-604 - Room J6.22 - J460-02-1ACU-601 Heating Valve Control Fail to Close Alarm | J460-02-2FCV-604_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-604_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1587 | J270-06-1PNL-001 | J460-02-2FCV-604 | Measurement | J460-02-2FCV-604 - Room J6.22 - J460-02-1ACU-601 Heating Valve Control Error Code | J460-02-2FCV-604_Err | J460-02-2FCV-604_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1588 | J460-02-1CP-601 | J460-02-1ACU-602 | Measurement | J460-02-2SC-625 - J460-02-1ACU-602 - Fan Speed | J460-02-2SC-625_FCUSpd | J460-02-2SC-625_FCUSpd | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1589 | J270-06-1PNL-001 | J460-02-1VAV-605 | Alarm | J460-02-1VAV-605 - Room J6.22 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-605_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-605_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1590 | J270-06-1PNL-001 | J460-02-1VAV-605 | Setting | J460-02-1VAV-605 - Room J6.22 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-605_Mode | J460-02-1VAV-605_Mode | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1591 | J270-06-1PNL-001 | J460-02-1VAV-605 | Setting | J460-02-1VAV-605 - Room J6.22 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-605_FlwSPShift | J460-02-1VAV-605_FlwSPShift | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1592 | J270-06-1PNL-001 | J460-02-1VAV-605 | Measurement | J460-02-1VAV-605 - Room J6.22 - Supply Air Flow Control Local Alarm | J460-02-1VAV-605_LocAlm | J460-02-1VAV-605_LocAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1593 | J270-06-1PNL-001 | J460-02-1VAV-605 | Alarm | J460-02-1VAV-605 - Room J6.22 - Supply Air Flow Control Local Alarm | J460-02-1VAV-605_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-605_LocAlm_Alm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1594 | J270-06-1PNL-001 | J460-02-1VAV-605 | Measurement | J460-02-1VAV-605 - Room J6.22 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-605_SumAlm | J460-02-1VAV-605_SumAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1595 | J270-06-1PNL-001 | J460-02-1VAV-605 | Alarm | J460-02-1VAV-605 - Room J6.22 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-605_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-605_SumAlm_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 1596 | J270-06-1PNL-001 | J460-02-1VAV-605 | Measurement | J460-02-1VAV-606-644 - Room J6.22 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-606-644_RmEaFlw | J460-02-1VAV-606-644_RmEaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1597 | J270-06-1PNL-001 | J460-02-1VAV-605 | Measurement | J460-02-1VAV-605 - Room J6.22 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-605_RmSaFlw | J460-02-1VAV-605_RmSaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1598 | J270-06-1PNL-001 | J460-02-1VAV-606 | Alarm | J460-02-2XU-606 - Room J6.22 - Fume hood - Communication Failure Alarm | J460-02-2XU-606_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2XU-606_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1599 | J270-06-1PNL-001 | J460-02-1VAV-606 | Measurement | J460-02-2XU-606 - Room J6.22 - Fume hood Actual Volume Flow | J460-02-2XU-606_ActFlow | J460-02-2XU-606_ActFlow | 0 | 800 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1600 | J270-06-1PNL-001 | J460-02-1VAV-606 | Measurement | J460-02-2XU-606 - Room J6.22 - Fume hood SP Volume Flow Display | J460-02-2XU-606_FlowSP | J460-02-2XU-606_FlowSP | 800 | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1601 | J270-06-1PNL-001 | J460-02-1VAV-606 | Measurement | J460-02-2XU-606 - Room J6.22 - Fume hood Actual Actuator Position | J460-02-2XU-606_RelPos | J460-02-2XU-606_RelPos | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1602 | J270-06-1PNL-001 | J460-02-1VAV-606 | Measurement | J460-02-2XU-606 - Room J6.22 - Fume hood Fault | J460-02-2XU-606_LocAlm | J460-02-2XU-606_LocAlm | NOFAULT | FAULT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1603 | J270-06-1PNL-001 | J460-02-1VAV-606 | Alarm | J460-02-2XU-606 - Room J6.22 - Fume hood Fault Alarm | J460-02-2XU-606_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2XU-606_LocAlm_Alm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1604 | J270-06-1PNL-001 | J460-02-1VAV-606 | Measurement | J460-02-2XU-606 - Room J6.22 - Fume hood Operating Mode Feedback | J460-02-2XU-606_Mode | J460-02-2XU-606_Mode | - | OFF | NORMAL | REDUCED | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1605 | J270-06-1PNL-001 | J460-02-2TC-603 | Alarm | J460-02-2TC-603 - Room J6.23 - Lab Controller - Communication Failure Alarm | J460-02-2TC-603_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TC-603_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1606 | J460-02-1CP-603 | J460-02-2TT-603 | Measurement | J460-02-2TT-603 - Room J6.23 - Temperature | J460-02-2TT-603_RmTemp | J460-02-2TT-603_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1607 | J460-02-1CP-603 | J460-02-2TT-603 | Alarm | J460-02-2TT-603 - Room J6.23 - Temperature High Alarm | J460-02-2TT-603_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-603_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1608 | J460-02-1CP-603 | J460-02-2TT-603 | Calculated | J460-02-2TT-603 - Room J6.23 - Temperature | J460-02-2TT-603_RmTemp_HASP | J460-02-2TT-603_RmTemp_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1609 | J460-02-1CP-603 | J460-02-2TT-603 | Alarm | J460-02-2TT-603 - Room J6.23 - Temperature Low Alarm | J460-02-2TT-603_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-603_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1610 | J460-02-1CP-603 | J460-02-2TT-603 | Calculated | J460-02-2TT-603 - Room J6.23 - Temperature | J460-02-2TT-603_RmTemp_LASP | J460-02-2TT-603_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1611 | J460-02-1CP-603 | J460-02-2TT-603 | Setting | J460-02-2TT-603 - Room J6.23 - Temperature Effective Setpoint | J460-02-2TT-603_EffRmTempSetpoint | J460-02-2TT-603_EffRmTempSetpoint | 22 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1612 | J460-02-1CP-603 | J460-02-2TT-603 | Setting | J460-02-2TT-603 - Room J6.23 - Temperature Proportional Band | J460-02-2TT-603_RmTemp_Set_P_Heat | J460-02-2TT-603_RmTemp_Set_P_Heat | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1613 | J460-02-1CP-603 | J460-02-2TT-603 | Setting | J460-02-2TT-603 - Room J6.23 - Temperature Integral Time | J460-02-2TT-603_RmTemp_Set_I_Heat | J460-02-2TT-603_RmTemp_Set_I_Heat | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1614 | J460-02-1CP-603 | J460-02-2TT-603 | Setting | J460-02-2TT-603 - Room J6.23 - Temperature Derivative Time | J460-02-2TT-603_RmTemp_Set_D_Heat | J460-02-2TT-603_RmTemp_Set_D_Heat | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1615 | J460-02-1CP-603 | J460-02-2TT-603 | Setting | J460-02-2TT-603 - Room J6.23 - Temperature Proportional Band | J460-02-2TT-603_RmTemp_Set_P_Cool | J460-02-2TT-603_RmTemp_Set_P_Cool | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1616 | J460-02-1CP-603 | J460-02-2TT-603 | Setting | J460-02-2TT-603 - Room J6.23 - Temperature Integral Time | J460-02-2TT-603_RmTemp_Set_I_Cool | J460-02-2TT-603_RmTemp_Set_I_Cool | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1617 | J460-02-1CP-603 | J460-02-2TT-603 | Setting | J460-02-2TT-603 - Room J6.23 - Temperature Derivative Time | J460-02-2TT-603_RmTemp_Set_D_Cool | J460-02-2TT-603_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1618 | J460-02-1CP-603 | J460-02-2MT-603 | Measurement | J460-02-2MT-603 - Room J6.23 - Humidity | J460-02-2MT-603_RmHum | J460-02-2MT-603_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1619 | J460-02-1CP-603 | J460-02-2MT-603 | Alarm | J460-02-2MT-603 - Room J6.23 - Humidity High Alarm | J460-02-2MT-603_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-603_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1620 | J460-02-1CP-603 | J460-02-2MT-603 | Setting | J460-02-2MT-603 - Room J6.23 - Humidity | J460-02-2MT-603_RmHum_HASP | J460-02-2MT-603_RmHum_HASP | - | 70 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1621 | J460-02-1CP-603 | J460-02-2MT-603 | Alarm | J460-02-2MT-603 - Room J6.23 - Humidity Low Alarm | J460-02-2MT-603_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-603_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1622 | J460-02-1CP-603 | J460-02-2MT-603 | Setting | J460-02-2MT-603 - Room J6.23 - Humidity | J460-02-2MT-603_RmHum_LASP | J460-02-2MT-603_RmHum_LASP | 40 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1623 | J270-06-1PNL-001 | J460-02-2FCV-605 | Alarm | J460-02-2FCV-605 - Room J6.23 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-605_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-605_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1624 | J270-06-1PNL-001 | J460-02-2FCV-605 | Measurement | J460-02-2FCV-605 - Room J6.23 - Reheater Valve Control Forced Position | J460-02-2FCV-605_ForcePos | J460-02-2FCV-605_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1625 | J270-06-1PNL-001 | J460-02-2FCV-605 | Setting | J460-02-2FCV-605 - Room J6.23 - Reheater Valve Control Forced Calibration | J460-02-2FCV-605_ForceCal | J460-02-2FCV-605_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1626 | J270-06-1PNL-001 | J460-02-2FCV-605 | Measurement | J460-02-2FCV-605 - Room J6.23 - Reheater Valve Control Status | J460-02-2FCV-605_MotState | J460-02-2FCV-605_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1627 | J270-06-1PNL-001 | J460-02-2FCV-605 | Measurement | J460-02-2FCV-605 - Room J6.23 - Reheater Valve Control Actual SP | J460-02-2FCV-605_ActSP | J460-02-2FCV-605_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1628 | J270-06-1PNL-001 | J460-02-2FCV-605 | Setting | J460-02-2FCV-605 - Room J6.23 - Reheater Valve Control SP | J460-02-2FCV-605_SP | J460-02-2FCV-605_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1629 | J270-06-1PNL-001 | J460-02-2FCV-605 | Alarm | J460-02-2FCV-605 - Room J6.23 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-605_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-605_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1630 | J270-06-1PNL-001 | J460-02-2FCV-605 | Alarm | J460-02-2FCV-605 - Room J6.23 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-605_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-605_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1631 | J270-06-1PNL-001 | J460-02-2FCV-605 | Measurement | J460-02-2FCV-605 - Room J6.23 - Reheater Valve Control Error Code | J460-02-2FCV-605_Err | J460-02-2FCV-605_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1632 | J270-06-1PNL-001 | J460-02-1VAV-607 | Alarm | J460-02-1VAV-607 - Room J6.23 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-607_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-607_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1633 | J270-06-1PNL-001 | J460-02-1VAV-607 | Setting | J460-02-1VAV-607 - Room J6.23 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-607_Mode | J460-02-1VAV-607_Mode | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1634 | J270-06-1PNL-001 | J460-02-1VAV-607 | Setting | J460-02-1VAV-607 - Room J6.23 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-607_FlwSPShift | J460-02-1VAV-607_FlwSPShift | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1635 | J270-06-1PNL-001 | J460-02-1VAV-607 | Measurement | J460-02-1VAV-607 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-607_LocAlm | J460-02-1VAV-607_LocAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1636 | J270-06-1PNL-001 | J460-02-1VAV-607 | Alarm | J460-02-1VAV-607 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-607_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-607_LocAlm_Alm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1637 | J270-06-1PNL-001 | J460-02-1VAV-607 | Measurement | J460-02-1VAV-607 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-607_SumAlm | J460-02-1VAV-607_SumAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1638 | J270-06-1PNL-001 | J460-02-1VAV-607 | Alarm | J460-02-1VAV-607 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-607_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-607_SumAlm_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 1639 | J270-06-1PNL-001 | J460-02-1VAV-607 | Measurement | J460-02-1VAV-608 - Room J6.23 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-608_RmEaFlwTot | J460-02-1VAV-608_RmEaFlwTot | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1640 | J270-06-1PNL-001 | J460-02-1VAV-607 | Measurement | J460-02-1VAV-607 - Room J6.23 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-607_RmSaFlw | J460-02-1VAV-607_RmSaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1641 | J270-06-1PNL-001 | J460-02-2FCV-606 | Alarm | J460-02-2FCV-606 - Room J6.23 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-606_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-606_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1642 | J270-06-1PNL-001 | J460-02-2FCV-606 | Measurement | J460-02-2FCV-606 - Room J6.23 - Reheater Valve Control Forced Position | J460-02-2FCV-606_ForcePos | J460-02-2FCV-606_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1643 | J270-06-1PNL-001 | J460-02-2FCV-606 | Setting | J460-02-2FCV-606 - Room J6.23 - Reheater Valve Control Forced Calibration | J460-02-2FCV-606_ForceCal | J460-02-2FCV-606_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1644 | J270-06-1PNL-001 | J460-02-2FCV-606 | Measurement | J460-02-2FCV-606 - Room J6.23 - Reheater Valve Control Status | J460-02-2FCV-606_MotState | J460-02-2FCV-606_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1645 | J270-06-1PNL-001 | J460-02-2FCV-606 | Measurement | J460-02-2FCV-606 - Room J6.23 - Reheater Valve Control Actual SP | J460-02-2FCV-606_ActSP | J460-02-2FCV-606_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1646 | J270-06-1PNL-001 | J460-02-2FCV-606 | Setting | J460-02-2FCV-606 - Room J6.23 - Reheater Valve Control SP | J460-02-2FCV-606_SP | J460-02-2FCV-606_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1647 | J270-06-1PNL-001 | J460-02-2FCV-606 | Alarm | J460-02-2FCV-606 - Room J6.23 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-606_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-606_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1648 | J270-06-1PNL-001 | J460-02-2FCV-606 | Alarm | J460-02-2FCV-606 - Room J6.23 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-606_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-606_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1649 | J270-06-1PNL-001 | J460-02-2FCV-606 | Measurement | J460-02-2FCV-606 - Room J6.23 - Reheater Valve Control Error Code | J460-02-2FCV-606_Err | J460-02-2FCV-606_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1650 | J270-06-1PNL-001 | J460-02-2FCV-607 | Alarm | J460-02-2FCV-607 - Room J6.23 - J460-02-1ACU-603 Cooling Valve Control - Communication Failure Alarm | J460-02-2FCV-607_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-607_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1651 | J270-06-1PNL-001 | J460-02-2FCV-607 | Measurement | J460-02-2FCV-607 - Room J6.23 - J460-02-1ACU-603 Cooling Valve Control Forced Position | J460-02-2FCV-607_ForcePos | J460-02-2FCV-607_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1652 | J270-06-1PNL-001 | J460-02-2FCV-607 | Setting | J460-02-2FCV-607 - Room J6.23 - J460-02-1ACU-603 Cooling Valve Control Forced Calibration | J460-02-2FCV-607_ForceCal | J460-02-2FCV-607_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1653 | J270-06-1PNL-001 | J460-02-2FCV-607 | Measurement | J460-02-2FCV-607 - Room J6.23 - J460-02-1ACU-603 Cooling Valve Control Status | J460-02-2FCV-607_MotState | J460-02-2FCV-607_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1654 | J270-06-1PNL-001 | J460-02-2FCV-607 | Measurement | J460-02-2FCV-607 - Room J6.23 - J460-02-1ACU-603 Cooling Valve Control Actual SP | J460-02-2FCV-607_ActSP | J460-02-2FCV-607_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1655 | J270-06-1PNL-001 | J460-02-2FCV-607 | Setting | J460-02-2FCV-607 - Room J6.23 - J460-02-1ACU-603 Cooling Valve Control SP | J460-02-2FCV-607_SP | J460-02-2FCV-607_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1656 | J270-06-1PNL-001 | J460-02-2FCV-607 | Alarm | J460-02-2FCV-607 - Room J6.23 - J460-02-1ACU-603 Cooling Valve Control Fail to Open Alarm | J460-02-2FCV-607_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-607_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1657 | J270-06-1PNL-001 | J460-02-2FCV-607 | Alarm | J460-02-2FCV-607 - Room J6.23 - J460-02-1ACU-603 Cooling Valve Control Fail to Close Alarm | J460-02-2FCV-607_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-607_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1658 | J270-06-1PNL-001 | J460-02-2FCV-607 | Measurement | J460-02-2FCV-607 - Room J6.23 - J460-02-1ACU-603 Cooling Valve Control Error Code | J460-02-2FCV-607_Err | J460-02-2FCV-607_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1659 | J460-02-1CP-603 | J460-02-2TT-619 | Measurement | J460-02-2TT-619 - Room J6.23 - J460-02-1ACU-603 - Supply Temperature | J460-02-2TT-619_SupAirTemp | J460-02-2TT-619_SupAirTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1660 | J460-02-1CP-603 | J460-02-2TT-619 | Measurement | J460-02-2TT-619 - Room J6.23 - J460-02-1ACU-603 - Supply Temperature Field | J460-02-2TT-619_SupAirTemp_Field | J460-02-2TT-619_SupAirTemp_Field | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1661 | J460-02-1CP-603 | J460-02-2TT-619 | Alarm | J460-02-2TT-619 - Room J6.23 - J460-02-1ACU-603 - Supply Temperature High Alarm | J460-02-2TT-619_SupAirTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-619_SupAirTempHiAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 1662 | J460-02-1CP-603 | J460-02-2TT-619 | Setting | J460-02-2TT-619 - Room J6.23 - J460-02-1ACU-603 - Supply Temperature | J460-02-2TT-619_SupAirTemp_HASP | J460-02-2TT-619_SupAirTemp_HASP | - | 22 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1663 | J460-02-1CP-603 | J460-02-2TT-619 | Alarm | J460-02-2TT-619 - Room J6.23 - J460-02-1ACU-603 - Supply Temperature Low Alarm | J460-02-2TT-619_SupAirTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-619_SupAirTempLoAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 1664 | J460-02-1CP-603 | J460-02-2TT-619 | Setting | J460-02-2TT-619 - Room J6.23 - J460-02-1ACU-603 - Supply Temperature | J460-02-2TT-619_SupAirTemp_LASP | J460-02-2TT-619_SupAirTemp_LASP | 18 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1665 | J460-02-1CP-603 | J460-02-2TT-619 | Setting | J460-02-2TT-619 - Room J6.23 - J460-02-1ACU-603 - Supply Temperature Calibration Mode Selection | J460-02-2TT-619_SupAirTempCalModeSel | J460-02-2TT-619_SupAirTempCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1666 | J460-02-1CP-603 | J460-02-2TT-619 | Alarm | J460-02-2TT-619 - Room J6.23 - J460-02-1ACU-603 - Supply Temperature Calibration Still Active Alarm | J460-02-2TT-619_SupAirTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-619_SupAirTempCalModeAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1667 | J460-02-1CP-603 | J460-02-1ACU-603 | Measurement | J460-02-2XA-619 - J460-02-1ACU-603 - Alarm | J460-02-2XA-619_FCUAlm | J460-02-2XA-619_FCUAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1668 | J460-02-1CP-603 | J460-02-1ACU-603 | Alarm | J460-02-2XA-619 - J460-02-1ACU-603 - Alarm | J460-02-2XA-619_FCUAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2XA-619_FCUAlm_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 1669 | J460-02-1CP-603 | J460-02-1ACU-603 | Measurement | J460-02-2SC-619 - J460-02-1ACU-603 - Fan Speed | J460-02-2SC-619_FCUSpd | J460-02-2SC-619_FCUSpd | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1670 | J270-06-1PNL-001 | J460-02-1VAV-609 | Alarm | J460-02-1VAV-609 - Room J6.23 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-609_CommFailAlm | J460-02-1VAV-609_CommFailAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-609_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1671 | J270-06-1PNL-001 | J460-02-1VAV-609 | Setting | J460-02-1VAV-609 - Room J6.23 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-609_Mode | J460-02-1VAV-609_Mode | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1672 | J270-06-1PNL-001 | J460-02-1VAV-609 | Setting | J460-02-1VAV-609 - Room J6.23 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-609_FlwSPShift | J460-02-1VAV-609_FlwSPShift | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1673 | J270-06-1PNL-001 | J460-02-1VAV-609 | Measurement | J460-02-1VAV-609 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-609_LocAlm | J460-02-1VAV-609_LocAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1674 | J270-06-1PNL-001 | J460-02-1VAV-609 | Alarm | J460-02-1VAV-609 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-609_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-609_LocAlm_Alm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1675 | J270-06-1PNL-001 | J460-02-1VAV-609 | Measurement | J460-02-1VAV-609 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-609_SumAlm | J460-02-1VAV-609_SumAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1676 | J270-06-1PNL-001 | J460-02-1VAV-609 | Alarm | J460-02-1VAV-609 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-609_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-609_SumAlm_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 1677 | J270-06-1PNL-001 | J460-02-1VAV-609 | Measurement | J460-02-1VAV-610-611 - Room J6.23 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-610-611_RmEaFlwTot | J460-02-1VAV-610-611_RmEaFlwTot | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1678 | J270-06-1PNL-001 | J460-02-1VAV-609 | Measurement | J460-02-1VAV-609 - Room J6.23 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-609_RmSaFlw | J460-02-1VAV-609_RmSaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1679 | J270-06-1PNL-001 | J460-02-2TC-609 | Alarm | J460-02-2TC-609 - Room J6.23 - Lab Controller - Communication Failure Alarm | J460-02-2TC-609_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TC-609_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1680 | J460-02-1CP-609 | J460-02-2TT-609 | Measurement | J460-02-2TT-609 - Room J6.23 - Temperature | J460-02-2TT-609_RmTemp | J460-02-2TT-609_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1681 | J460-02-1CP-609 | J460-02-2TT-609 | Alarm | J460-02-2TT-609 - Room J6.23 - Temperature High Alarm | J460-02-2TT-609_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-609_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1682 | J460-02-1CP-609 | J460-02-2TT-609 | Calculated | J460-02-2TT-609 - Room J6.23 - Temperature | J460-02-2TT-609_RmTemp_HASP | J460-02-2TT-609_RmTemp_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1683 | J460-02-1CP-609 | J460-02-2TT-609 | Alarm | J460-02-2TT-609 - Room J6.23 - Temperature Low Alarm | J460-02-2TT-609_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-609_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1684 | J460-02-1CP-609 | J460-02-2TT-609 | Calculated | J460-02-2TT-609 - Room J6.23 - Temperature | J460-02-2TT-609_RmTemp_LASP | J460-02-2TT-609_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1685 | J460-02-1CP-609 | J460-02-2TT-609 | Setting | J460-02-2TT-609 - Room J6.23 - Temperature Setpoint | J460-02-2TT-609_RmTempSetpoint | J460-02-2TT-609_RmTempSetpoint | 20 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1686 | J460-02-1CP-609 | J460-02-2TT-609 | Setting | J460-02-2TT-609 - Room J6.23 - Temperature Proportional Band | J460-02-2TT-609_RmTemp_Set_P_Heat | J460-02-2TT-609_RmTemp_Set_P_Heat | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1687 | J460-02-1CP-609 | J460-02-2TT-609 | Setting | J460-02-2TT-609 - Room J6.23 - Temperature Integral Time | J460-02-2TT-609_RmTemp_Set_I_Heat | J460-02-2TT-609_RmTemp_Set_I_Heat | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1688 | J460-02-1CP-609 | J460-02-2TT-609 | Setting | J460-02-2TT-609 - Room J6.23 - Temperature Derivative Time | J460-02-2TT-609_RmTemp_Set_D_Heat | J460-02-2TT-609_RmTemp_Set_D_Heat | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1689 | J460-02-1CP-609 | J460-02-2TT-609 | Setting | J460-02-2TT-609 - Room J6.23 - Temperature Proportional Band | J460-02-2TT-609_RmTemp_Set_P_Cool | J460-02-2TT-609_RmTemp_Set_P_Cool | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1690 | J460-02-1CP-609 | J460-02-2TT-609 | Setting | J460-02-2TT-609 - Room J6.23 - Temperature Integral Time | J460-02-2TT-609_RmTemp_Set_I_Cool | J460-02-2TT-609_RmTemp_Set_I_Cool | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1691 | J460-02-1CP-609 | J460-02-2TT-609 | Setting | J460-02-2TT-609 - Room J6.23 - Temperature Derivative Time | J460-02-2TT-609_RmTemp_Set_D_Cool | J460-02-2TT-609_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1692 | J460-02-1CP-609 | J460-02-2MT-609 | Measurement | J460-02-2MT-609 - Room J6.23 - Humidity | J460-02-2MT-609_RmHum | J460-02-2MT-609_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1693 | J460-02-1CP-609 | J460-02-2MT-609 | Alarm | J460-02-2MT-609 - Room J6.23 - Humidity High Alarm | J460-02-2MT-609_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-609_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1694 | J460-02-1CP-609 | J460-02-2MT-609 | Setting | J460-02-2MT-609 - Room J6.23 - Humidity | J460-02-2MT-609_RmHum_HASP | J460-02-2MT-609_RmHum_HASP | - | 70 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1695 | J460-02-1CP-609 | J460-02-2MT-609 | Alarm | J460-02-2MT-609 - Room J6.23 - Humidity Low Alarm | J460-02-2MT-609_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-609_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1696 | J460-02-1CP-609 | J460-02-2MT-609 | Setting | J460-02-2MT-609 - Room J6.23 - Humidity | J460-02-2MT-609_RmHum_LASP | J460-02-2MT-609_RmHum_LASP | 40 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1697 | J270-06-1PNL-001 | J460-02-2FCV-608 | Alarm | J460-02-2FCV-608 - Room J6.23 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-608_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-608_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1698 | J270-06-1PNL-001 | J460-02-2FCV-608 | Measurement | J460-02-2FCV-608 - Room J6.23 - Reheater Valve Control Forced Position | J460-02-2FCV-608_ForcePos | J460-02-2FCV-608_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1699 | J270-06-1PNL-001 | J460-02-2FCV-608 | Setting | J460-02-2FCV-608 - Room J6.23 - Reheater Valve Control Forced Calibration | J460-02-2FCV-608_ForceCal | J460-02-2FCV-608_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1700 | J270-06-1PNL-001 | J460-02-2FCV-608 | Measurement | J460-02-2FCV-608 - Room J6.23 - Reheater Valve Control Status | J460-02-2FCV-608_MotState | J460-02-2FCV-608_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1701 | J270-06-1PNL-001 | J460-02-2FCV-608 | Measurement | J460-02-2FCV-608 - Room J6.23 - Reheater Valve Control Actual SP | J460-02-2FCV-608_ActSP | J460-02-2FCV-608_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1702 | J270-06-1PNL-001 | J460-02-2FCV-608 | Setting | J460-02-2FCV-608 - Room J6.23 - Reheater Valve Control SP | J460-02-2FCV-608_SP | J460-02-2FCV-608_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1703 | J270-06-1PNL-001 | J460-02-2FCV-608 | Alarm | J460-02-2FCV-608 - Room J6.23 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-608_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-608_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1704 | J270-06-1PNL-001 | J460-02-2FCV-608 | Alarm | J460-02-2FCV-608 - Room J6.23 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-608_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-608_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1705 | J270-06-1PNL-001 | J460-02-2FCV-608 | Measurement | J460-02-2FCV-608 - Room J6.23 - Reheater Valve Control Error Code | J460-02-2FCV-608_Err | J460-02-2FCV-608_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1706 | J270-06-1PNL-001 | J460-02-2FCV-609 | Alarm | J460-02-2FCV-609 - Room J6.23 - J460-02-1ACU-604 Cooling Valve Control - Communication Failure Alarm | J460-02-2FCV-609_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-609_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1707 | J270-06-1PNL-001 | J460-02-2FCV-609 | Measurement | J460-02-2FCV-609 - Room J6.23 - J460-02-1ACU-604 Cooling Valve Control Forced Position | J460-02-2FCV-609_ForcePos | J460-02-2FCV-609_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1708 | J270-06-1PNL-001 | J460-02-2FCV-609 | Setting | J460-02-2FCV-609 - Room J6.23 - J460-02-1ACU-604 Cooling Valve Control Forced Calibration | J460-02-2FCV-609_ForceCal | J460-02-2FCV-609_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1709 | J270-06-1PNL-001 | J460-02-2FCV-609 | Measurement | J460-02-2FCV-609 - Room J6.23 - J460-02-1ACU-604 Cooling Valve Control Status | J460-02-2FCV-609_MotState | J460-02-2FCV-609_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1710 | J270-06-1PNL-001 | J460-02-2FCV-609 | Measurement | J460-02-2FCV-609 - Room J6.23 - J460-02-1ACU-604 Cooling Valve Control Actual SP | J460-02-2FCV-609_ActSP | J460-02-2FCV-609_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1711 | J270-06-1PNL-001 | J460-02-2FCV-609 | Setting | J460-02-2FCV-609 - Room J6.23 - J460-02-1ACU-604 Cooling Valve Control SP | J460-02-2FCV-609_SP | J460-02-2FCV-609_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1712 | J270-06-1PNL-001 | J460-02-2FCV-609 | Alarm | J460-02-2FCV-609 - Room J6.23 - J460-02-1ACU-604 Cooling Valve Control Fail to Open Alarm | J460-02-2FCV-609_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-609_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1713 | J270-06-1PNL-001 | J460-02-2FCV-609 | Alarm | J460-02-2FCV-609 - Room J6.23 - J460-02-1ACU-604 Cooling Valve Control Fail to Close Alarm | J460-02-2FCV-609_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-609_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1714 | J270-06-1PNL-001 | J460-02-2FCV-609 | Measurement | J460-02-2FCV-609 - Room J6.23 - J460-02-1ACU-604 Cooling Valve Control Error Code | J460-02-2FCV-609_Err | J460-02-2FCV-609_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1715 | J460-02-1CP-609 | J460-02-2TT-620 | Measurement | J460-02-2TT-620 - Room J6.23 - J460-02-1ACU-604 - Supply Temperature | J460-02-2TT-620_SupAirTemp | J460-02-2TT-620_SupAirTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1716 | J460-02-1CP-609 | J460-02-2TT-620 | Measurement | J460-02-2TT-620 - Room J6.23 - J460-02-1ACU-604 - Supply Temperature Field | J460-02-2TT-620_SupAirTemp_Field | J460-02-2TT-620_SupAirTemp_Field | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1717 | J460-02-1CP-609 | J460-02-2TT-620 | Alarm | J460-02-2TT-620 - Room J6.23 - J460-02-1ACU-604 - Supply Temperature High Alarm | J460-02-2TT-620_SupAirTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-620_SupAirTempHiAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 1718 | J460-02-1CP-609 | J460-02-2TT-620 | Setting | J460-02-2TT-620 - Room J6.23 - J460-02-1ACU-604 - Supply Temperature | J460-02-2TT-620_SupAirTemp_HASP | J460-02-2TT-620_SupAirTemp_HASP | - | 22 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1719 | J460-02-1CP-609 | J460-02-2TT-620 | Alarm | J460-02-2TT-620 - Room J6.23 - J460-02-1ACU-604 - Supply Temperature Low Alarm | J460-02-2TT-620_SupAirTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-620_SupAirTempLoAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 1720 | J460-02-1CP-609 | J460-02-2TT-620 | Setting | J460-02-2TT-620 - Room J6.23 - J460-02-1ACU-604 - Supply Temperature | J460-02-2TT-620_SupAirTemp_LASP | J460-02-2TT-620_SupAirTemp_LASP | 18 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1721 | J460-02-1CP-609 | J460-02-2TT-620 | Setting | J460-02-2TT-620 - Room J6.23 - J460-02-1ACU-604 - Supply Temperature Calibration Mode Selection | J460-02-2TT-620_SupAirTempCalModeSel | J460-02-2TT-620_SupAirTempCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1722 | J460-02-1CP-609 | J460-02-2TT-620 | Alarm | J460-02-2TT-620 - Room J6.23 - J460-02-1ACU-604 - Supply Temperature Calibration Still Active Alarm | J460-02-2TT-620_SupAirTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-620_SupAirTempCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1723 | J460-02-1CP-609 | J460-02-1ACU-604 | Measurement | J460-02-2XA-620 - J460-02-1ACU-604 - Alarm | J460-02-2XA-620_FCUAlm | J460-02-2XA-620_FCUAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1724 | J460-02-1CP-609 | J460-02-1ACU-604 | Alarm | J460-02-2XA-620 - J460-02-1ACU-604 - Alarm | J460-02-2XA-620_FCUAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2XA-620_FCUAlm_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 1725 | J460-02-1CP-609 | J460-02-1ACU-604 | Measurement | J460-02-2SC-620 - J460-02-1ACU-604 - Fan Speed | J460-02-2SC-620_FCUSpd | J460-02-2SC-620_FCUSpd | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1726 | J270-06-1PNL-001 | J460-02-1VAV-612 | Alarm | J460-02-1VAV-612 - Room J6.23 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-612_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-612_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1727 | J270-06-1PNL-001 | J460-02-1VAV-612 | Setting | J460-02-1VAV-612 - Room J6.23 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-612_Mode | J460-02-1VAV-612_Mode | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1728 | J270-06-1PNL-001 | J460-02-1VAV-612 | Setting | J460-02-1VAV-612 - Room J6.23 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-612_FlwSPShift | J460-02-1VAV-612_FlwSPShift | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1729 | J270-06-1PNL-001 | J460-02-1VAV-612 | Measurement | J460-02-1VAV-612 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-612_LocAlm | J460-02-1VAV-612_LocAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1730 | J270-06-1PNL-001 | J460-02-1VAV-612 | Alarm | J460-02-1VAV-612 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-612_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-612_LocAlm_Alm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1731 | J270-06-1PNL-001 | J460-02-1VAV-612 | Measurement | J460-02-1VAV-612 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-612_SumAlm | J460-02-1VAV-612_SumAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1732 | J270-06-1PNL-001 | J460-02-1VAV-612 | Alarm | J460-02-1VAV-612 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-612_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-612_SumAlm_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 1733 | J270-06-1PNL-001 | J460-02-1VAV-612 | Measurement | J460-02-1VAV-613-614 - Room J6.23 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-613-614_RmEaFlw | J460-02-1VAV-613-614_RmEaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1734 | J270-06-1PNL-001 | J460-02-1VAV-612 | Measurement | J460-02-1VAV-612 - Room J6.23 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-612_RmSaFlw | J460-02-1VAV-612_RmSaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1735 | J270-06-1PNL-001 | J460-02-2TC-610 | Alarm | J460-02-2TC-610 - Room J6.23 - Lab Controller - Communication Failure Alarm | J460-02-2TC-610_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TC-610_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1736 | J460-02-1CP-610 | J460-02-2TT-610 | Measurement | J460-02-2TT-610 - Room J6.23 - Temperature | J460-02-2TT-610_RmTemp | J460-02-2TT-610_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1737 | J460-02-1CP-610 | J460-02-2TT-610 | Alarm | J460-02-2TT-610 - Room J6.23 - Temperature High Alarm | J460-02-2TT-610_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-610_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1738 | J460-02-1CP-610 | J460-02-2TT-610 | Calculated | J460-02-2TT-610 - Room J6.23 - Temperature | J460-02-2TT-610_RmTemp_HASP | J460-02-2TT-610_RmTemp_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1739 | J460-02-1CP-610 | J460-02-2TT-610 | Alarm | J460-02-2TT-610 - Room J6.23 - Temperature Low Alarm | J460-02-2TT-610_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-610_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1740 | J460-02-1CP-610 | J460-02-2TT-610 | Calculated | J460-02-2TT-610 - Room J6.23 - Temperature | J460-02-2TT-610_RmTemp_LASP | J460-02-2TT-610_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1741 | J460-02-1CP-610 | J460-02-2TT-610 | Setting | J460-02-2TT-610 - Room J6.23 - Temperature Setpoint | J460-02-2TT-610_RmTempSetpoint | J460-02-2TT-610_RmTempSetpoint | 20 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1742 | J460-02-1CP-610 | J460-02-2TT-610 | Setting | J460-02-2TT-610 - Room J6.23 - Temperature Proportional Band | J460-02-2TT-610_RmTemp_Set_P_Heat | J460-02-2TT-610_RmTemp_Set_P_Heat | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1743 | J460-02-1CP-610 | J460-02-2TT-610 | Setting | J460-02-2TT-610 - Room J6.23 - Temperature Integral Time | J460-02-2TT-610_RmTemp_Set_I_Heat | J460-02-2TT-610_RmTemp_Set_I_Heat | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1744 | J460-02-1CP-610 | J460-02-2TT-610 | Setting | J460-02-2TT-610 - Room J6.23 - Temperature Derivative Time | J460-02-2TT-610_RmTemp_Set_D_Heat | J460-02-2TT-610_RmTemp_Set_D_Heat | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1745 | J460-02-1CP-610 | J460-02-2TT-610 | Setting | J460-02-2TT-610 - Room J6.23 - Temperature Proportional Band | J460-02-2TT-610_RmTemp_Set_P_Cool | J460-02-2TT-610_RmTemp_Set_P_Cool | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1746 | J460-02-1CP-610 | J460-02-2TT-610 | Setting | J460-02-2TT-610 - Room J6.23 - Temperature Integral Time | J460-02-2TT-610_RmTemp_Set_I_Cool | J460-02-2TT-610_RmTemp_Set_I_Cool | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1747 | J460-02-1CP-610 | J460-02-2TT-610 | Setting | J460-02-2TT-610 - Room J6.23 - Temperature Derivative Time | J460-02-2TT-610_RmTemp_Set_D_Cool | J460-02-2TT-610_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1748 | J460-02-1CP-610 | J460-02-2MT-610 | Measurement | J460-02-2MT-610 - Room J6.23 - Humidity | J460-02-2MT-610_RmHum | J460-02-2MT-610_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1749 | J460-02-1CP-610 | J460-02-2MT-610 | Alarm | J460-02-2MT-610 - Room J6.23 - Humidity High Alarm | J460-02-2MT-610_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-610_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1750 | J460-02-1CP-610 | J460-02-2MT-610 | Setting | J460-02-2MT-610 - Room J6.23 - Humidity | J460-02-2MT-610_RmHum_HASP | J460-02-2MT-610_RmHum_HASP | - | 70 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1751 | J460-02-1CP-610 | J460-02-2MT-610 | Alarm | J460-02-2MT-610 - Room J6.23 - Humidity Low Alarm | J460-02-2MT-610_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-610_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1752 | J460-02-1CP-610 | J460-02-2MT-610 | Setting | J460-02-2MT-610 - Room J6.23 - Humidity | J460-02-2MT-610_RmHum_LASP | J460-02-2MT-610_RmHum_LASP | 40 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1753 | J270-06-1PNL-001 | J460-02-2FCV-610 | Alarm | J460-02-2FCV-610 - Room J6.23 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-610_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-610_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1754 | J270-06-1PNL-001 | J460-02-2FCV-610 | Measurement | J460-02-2FCV-610 - Room J6.23 - Reheater Valve Control Forced Position | J460-02-2FCV-610_ForcePos | J460-02-2FCV-610_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1755 | J270-06-1PNL-001 | J460-02-2FCV-610 | Setting | J460-02-2FCV-610 - Room J6.23 - Reheater Valve Control Forced Calibration | J460-02-2FCV-610_ForceCal | J460-02-2FCV-610_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1756 | J270-06-1PNL-001 | J460-02-2FCV-610 | Measurement | J460-02-2FCV-610 - Room J6.23 - Reheater Valve Control Status | J460-02-2FCV-610_MotState | J460-02-2FCV-610_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1757 | J270-06-1PNL-001 | J460-02-2FCV-610 | Measurement | J460-02-2FCV-610 - Room J6.23 - Reheater Valve Control Actual SP | J460-02-2FCV-610_ActSP | J460-02-2FCV-610_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1758 | J270-06-1PNL-001 | J460-02-2FCV-610 | Setting | J460-02-2FCV-610 - Room J6.23 - Reheater Valve Control SP | J460-02-2FCV-610_SP | J460-02-2FCV-610_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1759 | J270-06-1PNL-001 | J460-02-2FCV-610 | Alarm | J460-02-2FCV-610 - Room J6.23 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-610_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-610_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1760 | J270-06-1PNL-001 | J460-02-2FCV-610 | Alarm | J460-02-2FCV-610 - Room J6.23 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-610_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-610_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1761 | J270-06-1PNL-001 | J460-02-2FCV-610 | Measurement | J460-02-2FCV-610 - Room J6.23 - Reheater Valve Control Error Code | J460-02-2FCV-610_Err | J460-02-2FCV-610_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1762 | J270-06-1PNL-001 | J460-02-2FCV-611 | Alarm | J460-02-2FCV-611 - Room J6.23 - J460-02-1ACU-605 Cooling Valve Control - Communication Failure Alarm | J460-02-2FCV-611_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-611_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1763 | J270-06-1PNL-001 | J460-02-2FCV-611 | Measurement | J460-02-2FCV-611 - Room J6.23 - J460-02-1ACU-605 Cooling Valve Control Forced Position | J460-02-2FCV-611_ForcePos | J460-02-2FCV-611_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1764 | J270-06-1PNL-001 | J460-02-2FCV-611 | Setting | J460-02-2FCV-611 - Room J6.23 - J460-02-1ACU-605 Cooling Valve Control Forced Calibration | J460-02-2FCV-611_ForceCal | J460-02-2FCV-611_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1765 | J270-06-1PNL-001 | J460-02-2FCV-611 | Measurement | J460-02-2FCV-611 - Room J6.23 - J460-02-1ACU-605 Cooling Valve Control Status | J460-02-2FCV-611_MotState | J460-02-2FCV-611_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1766 | J270-06-1PNL-001 | J460-02-2FCV-611 | Measurement | J460-02-2FCV-611 - Room J6.23 - J460-02-1ACU-605 Cooling Valve Control Actual SP | J460-02-2FCV-611_ActSP | J460-02-2FCV-611_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1767 | J270-06-1PNL-001 | J460-02-2FCV-611 | Setting | J460-02-2FCV-611 - Room J6.23 - J460-02-1ACU-605 Cooling Valve Control SP | J460-02-2FCV-611_SP | J460-02-2FCV-611_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1768 | J270-06-1PNL-001 | J460-02-2FCV-611 | Alarm | J460-02-2FCV-611 - Room J6.23 - J460-02-1ACU-605 Cooling Valve Control Fail to Open Alarm | J460-02-2FCV-611_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-611_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1769 | J270-06-1PNL-001 | J460-02-2FCV-611 | Alarm | J460-02-2FCV-611 - Room J6.23 - J460-02-1ACU-605 Cooling Valve Control Fail to Close Alarm | J460-02-2FCV-611_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-611_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1770 | J270-06-1PNL-001 | J460-02-2FCV-611 | Measurement | J460-02-2FCV-611 - Room J6.23 - J460-02-1ACU-605 Cooling Valve Control Error Code | J460-02-2FCV-611_Err | J460-02-2FCV-611_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1771 | J460-02-1CP-610 | J460-02-2TT-621 | Measurement | J460-02-2TT-621 - Room J6.23 - J460-02-1ACU-605 - Supply Temperature | J460-02-2TT-621_SupAirTemp | J460-02-2TT-621_SupAirTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1772 | J460-02-1CP-610 | J460-02-2TT-621 | Measurement | J460-02-2TT-621 - Room J6.23 - J460-02-1ACU-605 - Supply Temperature Field | J460-02-2TT-621_SupAirTemp_Field | J460-02-2TT-621_SupAirTemp_Field | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1773 | J460-02-1CP-610 | J460-02-2TT-621 | Alarm | J460-02-2TT-621 - Room J6.23 - J460-02-1ACU-605 - Supply Temperature High Alarm | J460-02-2TT-621_SupAirTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-621_SupAirTempHiAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 1774 | J460-02-1CP-610 | J460-02-2TT-621 | Setting | J460-02-2TT-621 - Room J6.23 - J460-02-1ACU-605 - Supply Temperature | J460-02-2TT-621_SupAirTemp_HASP | J460-02-2TT-621_SupAirTemp_HASP | - | 22 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1775 | J460-02-1CP-610 | J460-02-2TT-621 | Alarm | J460-02-2TT-621 - Room J6.23 - J460-02-1ACU-605 - Supply Temperature Low Alarm | J460-02-2TT-621_SupAirTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-621_SupAirTempLoAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 1776 | J460-02-1CP-610 | J460-02-2TT-621 | Setting | J460-02-2TT-621 - Room J6.23 - J460-02-1ACU-605 - Supply Temperature | J460-02-2TT-621_SupAirTemp_LASP | J460-02-2TT-621_SupAirTemp_LASP | 18 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1777 | J460-02-1CP-610 | J460-02-2TT-621 | Setting | J460-02-2TT-621 - Room J6.23 - J460-02-1ACU-605 - Supply Temperature Calibration Mode Selection | J460-02-2TT-621_SupAirTempCalModeSel | J460-02-2TT-621_SupAirTempCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1778 | J460-02-1CP-610 | J460-02-2TT-621 | Alarm | J460-02-2TT-621 - Room J6.23 - J460-02-1ACU-605 - Supply Temperature Calibration Still Active Alarm | J460-02-2TT-621_SupAirTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-621_SupAirTempCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1779 | J460-02-1CP-610 | J460-02-1ACU-605 | Measurement | J460-02-2XA-621 - J460-02-1ACU-605 - Alarm | J460-02-2XA-621_FCUAlm | J460-02-2XA-621_FCUAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1780 | J460-02-1CP-610 | J460-02-1ACU-605 | Alarm | J460-02-2XA-621 - J460-02-1ACU-605 - Alarm | J460-02-2XA-621_FCUAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2XA-621_FCUAlm_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 1781 | J460-02-1CP-610 | J460-02-1ACU-605 | Measurement | J460-02-2SC-621 - J460-02-1ACU-605 - Fan Speed | J460-02-2SC-621_FCUSpd | J460-02-2SC-621_FCUSpd | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1782 | J270-06-1PNL-001 | J460-02-1VAV-615 | Alarm | J460-02-1VAV-615 - Room J6.23 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-615_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-615_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1783 | J270-06-1PNL-001 | J460-02-1VAV-615 | Setting | J460-02-1VAV-615 - Room J6.23 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-615_Mode | J460-02-1VAV-615_Mode | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1784 | J270-06-1PNL-001 | J460-02-1VAV-615 | Setting | J460-02-1VAV-615 - Room J6.23 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-615_FlwSPShift | J460-02-1VAV-615_FlwSPShift | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1785 | J270-06-1PNL-001 | J460-02-1VAV-615 | Measurement | J460-02-1VAV-615 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-615_LocAlm | J460-02-1VAV-615_LocAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1786 | J270-06-1PNL-001 | J460-02-1VAV-615 | Alarm | J460-02-1VAV-615 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-615_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-615_LocAlm_Alm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1787 | J270-06-1PNL-001 | J460-02-1VAV-615 | Measurement | J460-02-1VAV-615 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-615_SumAlm | J460-02-1VAV-615_SumAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1788 | J270-06-1PNL-001 | J460-02-1VAV-615 | Alarm | J460-02-1VAV-615 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-615_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-615_SumAlm_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 1789 | J270-06-1PNL-001 | J460-02-1VAV-615 | Measurement | J460-02-1VAV-616-617-618 - Room J6.23 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-616-617-618_RmEaFlw | J460-02-1VAV-616-617-618_RmEaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1790 | J270-06-1PNL-001 | J460-02-1VAV-615 | Measurement | J460-02-1VAV-615 - Room J6.23 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-615_RmSaFlw | J460-02-1VAV-615_RmSaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1791 | J270-06-1PNL-001 | J460-02-2TC-604 | Alarm | J460-02-2TC-604 - Room J6.24 - Lab Controller - Communication Failure Alarm | J460-02-2TC-604_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TC-604_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1792 | J460-02-1CP-604 | J460-02-2TT-604 | Measurement | J460-02-2TT-604 - Room J6.24 - Temperature | J460-02-2TT-604_RmTemp | J460-02-2TT-604_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1793 | J460-02-1CP-604 | J460-02-2TT-604 | Alarm | J460-02-2TT-604 - Room J6.24 - Temperature High Alarm | J460-02-2TT-604_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-604_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1794 | J460-02-1CP-604 | J460-02-2TT-604 | Calculated | J460-02-2TT-604 - Room J6.24 - Temperature | J460-02-2TT-604_RmTemp_HASP | J460-02-2TT-604_RmTemp_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1795 | J460-02-1CP-604 | J460-02-2TT-604 | Alarm | J460-02-2TT-604 - Room J6.24 - Temperature Low Alarm | J460-02-2TT-604_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-604_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1796 | J460-02-1CP-604 | J460-02-2TT-604 | Calculated | J460-02-2TT-604 - Room J6.24 - Temperature | J460-02-2TT-604_RmTemp_LASP | J460-02-2TT-604_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1797 | J460-02-1CP-604 | J460-02-2TT-604 | Setting | J460-02-2TT-604 - Room J6.24 - Temperature Setpoint | J460-02-2TT-604_RmTempSetpoint | J460-02-2TT-604_RmTempSetpoint | 20 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1798 | J460-02-1CP-604 | J460-02-2TT-604 | Setting | J460-02-2TT-604 - Room J6.24 - Temperature Proportional Band | J460-02-2TT-604_RmTemp_Set_P_Heat | J460-02-2TT-604_RmTemp_Set_P_Heat | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1799 | J460-02-1CP-604 | J460-02-2TT-604 | Setting | J460-02-2TT-604 - Room J6.24 - Temperature Integral Time | J460-02-2TT-604_RmTemp_Set_I_Heat | J460-02-2TT-604_RmTemp_Set_I_Heat | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1800 | J460-02-1CP-604 | J460-02-2TT-604 | Setting | J460-02-2TT-604 - Room J6.24 - Temperature Derivative Time | J460-02-2TT-604_RmTemp_Set_D_Heat | J460-02-2TT-604_RmTemp_Set_D_Heat | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1801 | J460-02-1CP-604 | J460-02-2TT-604 | Setting | J460-02-2TT-604 - Room J6.24 - Temperature Proportional Band | J460-02-2TT-604_RmTemp_Set_P_Cool | J460-02-2TT-604_RmTemp_Set_P_Cool | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1802 | J460-02-1CP-604 | J460-02-2TT-604 | Setting | J460-02-2TT-604 - Room J6.24 - Temperature Integral Time | J460-02-2TT-604_RmTemp_Set_I_Cool | J460-02-2TT-604_RmTemp_Set_I_Cool | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1803 | J460-02-1CP-604 | J460-02-2TT-604 | Setting | J460-02-2TT-604 - Room J6.24 - Temperature Derivative Time | J460-02-2TT-604_RmTemp_Set_D_Cool | J460-02-2TT-604_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1804 | J460-02-1CP-604 | J460-02-2MT-604 | Measurement | J460-02-2MT-604 - Room J6.24 - Humidity | J460-02-2MT-604_RmHum | J460-02-2MT-604_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1805 | J460-02-1CP-604 | J460-02-2MT-604 | Alarm | J460-02-2MT-604 - Room J6.24 - Humidity High Alarm | J460-02-2MT-604_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-604_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1806 | J460-02-1CP-604 | J460-02-2MT-604 | Setting | J460-02-2MT-604 - Room J6.24 - Humidity | J460-02-2MT-604_RmHum_HASP | J460-02-2MT-604_RmHum_HASP | - | 70 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1807 | J460-02-1CP-604 | J460-02-2MT-604 | Alarm | J460-02-2MT-604 - Room J6.24 - Humidity Low Alarm | J460-02-2MT-604_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-604_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1808 | J460-02-1CP-604 | J460-02-2MT-604 | Setting | J460-02-2MT-604 - Room J6.24 - Humidity | J460-02-2MT-604_RmHum_LASP | J460-02-2MT-604_RmHum_LASP | 40 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1809 | J270-06-1PNL-001 | J460-02-2FCV-612 | Alarm | J460-02-2FCV-612 - Room J6.24 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-612_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-612_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1810 | J270-06-1PNL-001 | J460-02-2FCV-612 | Measurement | J460-02-2FCV-612 - Room J6.24 - Reheater Valve Control Forced Position | J460-02-2FCV-612_ForcePos | J460-02-2FCV-612_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1811 | J270-06-1PNL-001 | J460-02-2FCV-612 | Setting | J460-02-2FCV-612 - Room J6.24 - Reheater Valve Control Forced Calibration | J460-02-2FCV-612_ForceCal | J460-02-2FCV-612_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1812 | J270-06-1PNL-001 | J460-02-2FCV-612 | Measurement | J460-02-2FCV-612 - Room J6.24 - Reheater Valve Control Status | J460-02-2FCV-612_MotState | J460-02-2FCV-612_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1813 | J270-06-1PNL-001 | J460-02-2FCV-612 | Measurement | J460-02-2FCV-612 - Room J6.24 - Reheater Valve Control Actual SP | J460-02-2FCV-612_ActSP | J460-02-2FCV-612_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1814 | J270-06-1PNL-001 | J460-02-2FCV-612 | Setting | J460-02-2FCV-612 - Room J6.24 - Reheater Valve Control SP | J460-02-2FCV-612_SP | J460-02-2FCV-612_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1815 | J270-06-1PNL-001 | J460-02-2FCV-612 | Alarm | J460-02-2FCV-612 - Room J6.24 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-612_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-612_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1816 | J270-06-1PNL-001 | J460-02-2FCV-612 | Alarm | J460-02-2FCV-612 - Room J6.24 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-612_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-612_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1817 | J270-06-1PNL-001 | J460-02-2FCV-612 | Measurement | J460-02-2FCV-612 - Room J6.24 - Reheater Valve Control Error Code | J460-02-2FCV-612_Err | J460-02-2FCV-612_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1818 | J270-06-1PNL-001 | J460-02-2FCV-613 | Alarm | J460-02-2FCV-613 - Room J6.24 - J460-02-1ACU-606 Cooling Valve Control - Communication Failure Alarm | J460-02-2FCV-613_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-613_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1819 | J270-06-1PNL-001 | J460-02-2FCV-613 | Measurement | J460-02-2FCV-613 - Room J6.24 - J460-02-1ACU-606 Cooling Valve Control Forced Position | J460-02-2FCV-613_ForcePos | J460-02-2FCV-613_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1820 | J270-06-1PNL-001 | J460-02-2FCV-613 | Setting | J460-02-2FCV-613 - Room J6.24 - J460-02-1ACU-606 Cooling Valve Control Forced Calibration | J460-02-2FCV-613_ForceCal | J460-02-2FCV-613_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1821 | J270-06-1PNL-001 | J460-02-2FCV-613 | Measurement | J460-02-2FCV-613 - Room J6.24 - J460-02-1ACU-606 Cooling Valve Control Status | J460-02-2FCV-613_MotState | J460-02-2FCV-613_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1822 | J270-06-1PNL-001 | J460-02-2FCV-613 | Measurement | J460-02-2FCV-613 - Room J6.24 - J460-02-1ACU-606 Cooling Valve Control Actual SP | J460-02-2FCV-613_ActSP | J460-02-2FCV-613_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1823 | J270-06-1PNL-001 | J460-02-2FCV-613 | Setting | J460-02-2FCV-613 - Room J6.24 - J460-02-1ACU-606 Cooling Valve Control SP | J460-02-2FCV-613_SP | J460-02-2FCV-613_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1824 | J270-06-1PNL-001 | J460-02-2FCV-613 | Alarm | J460-02-2FCV-613 - Room J6.24 - J460-02-1ACU-606 Cooling Valve Control Fail to Open Alarm | J460-02-2FCV-613_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-613_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1825 | J270-06-1PNL-001 | J460-02-2FCV-613 | Alarm | J460-02-2FCV-613 - Room J6.24 - J460-02-1ACU-606 Cooling Valve Control Fail to Close Alarm | J460-02-2FCV-613_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-613_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1826 | J270-06-1PNL-001 | J460-02-2FCV-613 | Measurement | J460-02-2FCV-613 - Room J6.24 - J460-02-1ACU-606 Cooling Valve Control Error Code | J460-02-2FCV-613_Err | J460-02-2FCV-613_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1827 | J460-02-1CP-604 | J460-02-2TT-622 | Measurement | J460-02-2TT-622 - Room J6.24 - J460-02-1ACU-606 - Supply Temperature | J460-02-2TT-622_SupAirTemp | J460-02-2TT-622_SupAirTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1828 | J460-02-1CP-604 | J460-02-2TT-622 | Measurement | J460-02-2TT-622 - Room J6.24 - J460-02-1ACU-606 - Supply Temperature Field | J460-02-2TT-622_SupAirTemp_Field | J460-02-2TT-622_SupAirTemp_Field | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1829 | J460-02-1CP-604 | J460-02-2TT-622 | Alarm | J460-02-2TT-622 - Room J6.24 - J460-02-1ACU-606 - Supply Temperature High Alarm | J460-02-2TT-622_SupAirTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-622_SupAirTempHiAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 1830 | J460-02-1CP-604 | J460-02-2TT-622 | Setting | J460-02-2TT-622 - Room J6.24 - J460-02-1ACU-606 - Supply Temperature | J460-02-2TT-622_SupAirTemp_HASP | J460-02-2TT-622_SupAirTemp_HASP | - | 22 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1831 | J460-02-1CP-604 | J460-02-2TT-622 | Alarm | J460-02-2TT-622 - Room J6.24 - J460-02-1ACU-606 - Supply Temperature Low Alarm | J460-02-2TT-622_SupAirTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-622_SupAirTempLoAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 1832 | J460-02-1CP-604 | J460-02-2TT-622 | Setting | J460-02-2TT-622 - Room J6.24 - J460-02-1ACU-606 - Supply Temperature | J460-02-2TT-622_SupAirTemp_LASP | J460-02-2TT-622_SupAirTemp_LASP | 18 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1833 | J460-02-1CP-604 | J460-02-2TT-622 | Setting | J460-02-2TT-622 - Room J6.24 - J460-02-1ACU-606 - Supply Temperature Calibration Mode Selection | J460-02-2TT-622_SupAirTempCalModeSel | J460-02-2TT-622_SupAirTempCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1834 | J460-02-1CP-604 | J460-02-2TT-622 | Alarm | J460-02-2TT-622 - Room J6.24 - J460-02-1ACU-606 - Supply Temperature Calibration Still Active Alarm | J460-02-2TT-622_SupAirTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-622_SupAirTempCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1835 | J460-02-1CP-604 | J460-02-1ACU-606 | Measurement | J460-02-2XA-622 - J460-02-1ACU-606 - Alarm | J460-02-2XA-622_FCUAlm | J460-02-2XA-622_FCUAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1836 | J460-02-1CP-604 | J460-02-1ACU-606 | Alarm | J460-02-2XA-622 - J460-02-1ACU-606 - Alarm | J460-02-2XA-622_FCUAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2XA-622_FCUAlm_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 1837 | J460-02-1CP-604 | J460-02-1ACU-606 | Measurement | J460-02-2SC-622 - J460-02-1ACU-606 - Fan Speed | J460-02-2SC-622_FCUSpd | J460-02-2SC-622_FCUSpd | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1838 | J270-06-1PNL-001 | J460-02-1VAV-619 | Alarm | J460-02-1VAV-619 - Room J6.24 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-619_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-619_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1839 | J270-06-1PNL-001 | J460-02-1VAV-619 | Setting | J460-02-1VAV-619 - Room J6.24 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-619_Mode | J460-02-1VAV-619_Mode | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1840 | J270-06-1PNL-001 | J460-02-1VAV-619 | Setting | J460-02-1VAV-619 - Room J6.24 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-619_FlwSPShift | J460-02-1VAV-619_FlwSPShift | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1841 | J270-06-1PNL-001 | J460-02-1VAV-619 | Measurement | J460-02-1VAV-619 - Room J6.24 - Supply Air Flow Control Local Alarm | J460-02-1VAV-619_LocAlm | J460-02-1VAV-619_LocAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1842 | J270-06-1PNL-001 | J460-02-1VAV-619 | Alarm | J460-02-1VAV-619 - Room J6.24 - Supply Air Flow Control Local Alarm | J460-02-1VAV-619_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-619_LocAlm_Alm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1843 | J270-06-1PNL-001 | J460-02-1VAV-619 | Measurement | J460-02-1VAV-619 - Room J6.24 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-619_SumAlm | J460-02-1VAV-619_SumAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1844 | J270-06-1PNL-001 | J460-02-1VAV-619 | Alarm | J460-02-1VAV-619 - Room J6.24 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-619_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-619_SumAlm_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 1845 | J270-06-1PNL-001 | J460-02-1VAV-619 | Measurement | J460-02-1VAV-620 - Room J6.24 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-620_RmEaFlw | J460-02-1VAV-620_RmEaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1846 | J270-06-1PNL-001 | J460-02-1VAV-619 | Measurement | J460-02-1VAV-619 - Room J6.24 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-619_RmSaFlw | J460-02-1VAV-619_RmSaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1847 | J270-06-1PNL-001 | J460-02-2TC-611 | Alarm | J460-02-2TC-611 - Room J6.24 - Lab Controller - Communication Failure Alarm | J460-02-2TC-611_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TC-611_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1848 | J460-02-1CP-611 | J460-02-2TT-611 | Measurement | J460-02-2TT-611 - Room J6.24 - Temperature | J460-02-2TT-611_RmTemp | J460-02-2TT-611_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1849 | J460-02-1CP-611 | J460-02-2TT-611 | Alarm | J460-02-2TT-611 - Room J6.24 - Temperature High Alarm | J460-02-2TT-611_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-611_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1850 | J460-02-1CP-611 | J460-02-2TT-611 | Calculated | J460-02-2TT-611 - Room J6.24 - Temperature | J460-02-2TT-611_RmTemp_HASP | J460-02-2TT-611_RmTemp_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1851 | J460-02-1CP-611 | J460-02-2TT-611 | Alarm | J460-02-2TT-611 - Room J6.24 - Temperature Low Alarm | J460-02-2TT-611_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-611_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1852 | J460-02-1CP-611 | J460-02-2TT-611 | Calculated | J460-02-2TT-611 - Room J6.24 - Temperature | J460-02-2TT-611_RmTemp_LASP | J460-02-2TT-611_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1853 | J460-02-1CP-611 | J460-02-2TT-611 | Setting | J460-02-2TT-611 - Room J6.24 - Temperature Setpoint | J460-02-2TT-611_RmTempSetpoint | J460-02-2TT-611_RmTempSetpoint | 20 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1854 | J460-02-1CP-611 | J460-02-2TT-611 | Setting | J460-02-2TT-611 - Room J6.24 - Temperature Proportional Band | J460-02-2TT-611_RmTemp_Set_P_Heat | J460-02-2TT-611_RmTemp_Set_P_Heat | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1855 | J460-02-1CP-611 | J460-02-2TT-611 | Setting | J460-02-2TT-611 - Room J6.24 - Temperature Integral Time | J460-02-2TT-611_RmTemp_Set_I_Heat | J460-02-2TT-611_RmTemp_Set_I_Heat | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1856 | J460-02-1CP-611 | J460-02-2TT-611 | Setting | J460-02-2TT-611 - Room J6.24 - Temperature Derivative Time | J460-02-2TT-611_RmTemp_Set_D_Heat | J460-02-2TT-611_RmTemp_Set_D_Heat | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1857 | J460-02-1CP-611 | J460-02-2TT-611 | Setting | J460-02-2TT-611 - Room J6.24 - Temperature Proportional Band | J460-02-2TT-611_RmTemp_Set_P_Cool | J460-02-2TT-611_RmTemp_Set_P_Cool | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1858 | J460-02-1CP-611 | J460-02-2TT-611 | Setting | J460-02-2TT-611 - Room J6.24 - Temperature Integral Time | J460-02-2TT-611_RmTemp_Set_I_Cool | J460-02-2TT-611_RmTemp_Set_I_Cool | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1859 | J460-02-1CP-611 | J460-02-2TT-611 | Setting | J460-02-2TT-611 - Room J6.24 - Temperature Derivative Time | J460-02-2TT-611_RmTemp_Set_D_Cool | J460-02-2TT-611_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1860 | J460-02-1CP-611 | J460-02-2MT-611 | Measurement | J460-02-2MT-611 - Room J6.24 - Humidity | J460-02-2MT-611_RmHum | J460-02-2MT-611_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1861 | J460-02-1CP-611 | J460-02-2MT-611 | Alarm | J460-02-2MT-611 - Room J6.24 - Humidity High Alarm | J460-02-2MT-611_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-611_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
2.0 | 1862 | J460-02-1CP-611 | J460-02-2MT-611 | Setting | J460-02-2MT-611 - Room J6.24 - Humidity | J460-02-2MT-611_RmHum_HASP | J460-02-2MT-611_RmHum_HASP | - | 70 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1863 | J460-02-1CP-611 | J460-02-2MT-611 | Alarm | J460-02-2MT-611 - Room J6.24 - Humidity Low Alarm | J460-02-2MT-611_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-611_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
2.0 | 1864 | J460-02-1CP-611 | J460-02-2MT-611 | Setting | J460-02-2MT-611 - Room J6.24 - Humidity | J460-02-2MT-611_RmHum_LASP | J460-02-2MT-611_RmHum_LASP | 40 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1865 | J270-06-1PNL-001 | J460-02-2FCV-614 | Alarm | J460-02-2FCV-614 - Room J6.24 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-614_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-614_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1866 | J270-06-1PNL-001 | J460-02-2FCV-614 | Measurement | J460-02-2FCV-614 - Room J6.24 - Reheater Valve Control Forced Position | J460-02-2FCV-614_ForcePos | J460-02-2FCV-614_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1867 | J270-06-1PNL-001 | J460-02-2FCV-614 | Setting | J460-02-2FCV-614 - Room J6.24 - Reheater Valve Control Forced Calibration | J460-02-2FCV-614_ForceCal | J460-02-2FCV-614_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1868 | J270-06-1PNL-001 | J460-02-2FCV-614 | Measurement | J460-02-2FCV-614 - Room J6.24 - Reheater Valve Control Status | J460-02-2FCV-614_MotState | J460-02-2FCV-614_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1869 | J270-06-1PNL-001 | J460-02-2FCV-614 | Measurement | J460-02-2FCV-614 - Room J6.24 - Reheater Valve Control Actual SP | J460-02-2FCV-614_ActSP | J460-02-2FCV-614_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1870 | J270-06-1PNL-001 | J460-02-2FCV-614 | Setting | J460-02-2FCV-614 - Room J6.24 - Reheater Valve Control SP | J460-02-2FCV-614_SP | J460-02-2FCV-614_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1871 | J270-06-1PNL-001 | J460-02-2FCV-614 | Alarm | J460-02-2FCV-614 - Room J6.24 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-614_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-614_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1872 | J270-06-1PNL-001 | J460-02-2FCV-614 | Alarm | J460-02-2FCV-614 - Room J6.24 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-614_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-614_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1873 | J270-06-1PNL-001 | J460-02-2FCV-614 | Measurement | J460-02-2FCV-614 - Room J6.24 - Reheater Valve Control Error Code | J460-02-2FCV-614_Err | J460-02-2FCV-614_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1874 | J270-06-1PNL-001 | J460-02-2FCV-615 | Alarm | J460-02-2FCV-615 - Room J6.24 - J460-02-1ACU-607 Cooling Valve Control - Communication Failure Alarm | J460-02-2FCV-615_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-615_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1875 | J270-06-1PNL-001 | J460-02-2FCV-615 | Measurement | J460-02-2FCV-615 - Room J6.24 - J460-02-1ACU-607 Cooling Valve Control Forced Position | J460-02-2FCV-615_ForcePos | J460-02-2FCV-615_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1876 | J270-06-1PNL-001 | J460-02-2FCV-615 | Setting | J460-02-2FCV-615 - Room J6.24 - J460-02-1ACU-607 Cooling Valve Control Forced Calibration | J460-02-2FCV-615_ForceCal | J460-02-2FCV-615_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1877 | J270-06-1PNL-001 | J460-02-2FCV-615 | Measurement | J460-02-2FCV-615 - Room J6.24 - J460-02-1ACU-607 Cooling Valve Control Status | J460-02-2FCV-615_MotState | J460-02-2FCV-615_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1878 | J270-06-1PNL-001 | J460-02-2FCV-615 | Measurement | J460-02-2FCV-615 - Room J6.24 - J460-02-1ACU-607 Cooling Valve Control Actual SP | J460-02-2FCV-615_ActSP | J460-02-2FCV-615_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1879 | J270-06-1PNL-001 | J460-02-2FCV-615 | Setting | J460-02-2FCV-615 - Room J6.24 - J460-02-1ACU-607 Cooling Valve Control SP | J460-02-2FCV-615_SP | J460-02-2FCV-615_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1880 | J270-06-1PNL-001 | J460-02-2FCV-615 | Alarm | J460-02-2FCV-615 - Room J6.24 - J460-02-1ACU-607 Cooling Valve Control Fail to Open Alarm | J460-02-2FCV-615_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-615_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1881 | J270-06-1PNL-001 | J460-02-2FCV-615 | Alarm | J460-02-2FCV-615 - Room J6.24 - J460-02-1ACU-607 Cooling Valve Control Fail to Close Alarm | J460-02-2FCV-615_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-615_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1882 | J270-06-1PNL-001 | J460-02-2FCV-615 | Measurement | J460-02-2FCV-615 - Room J6.24 - J460-02-1ACU-607 Cooling Valve Control Error Code | J460-02-2FCV-615_Err | J460-02-2FCV-615_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1883 | J460-02-1CP-611 | J460-02-2TT-623 | Measurement | J460-02-2TT-623 - Room J6.24 - J460-02-1ACU-607 - Supply Temperature | J460-02-2TT-623_SupAirTemp | J460-02-2TT-623_SupAirTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1884 | J460-02-1CP-611 | J460-02-2TT-623 | Measurement | J460-02-2TT-623 - Room J6.24 - J460-02-1ACU-607 - Supply Temperature Field | J460-02-2TT-623_SupAirTemp_Field | J460-02-2TT-623_SupAirTemp_Field | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1885 | J460-02-1CP-611 | J460-02-2TT-623 | Alarm | J460-02-2TT-623 - Room J6.24 - J460-02-1ACU-607 - Supply Temperature High Alarm | J460-02-2TT-623_SupAirTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-623_SupAirTempHiAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 1886 | J460-02-1CP-611 | J460-02-2TT-623 | Setting | J460-02-2TT-623 - Room J6.24 - J460-02-1ACU-607 - Supply Temperature | J460-02-2TT-623_SupAirTemp_HASP | J460-02-2TT-623_SupAirTemp_HASP | - | 22 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1887 | J460-02-1CP-611 | J460-02-2TT-623 | Alarm | J460-02-2TT-623 - Room J6.24 - J460-02-1ACU-607 - Supply Temperature Low Alarm | J460-02-2TT-623_SupAirTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-623_SupAirTempLoAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 1888 | J460-02-1CP-611 | J460-02-2TT-623 | Setting | J460-02-2TT-623 - Room J6.24 - J460-02-1ACU-607 - Supply Temperature | J460-02-2TT-623_SupAirTemp_LASP | J460-02-2TT-623_SupAirTemp_LASP | 18 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1889 | J460-02-1CP-611 | J460-02-2TT-623 | Setting | J460-02-2TT-623 - Room J6.24 - J460-02-1ACU-607 - Supply Temperature Calibration Mode Selection | J460-02-2TT-623_SupAirTempCalModeSel | J460-02-2TT-623_SupAirTempCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1890 | J460-02-1CP-611 | J460-02-2TT-623 | Alarm | J460-02-2TT-623 - Room J6.24 - J460-02-1ACU-607 - Supply Temperature Calibration Still Active Alarm | J460-02-2TT-623_SupAirTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-623_SupAirTempCalModeAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1891 | J460-02-1CP-611 | J460-02-1ACU-607 | Measurement | J460-02-2XA-623 - J460-02-1ACU-607 - Alarm | J460-02-2XA-623_FCUAlm | J460-02-2XA-623_FCUAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1892 | J460-02-1CP-611 | J460-02-1ACU-607 | Alarm | J460-02-2XA-623 - J460-02-1ACU-607 - Alarm | J460-02-2XA-623_FCUAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2XA-623_FCUAlm_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 1893 | J460-02-1CP-611 | J460-02-1ACU-607 | Measurement | J460-02-2SC-623 - J460-02-1ACU-607 - Fan Speed | J460-02-2SC-623_FCUSpd | J460-02-2SC-623_FCUSpd | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1894 | J270-06-1PNL-001 | J460-02-1VAV-621 | Alarm | J460-02-1VAV-621 - Room J6.24 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-621_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-621_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1895 | J270-06-1PNL-001 | J460-02-1VAV-621 | Setting | J460-02-1VAV-621 - Room J6.24 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-621_Mode | J460-02-1VAV-621_Mode | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1896 | J270-06-1PNL-001 | J460-02-1VAV-621 | Setting | J460-02-1VAV-621 - Room J6.24 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-621_FlwSPShift | J460-02-1VAV-621_FlwSPShift | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1897 | J270-06-1PNL-001 | J460-02-1VAV-621 | Measurement | J460-02-1VAV-621 - Room J6.24 - Supply Air Flow Control Local Alarm | J460-02-1VAV-621_LocAlm | J460-02-1VAV-621_LocAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1898 | J270-06-1PNL-001 | J460-02-1VAV-621 | Alarm | J460-02-1VAV-621 - Room J6.24 - Supply Air Flow Control Local Alarm | J460-02-1VAV-621_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-621_LocAlm_Alm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1899 | J270-06-1PNL-001 | J460-02-1VAV-621 | Measurement | J460-02-1VAV-621 - Room J6.24 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-621_SumAlm | J460-02-1VAV-621_SumAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1900 | J270-06-1PNL-001 | J460-02-1VAV-621 | Alarm | J460-02-1VAV-621 - Room J6.24 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-621_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-621_SumAlm_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 1901 | J270-06-1PNL-001 | J460-02-1VAV-621 | Measurement | J460-02-1VAV-622 - Room J6.24 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-622_RmEaFlw | J460-02-1VAV-622_RmEaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1902 | J270-06-1PNL-001 | J460-02-1VAV-621 | Measurement | J460-02-1VAV-621 - Room J6.24 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-621_RmSaFlw | J460-02-1VAV-621_RmSaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1903 | J270-06-1PNL-001 | J460-02-2FCV-616 | Alarm | J460-02-2FCV-616 - Room J6.20 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-616_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-616_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1904 | J270-06-1PNL-001 | J460-02-2FCV-616 | Measurement | J460-02-2FCV-616 - Room J6.20 - Reheater Valve Control Forced Position | J460-02-2FCV-616_ForcePos | J460-02-2FCV-616_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1905 | J270-06-1PNL-001 | J460-02-2FCV-616 | Setting | J460-02-2FCV-616 - Room J6.20 - Reheater Valve Control Forced Calibration | J460-02-2FCV-616_ForceCal | J460-02-2FCV-616_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1906 | J270-06-1PNL-001 | J460-02-2FCV-616 | Measurement | J460-02-2FCV-616 - Room J6.20 - Reheater Valve Control Status | J460-02-2FCV-616_MotState | J460-02-2FCV-616_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1907 | J270-06-1PNL-001 | J460-02-2FCV-616 | Measurement | J460-02-2FCV-616 - Room J6.20 - Reheater Valve Control Actual SP | J460-02-2FCV-616_ActSP | J460-02-2FCV-616_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1908 | J270-06-1PNL-001 | J460-02-2FCV-616 | Setting | J460-02-2FCV-616 - Room J6.20 - Reheater Valve Control SP | J460-02-2FCV-616_SP | J460-02-2FCV-616_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1909 | J270-06-1PNL-001 | J460-02-2FCV-616 | Alarm | J460-02-2FCV-616 - Room J6.20 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-616_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-616_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1910 | J270-06-1PNL-001 | J460-02-2FCV-616 | Alarm | J460-02-2FCV-616 - Room J6.20 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-616_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-616_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1911 | J270-06-1PNL-001 | J460-02-2FCV-616 | Measurement | J460-02-2FCV-616 - Room J6.20 - Reheater Valve Control Error Code | J460-02-2FCV-616_Err | J460-02-2FCV-616_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1912 | J270-06-1PNL-001 | J460-02-1VAV-623 | Alarm | J460-02-1VAV-623 - Room J6.20 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-623_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-623_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1913 | J270-06-1PNL-001 | J460-02-1VAV-623 | Setting | J460-02-1VAV-623 - Room J6.20 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-623_Mode | J460-02-1VAV-623_Mode | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1914 | J270-06-1PNL-001 | J460-02-1VAV-623 | Setting | J460-02-1VAV-623 - Room J6.20 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-623_FlwSPShift | J460-02-1VAV-623_FlwSPShift | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1915 | J270-06-1PNL-001 | J460-02-1VAV-623 | Measurement | J460-02-1VAV-623 - Room J6.20 - Supply Air Flow Control Local Alarm | J460-02-1VAV-623_LocAlm | J460-02-1VAV-623_LocAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1916 | J270-06-1PNL-001 | J460-02-1VAV-623 | Alarm | J460-02-1VAV-623 - Room J6.20 - Supply Air Flow Control Local Alarm | J460-02-1VAV-623_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-623_LocAlm_Alm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1917 | J270-06-1PNL-001 | J460-02-1VAV-623 | Measurement | J460-02-1VAV-623 - Room J6.20 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-623_SumAlm | J460-02-1VAV-623_SumAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1918 | J270-06-1PNL-001 | J460-02-1VAV-623 | Alarm | J460-02-1VAV-623 - Room J6.20 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-623_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-623_SumAlm_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 1919 | J270-06-1PNL-001 | J460-02-1VAV-623 | Measurement | J460-02-1VAV-624-625 - Room J6.20 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-624-625_RmEaFlwTot | J460-02-1VAV-624-625_RmEaFlwTot | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1920 | J270-06-1PNL-001 | J460-02-1VAV-623 | Measurement | J460-02-1VAV-623 - Room J6.20 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-623_RmSaFlw | J460-02-1VAV-623_RmSaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1921 | J270-06-1PNL-001 | J460-02-2TC-612 | Alarm | J460-02-2TC-612 - Room J6.20 - Lab Controller - Communication Failure Alarm | J460-02-2TC-612_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TC-612_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1922 | J460-02-1CP-612 | J460-02-2TT-612 | Measurement | J460-02-2TT-612 - Room J6.20 - Temperature | J460-02-2TT-612_RmTemp | J460-02-2TT-612_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1923 | J460-02-1CP-612 | J460-02-2TT-612 | Alarm | J460-02-2TT-612 - Room J6.20 - Temperature High Alarm | J460-02-2TT-612_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-612_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1924 | J460-02-1CP-612 | J460-02-2TT-612 | Calculated | J460-02-2TT-612 - Room J6.20 - Temperature | J460-02-2TT-612_RmTemp_HASP | J460-02-2TT-612_RmTemp_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1925 | J460-02-1CP-612 | J460-02-2TT-612 | Alarm | J460-02-2TT-612 - Room J6.20 - Temperature Low Alarm | J460-02-2TT-612_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-612_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1926 | J460-02-1CP-612 | J460-02-2TT-612 | Calculated | J460-02-2TT-612 - Room J6.20 - Temperature | J460-02-2TT-612_RmTemp_LASP | J460-02-2TT-612_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1927 | J460-02-1CP-612 | J460-02-2TT-612 | Setting | J460-02-2TT-612 - Room J6.20 - Temperature Effective Setpoint | J460-02-2TT-612_EffRmTempSetpoint | J460-02-2TT-612_EffRmTempSetpoint | 22 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1928 | J460-02-1CP-612 | J460-02-2TT-612 | Setting | J460-02-2TT-612 - Room J6.20 - Temperature Proportional Band | J460-02-2TT-612_RmTemp_Set_P_Heat | J460-02-2TT-612_RmTemp_Set_P_Heat | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1929 | J460-02-1CP-612 | J460-02-2TT-612 | Setting | J460-02-2TT-612 - Room J6.20 - Temperature Integral Time | J460-02-2TT-612_RmTemp_Set_I_Heat | J460-02-2TT-612_RmTemp_Set_I_Heat | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1930 | J460-02-1CP-612 | J460-02-2TT-612 | Setting | J460-02-2TT-612 - Room J6.20 - Temperature Derivative Time | J460-02-2TT-612_RmTemp_Set_D_Heat | J460-02-2TT-612_RmTemp_Set_D_Heat | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1931 | J460-02-1CP-612 | J460-02-2TT-612 | Setting | J460-02-2TT-612 - Room J6.20 - Temperature Proportional Band | J460-02-2TT-612_RmTemp_Set_P_Cool | J460-02-2TT-612_RmTemp_Set_P_Cool | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1932 | J460-02-1CP-612 | J460-02-2TT-612 | Setting | J460-02-2TT-612 - Room J6.20 - Temperature Integral Time | J460-02-2TT-612_RmTemp_Set_I_Cool | J460-02-2TT-612_RmTemp_Set_I_Cool | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1933 | J460-02-1CP-612 | J460-02-2TT-612 | Setting | J460-02-2TT-612 - Room J6.20 - Temperature Derivative Time | J460-02-2TT-612_RmTemp_Set_D_Cool | J460-02-2TT-612_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1934 | J460-02-1CP-612 | J460-02-2MT-612 | Measurement | J460-02-2MT-612 - Room J6.20 - Humidity | J460-02-2MT-612_RmHum | J460-02-2MT-612_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1935 | J460-02-1CP-612 | J460-02-2MT-612 | Alarm | J460-02-2MT-612 - Room J6.20 - Humidity High Alarm | J460-02-2MT-612_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-612_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1936 | J460-02-1CP-612 | J460-02-2MT-612 | Setting | J460-02-2MT-612 - Room J6.20 - Humidity | J460-02-2MT-612_RmHum_HASP | J460-02-2MT-612_RmHum_HASP | - | 70 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1937 | J460-02-1CP-612 | J460-02-2MT-612 | Alarm | J460-02-2MT-612 - Room J6.20 - Humidity Low Alarm | J460-02-2MT-612_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-612_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1938 | J460-02-1CP-612 | J460-02-2MT-612 | Setting | J460-02-2MT-612 - Room J6.20 - Humidity | J460-02-2MT-612_RmHum_LASP | J460-02-2MT-612_RmHum_LASP | 40 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1939 | J270-06-1PNL-001 | J460-02-2FCV-617 | Alarm | J460-02-2FCV-617 - Room J6.20 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-617_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-617_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1940 | J270-06-1PNL-001 | J460-02-2FCV-617 | Measurement | J460-02-2FCV-617 - Room J6.20 - Reheater Valve Control Forced Position | J460-02-2FCV-617_ForcePos | J460-02-2FCV-617_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1941 | J270-06-1PNL-001 | J460-02-2FCV-617 | Setting | J460-02-2FCV-617 - Room J6.20 - Reheater Valve Control Forced Calibration | J460-02-2FCV-617_ForceCal | J460-02-2FCV-617_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1942 | J270-06-1PNL-001 | J460-02-2FCV-617 | Measurement | J460-02-2FCV-617 - Room J6.20 - Reheater Valve Control Status | J460-02-2FCV-617_MotState | J460-02-2FCV-617_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1943 | J270-06-1PNL-001 | J460-02-2FCV-617 | Measurement | J460-02-2FCV-617 - Room J6.20 - Reheater Valve Control Actual SP | J460-02-2FCV-617_ActSP | J460-02-2FCV-617_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1944 | J270-06-1PNL-001 | J460-02-2FCV-617 | Setting | J460-02-2FCV-617 - Room J6.20 - Reheater Valve Control SP | J460-02-2FCV-617_SP | J460-02-2FCV-617_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1945 | J270-06-1PNL-001 | J460-02-2FCV-617 | Alarm | J460-02-2FCV-617 - Room J6.20 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-617_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-617_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1946 | J270-06-1PNL-001 | J460-02-2FCV-617 | Alarm | J460-02-2FCV-617 - Room J6.20 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-617_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-617_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1947 | J270-06-1PNL-001 | J460-02-2FCV-617 | Measurement | J460-02-2FCV-617 - Room J6.20 - Reheater Valve Control Error Code | J460-02-2FCV-617_Err | J460-02-2FCV-617_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1948 | J270-06-1PNL-001 | J460-02-2FCV-618 | Alarm | J460-02-2FCV-618 - Room J6.20 - J460-02-1ACU-609 Cooling Valve Control - Communication Failure Alarm | J460-02-2FCV-618_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-618_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1949 | J270-06-1PNL-001 | J460-02-2FCV-618 | Measurement | J460-02-2FCV-618 - Room J6.20 - J460-02-1ACU-609 Cooling Valve Control Forced Position | J460-02-2FCV-618_ForcePos | J460-02-2FCV-618_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1950 | J270-06-1PNL-001 | J460-02-2FCV-618 | Setting | J460-02-2FCV-618 - Room J6.20 - J460-02-1ACU-609 Cooling Valve Control Forced Calibration | J460-02-2FCV-618_ForceCal | J460-02-2FCV-618_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1951 | J270-06-1PNL-001 | J460-02-2FCV-618 | Measurement | J460-02-2FCV-618 - Room J6.20 - J460-02-1ACU-609 Cooling Valve Control Status | J460-02-2FCV-618_MotState | J460-02-2FCV-618_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1952 | J270-06-1PNL-001 | J460-02-2FCV-618 | Measurement | J460-02-2FCV-618 - Room J6.20 - J460-02-1ACU-609 Cooling Valve Control Actual SP | J460-02-2FCV-618_ActSP | J460-02-2FCV-618_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1953 | J270-06-1PNL-001 | J460-02-2FCV-618 | Setting | J460-02-2FCV-618 - Room J6.20 - J460-02-1ACU-609 Cooling Valve Control SP | J460-02-2FCV-618_SP | J460-02-2FCV-618_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1954 | J270-06-1PNL-001 | J460-02-2FCV-618 | Alarm | J460-02-2FCV-618 - Room J6.20 - J460-02-1ACU-609 Cooling Valve Control Fail to Open Alarm | J460-02-2FCV-618_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-618_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1955 | J270-06-1PNL-001 | J460-02-2FCV-618 | Alarm | J460-02-2FCV-618 - Room J6.20 - J460-02-1ACU-609 Cooling Valve Control Fail to Close Alarm | J460-02-2FCV-618_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-618_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 1956 | J270-06-1PNL-001 | J460-02-2FCV-618 | Measurement | J460-02-2FCV-618 - Room J6.20 - J460-02-1ACU-609 Cooling Valve Control Error Code | J460-02-2FCV-618_Err | J460-02-2FCV-618_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1957 | J460-02-1CP-612 | J460-02-2TT-624 | Measurement | J460-02-2TT-624 - Room J6.20 - J460-02-1ACU-609 - Supply Temperature | J460-02-2TT-624_SupAirTemp | J460-02-2TT-624_SupAirTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1958 | J460-02-1CP-612 | J460-02-2TT-624 | Measurement | J460-02-2TT-624 - Room J6.20 - J460-02-1ACU-609 - Supply Temperature Field | J460-02-2TT-624_SupAirTemp_Field | J460-02-2TT-624_SupAirTemp_Field | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1959 | J460-02-1CP-612 | J460-02-2TT-624 | Alarm | J460-02-2TT-624 - Room J6.20 - J460-02-1ACU-609 - Supply Temperature High Alarm | J460-02-2TT-624_SupAirTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-624_SupAirTempHiAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 1960 | J460-02-1CP-612 | J460-02-2TT-624 | Setting | J460-02-2TT-624 - Room J6.20 - J460-02-1ACU-609 - Supply Temperature | J460-02-2TT-624_SupAirTemp_HASP | J460-02-2TT-624_SupAirTemp_HASP | - | 22 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1961 | J460-02-1CP-612 | J460-02-2TT-624 | Alarm | J460-02-2TT-624 - Room J6.20 - J460-02-1ACU-609 - Supply Temperature Low Alarm | J460-02-2TT-624_SupAirTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-624_SupAirTempLoAlm | 3 | Y | - | bar: State 2 to State 64
2.1 | 1962 | J460-02-1CP-612 | J460-02-2TT-624 | Setting | J460-02-2TT-624 - Room J6.20 - J460-02-1ACU-609 - Supply Temperature | J460-02-2TT-624_SupAirTemp_LASP | J460-02-2TT-624_SupAirTemp_LASP | 18 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1963 | J460-02-1CP-612 | J460-02-2TT-624 | Setting | J460-02-2TT-624 - Room J6.20 - J460-02-1ACU-609 - Supply Temperature Calibration Mode Selection | J460-02-2TT-624_SupAirTempCalModeSel | J460-02-2TT-624_SupAirTempCalModeSel | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1964 | J460-02-1CP-612 | J460-02-2TT-624 | Alarm | J460-02-2TT-624 - Room J6.20 - J460-02-1ACU-609 - Supply Temperature Calibration Still Active Alarm | J460-02-2TT-624_SupAirTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-624_SupAirTempCalModeAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1965 | J460-02-1CP-612 | J460-02-1ACU-609 | Measurement | J460-02-2XA-624 - J460-02-1ACU-609 - Alarm | J460-02-2XA-624_FCUAlm | J460-02-2XA-624_FCUAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1966 | J460-02-1CP-612 | J460-02-1ACU-609 | Alarm | J460-02-2XA-624 - J460-02-1ACU-609 - Alarm | J460-02-2XA-624_FCUAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2XA-624_FCUAlm_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 1967 | J460-02-1CP-612 | J460-02-1ACU-609 | Measurement | J460-02-2SC-624 - J460-02-1ACU-609 - Fan Speed | J460-02-2SC-624_FCUSpd | J460-02-2SC-624_FCUSpd | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1968 | J270-06-1PNL-001 | J460-02-1VAV-626 | Alarm | J460-02-1VAV-626 - Room J6.20 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-626_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-626_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1969 | J270-06-1PNL-001 | J460-02-1VAV-626 | Setting | J460-02-1VAV-626 - Room J6.20 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-626_Mode | J460-02-1VAV-626_Mode | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1970 | J270-06-1PNL-001 | J460-02-1VAV-626 | Setting | J460-02-1VAV-626 - Room J6.20 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-626_FlwSPShift | J460-02-1VAV-626_FlwSPShift | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1971 | J270-06-1PNL-001 | J460-02-1VAV-626 | Measurement | J460-02-1VAV-626 - Room J6.20 - Supply Air Flow Control Local Alarm | J460-02-1VAV-626_LocAlm | J460-02-1VAV-626_LocAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1972 | J270-06-1PNL-001 | J460-02-1VAV-626 | Alarm | J460-02-1VAV-626 - Room J6.20 - Supply Air Flow Control Local Alarm | J460-02-1VAV-626_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-626_LocAlm_Alm | 2 | Y | - | bar: State 2 to State 64
2.0 | 1973 | J270-06-1PNL-001 | J460-02-1VAV-626 | Measurement | J460-02-1VAV-626 - Room J6.20 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-626_SumAlm | J460-02-1VAV-626_SumAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1974 | J270-06-1PNL-001 | J460-02-1VAV-626 | Alarm | J460-02-1VAV-626 - Room J6.20 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-626_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-626_SumAlm_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 1975 | J270-06-1PNL-001 | J460-02-1VAV-626 | Measurement | J460-02-1VAV-627-628-629 - Room J6.20 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-627-628-629_RmEaFlwTot | J460-02-1VAV-627-628-629_RmEaFlwTot | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1976 | J270-06-1PNL-001 | J460-02-1VAV-626 | Measurement | J460-02-1VAV-626 - Room J6.20 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-626_RmSaFlw | J460-02-1VAV-626_RmSaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1977 | J270-06-1PNL-001 | J460-02-2TC-605 | Alarm | J460-02-2TC-605 - Room J6.17 - Lab Controller - Communication Failure Alarm | J460-02-2TC-605_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TC-605_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1978 | J460-02-1CP-605 | J460-02-2TT-605 | Measurement | J460-02-2TT-605 - Room J6.17 - Temperature | J460-02-2TT-605_RmTemp | J460-02-2TT-605_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1979 | J460-02-1CP-605 | J460-02-2TT-605 | Alarm | J460-02-2TT-605 - Room J6.17 - Temperature High Alarm | J460-02-2TT-605_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-605_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1980 | J460-02-1CP-605 | J460-02-2TT-605 | Calculated | J460-02-2TT-605 - Room J6.17 - Temperature | J460-02-2TT-605_RmTemp_HASP | J460-02-2TT-605_RmTemp_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1981 | J460-02-1CP-605 | J460-02-2TT-605 | Alarm | J460-02-2TT-605 - Room J6.17 - Temperature Low Alarm | J460-02-2TT-605_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-605_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1982 | J460-02-1CP-605 | J460-02-2TT-605 | Calculated | J460-02-2TT-605 - Room J6.17 - Temperature | J460-02-2TT-605_RmTemp_LASP | J460-02-2TT-605_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1983 | J460-02-1CP-605 | J460-02-2TT-605 | Setting | J460-02-2TT-605 - Room J6.17 - Temperature Setpoint | J460-02-2TT-605_RmTempSetpoint | J460-02-2TT-605_RmTempSetpoint | 20 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1984 | J460-02-1CP-605 | J460-02-2TT-605 | Setting | J460-02-2TT-605 - Room J6.17 - Temperature Proportional Band | J460-02-2TT-605_RmTemp_Set_P_Heat | J460-02-2TT-605_RmTemp_Set_P_Heat | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1985 | J460-02-1CP-605 | J460-02-2TT-605 | Setting | J460-02-2TT-605 - Room J6.17 - Temperature Integral Time | J460-02-2TT-605_RmTemp_Set_I_Heat | J460-02-2TT-605_RmTemp_Set_I_Heat | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1986 | J460-02-1CP-605 | J460-02-2TT-605 | Setting | J460-02-2TT-605 - Room J6.17 - Temperature Derivative Time | J460-02-2TT-605_RmTemp_Set_D_Heat | J460-02-2TT-605_RmTemp_Set_D_Heat | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1987 | J460-02-1CP-605 | J460-02-2TT-605 | Setting | J460-02-2TT-605 - Room J6.17 - Temperature Proportional Band | J460-02-2TT-605_RmTemp_Set_P_Cool | J460-02-2TT-605_RmTemp_Set_P_Cool | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1988 | J460-02-1CP-605 | J460-02-2TT-605 | Setting | J460-02-2TT-605 - Room J6.17 - Temperature Integral Time | J460-02-2TT-605_RmTemp_Set_I_Cool | J460-02-2TT-605_RmTemp_Set_I_Cool | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1989 | J460-02-1CP-605 | J460-02-2TT-605 | Setting | J460-02-2TT-605 - Room J6.17 - Temperature Derivative Time | J460-02-2TT-605_RmTemp_Set_D_Cool | J460-02-2TT-605_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1990 | J460-02-1CP-605 | J460-02-2MT-605 | Measurement | J460-02-2MT-605 - Room J6.17 - Humidity | J460-02-2MT-605_RmHum | J460-02-2MT-605_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1991 | J460-02-1CP-605 | J460-02-2MT-605 | Alarm | J460-02-2MT-605 - Room J6.17 - Humidity High Alarm | J460-02-2MT-605_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-605_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1992 | J460-02-1CP-605 | J460-02-2MT-605 | Setting | J460-02-2MT-605 - Room J6.17 - Humidity | J460-02-2MT-605_RmHum_HASP | J460-02-2MT-605_RmHum_HASP | - | 70 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1993 | J460-02-1CP-605 | J460-02-2MT-605 | Alarm | J460-02-2MT-605 - Room J6.17 - Humidity Low Alarm | J460-02-2MT-605_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-605_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 1994 | J460-02-1CP-605 | J460-02-2MT-605 | Setting | J460-02-2MT-605 - Room J6.17 - Humidity | J460-02-2MT-605_RmHum_LASP | J460-02-2MT-605_RmHum_LASP | 40 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1995 | J270-06-1PNL-001 | J460-02-2FCV-619 | Alarm | J460-02-2FCV-619 - Room J6.17 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-619_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-619_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 1996 | J270-06-1PNL-001 | J460-02-2FCV-619 | Measurement | J460-02-2FCV-619 - Room J6.17 - Reheater Valve Control Forced Position | J460-02-2FCV-619_ForcePos | J460-02-2FCV-619_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1997 | J270-06-1PNL-001 | J460-02-2FCV-619 | Setting | J460-02-2FCV-619 - Room J6.17 - Reheater Valve Control Forced Calibration | J460-02-2FCV-619_ForceCal | J460-02-2FCV-619_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 1998 | J270-06-1PNL-001 | J460-02-2FCV-619 | Measurement | J460-02-2FCV-619 - Room J6.17 - Reheater Valve Control Status | J460-02-2FCV-619_MotState | J460-02-2FCV-619_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 1999 | J270-06-1PNL-001 | J460-02-2FCV-619 | Measurement | J460-02-2FCV-619 - Room J6.17 - Reheater Valve Control Actual SP | J460-02-2FCV-619_ActSP | J460-02-2FCV-619_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2000 | J270-06-1PNL-001 | J460-02-2FCV-619 | Setting | J460-02-2FCV-619 - Room J6.17 - Reheater Valve Control SP | J460-02-2FCV-619_SP | J460-02-2FCV-619_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2001 | J270-06-1PNL-001 | J460-02-2FCV-619 | Alarm | J460-02-2FCV-619 - Room J6.17 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-619_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-619_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2002 | J270-06-1PNL-001 | J460-02-2FCV-619 | Alarm | J460-02-2FCV-619 - Room J6.17 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-619_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-619_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2003 | J270-06-1PNL-001 | J460-02-2FCV-619 | Measurement | J460-02-2FCV-619 - Room J6.17 - Reheater Valve Control Error Code | J460-02-2FCV-619_Err | J460-02-2FCV-619_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2004 | J270-06-1PNL-001 | J460-02-1VAV-630 | Alarm | J460-02-1VAV-630 - Room J6.17 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-630_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-630_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 2005 | J270-06-1PNL-001 | J460-02-1VAV-630 | Setting | J460-02-1VAV-630 - Room J6.17 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-630_Mode | J460-02-1VAV-630_Mode | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2006 | J270-06-1PNL-001 | J460-02-1VAV-630 | Setting | J460-02-1VAV-630 - Room J6.17 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-630_FlwSPShift | J460-02-1VAV-630_FlwSPShift | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2007 | J270-06-1PNL-001 | J460-02-1VAV-630 | Measurement | J460-02-1VAV-630 - Room J6.17 - Supply Air Flow Control Local Alarm | J460-02-1VAV-630_LocAlm | J460-02-1VAV-630_LocAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2008 | J270-06-1PNL-001 | J460-02-1VAV-630 | Alarm | J460-02-1VAV-630 - Room J6.17 - Supply Air Flow Control Local Alarm | J460-02-1VAV-630_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-630_LocAlm_Alm | 2 | Y | - | bar: State 2 to State 64
2.0 | 2009 | J270-06-1PNL-001 | J460-02-1VAV-630 | Measurement | J460-02-1VAV-630 - Room J6.17 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-630_SumAlm | J460-02-1VAV-630_SumAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2010 | J270-06-1PNL-001 | J460-02-1VAV-630 | Alarm | J460-02-1VAV-630 - Room J6.17 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-630_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-630_SumAlm_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 2011 | J270-06-1PNL-001 | J460-02-1VAV-630 | Measurement | J460-02-1VAV-631-632 - Room J6.17 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-631-632_RmEaFlw | J460-02-1VAV-631-632_RmEaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2012 | J270-06-1PNL-001 | J460-02-1VAV-630 | Measurement | J460-02-1VAV-630 - Room J6.17 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-630_RmSaFlw | J460-02-1VAV-630_RmSaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2013 | J270-06-1PNL-001 | J460-02-2TC-613 | Alarm | J460-02-2TC-613 - Room J6.17 - Lab Controller - Communication Failure Alarm | J460-02-2TC-613_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TC-613_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2014 | J460-02-1CP-613 | J460-02-2TT-613 | Measurement | J460-02-2TT-613 - Room J6.17 - Temperature | J460-02-2TT-613_RmTemp | J460-02-2TT-613_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2015 | J460-02-1CP-613 | J460-02-2TT-613 | Alarm | J460-02-2TT-613 - Room J6.17 - Temperature High Alarm | J460-02-2TT-613_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-613_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2016 | J460-02-1CP-613 | J460-02-2TT-613 | Calculated | J460-02-2TT-613 - Room J6.17 - Temperature | J460-02-2TT-613_RmTemp_HASP | J460-02-2TT-613_RmTemp_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2017 | J460-02-1CP-613 | J460-02-2TT-613 | Alarm | J460-02-2TT-613 - Room J6.17 - Temperature Low Alarm | J460-02-2TT-613_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-613_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2018 | J460-02-1CP-613 | J460-02-2TT-613 | Calculated | J460-02-2TT-613 - Room J6.17 - Temperature | J460-02-2TT-613_RmTemp_LASP | J460-02-2TT-613_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2019 | J460-02-1CP-613 | J460-02-2TT-613 | Setting | J460-02-2TT-613 - Room J6.17 - Temperature Setpoint | J460-02-2TT-613_RmTempSetpoint | J460-02-2TT-613_RmTempSetpoint | 20 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2020 | J460-02-1CP-613 | J460-02-2TT-613 | Setting | J460-02-2TT-613 - Room J6.17 - Temperature Proportional Band | J460-02-2TT-613_RmTemp_Set_P_Heat | J460-02-2TT-613_RmTemp_Set_P_Heat | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2021 | J460-02-1CP-613 | J460-02-2TT-613 | Setting | J460-02-2TT-613 - Room J6.17 - Temperature Integral Time | J460-02-2TT-613_RmTemp_Set_I_Heat | J460-02-2TT-613_RmTemp_Set_I_Heat | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2022 | J460-02-1CP-613 | J460-02-2TT-613 | Setting | J460-02-2TT-613 - Room J6.17 - Temperature Derivative Time | J460-02-2TT-613_RmTemp_Set_D_Heat | J460-02-2TT-613_RmTemp_Set_D_Heat | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2023 | J460-02-1CP-613 | J460-02-2TT-613 | Setting | J460-02-2TT-613 - Room J6.17 - Temperature Proportional Band | J460-02-2TT-613_RmTemp_Set_P_Cool | J460-02-2TT-613_RmTemp_Set_P_Cool | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2024 | J460-02-1CP-613 | J460-02-2TT-613 | Setting | J460-02-2TT-613 - Room J6.17 - Temperature Integral Time | J460-02-2TT-613_RmTemp_Set_I_Cool | J460-02-2TT-613_RmTemp_Set_I_Cool | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2025 | J460-02-1CP-613 | J460-02-2TT-613 | Setting | J460-02-2TT-613 - Room J6.17 - Temperature Derivative Time | J460-02-2TT-613_RmTemp_Set_D_Cool | J460-02-2TT-613_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2026 | J460-02-1CP-613 | J460-02-2MT-613 | Measurement | J460-02-2MT-613 - Room J6.17 - Humidity | J460-02-2MT-613_RmHum | J460-02-2MT-613_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2027 | J460-02-1CP-613 | J460-02-2MT-613 | Alarm | J460-02-2MT-613 - Room J6.17 - Humidity High Alarm | J460-02-2MT-613_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-613_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 2028 | J460-02-1CP-613 | J460-02-2MT-613 | Setting | J460-02-2MT-613 - Room J6.17 - Humidity | J460-02-2MT-613_RmHum_HASP | J460-02-2MT-613_RmHum_HASP | - | 70 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2029 | J460-02-1CP-613 | J460-02-2MT-613 | Alarm | J460-02-2MT-613 - Room J6.17 - Humidity Low Alarm | J460-02-2MT-613_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-613_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 2030 | J460-02-1CP-613 | J460-02-2MT-613 | Setting | J460-02-2MT-613 - Room J6.17 - Humidity | J460-02-2MT-613_RmHum_LASP | J460-02-2MT-613_RmHum_LASP | 40 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2031 | J270-06-1PNL-001 | J460-02-2FCV-620 | Alarm | J460-02-2FCV-620 - Room J6.17 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-620_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-620_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2032 | J270-06-1PNL-001 | J460-02-2FCV-620 | Measurement | J460-02-2FCV-620 - Room J6.17 - Reheater Valve Control Forced Position | J460-02-2FCV-620_ForcePos | J460-02-2FCV-620_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2033 | J270-06-1PNL-001 | J460-02-2FCV-620 | Setting | J460-02-2FCV-620 - Room J6.17 - Reheater Valve Control Forced Calibration | J460-02-2FCV-620_ForceCal | J460-02-2FCV-620_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2034 | J270-06-1PNL-001 | J460-02-2FCV-620 | Measurement | J460-02-2FCV-620 - Room J6.17 - Reheater Valve Control Status | J460-02-2FCV-620_MotState | J460-02-2FCV-620_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2035 | J270-06-1PNL-001 | J460-02-2FCV-620 | Measurement | J460-02-2FCV-620 - Room J6.17 - Reheater Valve Control Actual SP | J460-02-2FCV-620_ActSP | J460-02-2FCV-620_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2036 | J270-06-1PNL-001 | J460-02-2FCV-620 | Setting | J460-02-2FCV-620 - Room J6.17 - Reheater Valve Control SP | J460-02-2FCV-620_SP | J460-02-2FCV-620_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2037 | J270-06-1PNL-001 | J460-02-2FCV-620 | Alarm | J460-02-2FCV-620 - Room J6.17 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-620_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-620_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2038 | J270-06-1PNL-001 | J460-02-2FCV-620 | Alarm | J460-02-2FCV-620 - Room J6.17 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-620_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-620_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2039 | J270-06-1PNL-001 | J460-02-2FCV-620 | Measurement | J460-02-2FCV-620 - Room J6.17 - Reheater Valve Control Error Code | J460-02-2FCV-620_Err | J460-02-2FCV-620_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2040 | J270-06-1PNL-001 | J460-02-1VAV-633 | Alarm | J460-02-1VAV-633 - Room J6.17 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-633_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-633_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 2041 | J270-06-1PNL-001 | J460-02-1VAV-633 | Setting | J460-02-1VAV-633 - Room J6.17 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-633_Mode | J460-02-1VAV-633_Mode | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2042 | J270-06-1PNL-001 | J460-02-1VAV-633 | Setting | J460-02-1VAV-633 - Room J6.17 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-633_FlwSPShift | J460-02-1VAV-633_FlwSPShift | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2043 | J270-06-1PNL-001 | J460-02-1VAV-633 | Measurement | J460-02-1VAV-633 - Room J6.17 - Supply Air Flow Control Local Alarm | J460-02-1VAV-633_LocAlm | J460-02-1VAV-633_LocAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2044 | J270-06-1PNL-001 | J460-02-1VAV-633 | Alarm | J460-02-1VAV-633 - Room J6.17 - Supply Air Flow Control Local Alarm | J460-02-1VAV-633_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-633_LocAlm_Alm | 2 | Y | - | bar: State 2 to State 64
2.0 | 2045 | J270-06-1PNL-001 | J460-02-1VAV-633 | Measurement | J460-02-1VAV-633 - Room J6.17 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-633_SumAlm | J460-02-1VAV-633_SumAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2046 | J270-06-1PNL-001 | J460-02-1VAV-633 | Alarm | J460-02-1VAV-633 - Room J6.17 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-633_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-633_SumAlm_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 2047 | J270-06-1PNL-001 | J460-02-1VAV-633 | Measurement | J460-02-1VAV-634-635 - Room J6.17 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-634-635_RmEaFlw | J460-02-1VAV-634-635_RmEaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2048 | J270-06-1PNL-001 | J460-02-1VAV-633 | Measurement | J460-02-1VAV-633 - Room J6.17 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-633_RmSaFlw | J460-02-1VAV-633_RmSaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2049 | J270-06-1PNL-001 | J460-02-2TC-614 | Alarm | J460-02-2TC-614 - Room J6.17 - Lab Controller - Communication Failure Alarm | J460-02-2TC-614_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TC-614_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2050 | J460-02-1CP-614 | J460-02-2TT-614 | Measurement | J460-02-2TT-614 - Room J6.17 - Temperature | J460-02-2TT-614_RmTemp | J460-02-2TT-614_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2051 | J460-02-1CP-614 | J460-02-2TT-614 | Alarm | J460-02-2TT-614 - Room J6.17 - Temperature High Alarm | J460-02-2TT-614_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-614_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2052 | J460-02-1CP-614 | J460-02-2TT-614 | Calculated | J460-02-2TT-614 - Room J6.17 - Temperature | J460-02-2TT-614_RmTemp_HASP | J460-02-2TT-614_RmTemp_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2053 | J460-02-1CP-614 | J460-02-2TT-614 | Alarm | J460-02-2TT-614 - Room J6.17 - Temperature Low Alarm | J460-02-2TT-614_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-614_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2054 | J460-02-1CP-614 | J460-02-2TT-614 | Calculated | J460-02-2TT-614 - Room J6.17 - Temperature | J460-02-2TT-614_RmTemp_LASP | J460-02-2TT-614_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2055 | J460-02-1CP-614 | J460-02-2TT-614 | Setting | J460-02-2TT-614 - Room J6.17 - Temperature Setpoint | J460-02-2TT-614_RmTempSetpoint | J460-02-2TT-614_RmTempSetpoint | 20 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2056 | J460-02-1CP-614 | J460-02-2TT-614 | Setting | J460-02-2TT-614 - Room J6.17 - Temperature Proportional Band | J460-02-2TT-614_RmTemp_Set_P_Heat | J460-02-2TT-614_RmTemp_Set_P_Heat | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2057 | J460-02-1CP-614 | J460-02-2TT-614 | Setting | J460-02-2TT-614 - Room J6.17 - Temperature Integral Time | J460-02-2TT-614_RmTemp_Set_I_Heat | J460-02-2TT-614_RmTemp_Set_I_Heat | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2058 | J460-02-1CP-614 | J460-02-2TT-614 | Setting | J460-02-2TT-614 - Room J6.17 - Temperature Derivative Time | J460-02-2TT-614_RmTemp_Set_D_Heat | J460-02-2TT-614_RmTemp_Set_D_Heat | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2059 | J460-02-1CP-614 | J460-02-2TT-614 | Setting | J460-02-2TT-614 - Room J6.17 - Temperature Proportional Band | J460-02-2TT-614_RmTemp_Set_P_Cool | J460-02-2TT-614_RmTemp_Set_P_Cool | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2060 | J460-02-1CP-614 | J460-02-2TT-614 | Setting | J460-02-2TT-614 - Room J6.17 - Temperature Integral Time | J460-02-2TT-614_RmTemp_Set_I_Cool | J460-02-2TT-614_RmTemp_Set_I_Cool | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2061 | J460-02-1CP-614 | J460-02-2TT-614 | Setting | J460-02-2TT-614 - Room J6.17 - Temperature Derivative Time | J460-02-2TT-614_RmTemp_Set_D_Cool | J460-02-2TT-614_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2062 | J460-02-1CP-614 | J460-02-2MT-614 | Measurement | J460-02-2MT-614 - Room J6.17 - Humidity | J460-02-2MT-614_RmHum | J460-02-2MT-614_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2063 | J460-02-1CP-614 | J460-02-2MT-614 | Alarm | J460-02-2MT-614 - Room J6.17 - Humidity High Alarm | J460-02-2MT-614_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-614_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 2064 | J460-02-1CP-614 | J460-02-2MT-614 | Setting | J460-02-2MT-614 - Room J6.17 - Humidity | J460-02-2MT-614_RmHum_HASP | J460-02-2MT-614_RmHum_HASP | - | 70 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2065 | J460-02-1CP-614 | J460-02-2MT-614 | Alarm | J460-02-2MT-614 - Room J6.17 - Humidity Low Alarm | J460-02-2MT-614_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-614_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 2066 | J460-02-1CP-614 | J460-02-2MT-614 | Setting | J460-02-2MT-614 - Room J6.17 - Humidity | J460-02-2MT-614_RmHum_LASP | J460-02-2MT-614_RmHum_LASP | 40 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2067 | J270-06-1PNL-001 | J460-02-2FCV-621 | Alarm | J460-02-2FCV-621 - Room J6.17 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-621_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-621_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2068 | J270-06-1PNL-001 | J460-02-2FCV-621 | Measurement | J460-02-2FCV-621 - Room J6.17 - Reheater Valve Control Forced Position | J460-02-2FCV-621_ForcePos | J460-02-2FCV-621_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2069 | J270-06-1PNL-001 | J460-02-2FCV-621 | Setting | J460-02-2FCV-621 - Room J6.17 - Reheater Valve Control Forced Calibration | J460-02-2FCV-621_ForceCal | J460-02-2FCV-621_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2070 | J270-06-1PNL-001 | J460-02-2FCV-621 | Measurement | J460-02-2FCV-621 - Room J6.17 - Reheater Valve Control Status | J460-02-2FCV-621_MotState | J460-02-2FCV-621_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2071 | J270-06-1PNL-001 | J460-02-2FCV-621 | Measurement | J460-02-2FCV-621 - Room J6.17 - Reheater Valve Control Actual SP | J460-02-2FCV-621_ActSP | J460-02-2FCV-621_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2072 | J270-06-1PNL-001 | J460-02-2FCV-621 | Setting | J460-02-2FCV-621 - Room J6.17 - Reheater Valve Control SP | J460-02-2FCV-621_SP | J460-02-2FCV-621_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2073 | J270-06-1PNL-001 | J460-02-2FCV-621 | Alarm | J460-02-2FCV-621 - Room J6.17 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-621_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-621_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2074 | J270-06-1PNL-001 | J460-02-2FCV-621 | Alarm | J460-02-2FCV-621 - Room J6.17 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-621_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-621_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2075 | J270-06-1PNL-001 | J460-02-2FCV-621 | Measurement | J460-02-2FCV-621 - Room J6.17 - Reheater Valve Control Error Code | J460-02-2FCV-621_Err | J460-02-2FCV-621_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2076 | J270-06-1PNL-001 | J460-02-1VAV-636 | Alarm | J460-02-1VAV-636 - Room J6.17 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-636_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-636_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 2077 | J270-06-1PNL-001 | J460-02-1VAV-636 | Setting | J460-02-1VAV-636 - Room J6.17 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-636_Mode | J460-02-1VAV-636_Mode | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2078 | J270-06-1PNL-001 | J460-02-1VAV-636 | Setting | J460-02-1VAV-636 - Room J6.17 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-636_FlwSPShift | J460-02-1VAV-636_FlwSPShift | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2079 | J270-06-1PNL-001 | J460-02-1VAV-636 | Measurement | J460-02-1VAV-636 - Room J6.17 - Supply Air Flow Control Local Alarm | J460-02-1VAV-636_LocAlm | J460-02-1VAV-636_LocAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2080 | J270-06-1PNL-001 | J460-02-1VAV-636 | Alarm | J460-02-1VAV-636 - Room J6.17 - Supply Air Flow Control Local Alarm | J460-02-1VAV-636_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-636_LocAlm_Alm | 2 | Y | - | bar: State 2 to State 64
2.0 | 2081 | J270-06-1PNL-001 | J460-02-1VAV-636 | Measurement | J460-02-1VAV-636 - Room J6.17 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-636_SumAlm | J460-02-1VAV-636_SumAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2082 | J270-06-1PNL-001 | J460-02-1VAV-636 | Alarm | J460-02-1VAV-636 - Room J6.17 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-636_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-636_SumAlm_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 2083 | J270-06-1PNL-001 | J460-02-1VAV-636 | Measurement | J460-02-1VAV-637-638 - Room J6.17 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-637-638_RmEaFlw | J460-02-1VAV-637-638_RmEaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2084 | J270-06-1PNL-001 | J460-02-1VAV-636 | Measurement | J460-02-1VAV-636 - Room J6.17 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-636_RmSaFlw | J460-02-1VAV-636_RmSaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2085 | J270-06-1PNL-001 | J460-02-2TC-606 | Alarm | J460-02-2TC-606 - Room J6.14 - Lab Controller - Communication Failure Alarm | J460-02-2TC-606_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TC-606_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2086 | J460-02-1CP-606 | J460-02-2TT-606 | Measurement | J460-02-2TT-606 - Room J6.14 - Temperature | J460-02-2TT-606_RmTemp | J460-02-2TT-606_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2087 | J460-02-1CP-606 | J460-02-2TT-606 | Alarm | J460-02-2TT-606 - Room J6.14 - Temperature High Alarm | J460-02-2TT-606_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-606_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2088 | J460-02-1CP-606 | J460-02-2TT-606 | Calculated | J460-02-2TT-606 - Room J6.14 - Temperature | J460-02-2TT-606_RmTemp_HASP | J460-02-2TT-606_RmTemp_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2089 | J460-02-1CP-606 | J460-02-2TT-606 | Alarm | J460-02-2TT-606 - Room J6.14 - Temperature Low Alarm | J460-02-2TT-606_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-606_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2090 | J460-02-1CP-606 | J460-02-2TT-606 | Calculated | J460-02-2TT-606 - Room J6.14 - Temperature | J460-02-2TT-606_RmTemp_LASP | J460-02-2TT-606_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2091 | J460-02-1CP-606 | J460-02-2TT-606 | Setting | J460-02-2TT-606 - Room J6.14 - Temperature Setpoint | J460-02-2TT-606_RmTempSetpoint | J460-02-2TT-606_RmTempSetpoint | 20 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2092 | J460-02-1CP-606 | J460-02-2TT-606 | Setting | J460-02-2TT-606 - Room J6.14 - Temperature Proportional Band | J460-02-2TT-606_RmTemp_Set_P_Heat | J460-02-2TT-606_RmTemp_Set_P_Heat | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2093 | J460-02-1CP-606 | J460-02-2TT-606 | Setting | J460-02-2TT-606 - Room J6.14 - Temperature Integral Time | J460-02-2TT-606_RmTemp_Set_I_Heat | J460-02-2TT-606_RmTemp_Set_I_Heat | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2094 | J460-02-1CP-606 | J460-02-2TT-606 | Setting | J460-02-2TT-606 - Room J6.14 - Temperature Derivative Time | J460-02-2TT-606_RmTemp_Set_D_Heat | J460-02-2TT-606_RmTemp_Set_D_Heat | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2095 | J460-02-1CP-606 | J460-02-2TT-606 | Setting | J460-02-2TT-606 - Room J6.14 - Temperature Proportional Band | J460-02-2TT-606_RmTemp_Set_P_Cool | J460-02-2TT-606_RmTemp_Set_P_Cool | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2096 | J460-02-1CP-606 | J460-02-2TT-606 | Setting | J460-02-2TT-606 - Room J6.14 - Temperature Integral Time | J460-02-2TT-606_RmTemp_Set_I_Cool | J460-02-2TT-606_RmTemp_Set_I_Cool | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2097 | J460-02-1CP-606 | J460-02-2TT-606 | Setting | J460-02-2TT-606 - Room J6.14 - Temperature Derivative Time | J460-02-2TT-606_RmTemp_Set_D_Cool | J460-02-2TT-606_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2098 | J460-02-1CP-606 | J460-02-2MT-606 | Measurement | J460-02-2MT-606 - Room J6.14 - Humidity | J460-02-2MT-606_RmHum | J460-02-2MT-606_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2099 | J460-02-1CP-606 | J460-02-2MT-606 | Alarm | J460-02-2MT-606 - Room J6.14 - Humidity High Alarm | J460-02-2MT-606_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-606_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 2100 | J460-02-1CP-606 | J460-02-2MT-606 | Setting | J460-02-2MT-606 - Room J6.14 - Humidity | J460-02-2MT-606_RmHum_HASP | J460-02-2MT-606_RmHum_HASP | - | 70 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2101 | J460-02-1CP-606 | J460-02-2MT-606 | Alarm | J460-02-2MT-606 - Room J6.14 - Humidity Low Alarm | J460-02-2MT-606_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-606_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 2102 | J460-02-1CP-606 | J460-02-2MT-606 | Setting | J460-02-2MT-606 - Room J6.14 - Humidity | J460-02-2MT-606_RmHum_LASP | J460-02-2MT-606_RmHum_LASP | 40 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2103 | J270-06-1PNL-001 | J460-02-2FCV-622 | Alarm | J460-02-2FCV-622 - Room J6.14 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-622_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-622_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2104 | J270-06-1PNL-001 | J460-02-2FCV-622 | Measurement | J460-02-2FCV-622 - Room J6.14 - Reheater Valve Control Forced Position | J460-02-2FCV-622_ForcePos | J460-02-2FCV-622_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2105 | J270-06-1PNL-001 | J460-02-2FCV-622 | Setting | J460-02-2FCV-622 - Room J6.14 - Reheater Valve Control Forced Calibration | J460-02-2FCV-622_ForceCal | J460-02-2FCV-622_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2106 | J270-06-1PNL-001 | J460-02-2FCV-622 | Measurement | J460-02-2FCV-622 - Room J6.14 - Reheater Valve Control Status | J460-02-2FCV-622_MotState | J460-02-2FCV-622_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2107 | J270-06-1PNL-001 | J460-02-2FCV-622 | Measurement | J460-02-2FCV-622 - Room J6.14 - Reheater Valve Control Actual SP | J460-02-2FCV-622_ActSP | J460-02-2FCV-622_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2108 | J270-06-1PNL-001 | J460-02-2FCV-622 | Setting | J460-02-2FCV-622 - Room J6.14 - Reheater Valve Control SP | J460-02-2FCV-622_SP | J460-02-2FCV-622_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2109 | J270-06-1PNL-001 | J460-02-2FCV-622 | Alarm | J460-02-2FCV-622 - Room J6.14 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-622_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-622_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2110 | J270-06-1PNL-001 | J460-02-2FCV-622 | Alarm | J460-02-2FCV-622 - Room J6.14 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-622_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-622_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2111 | J270-06-1PNL-001 | J460-02-2FCV-622 | Measurement | J460-02-2FCV-622 - Room J6.14 - Reheater Valve Control Error Code | J460-02-2FCV-622_Err | J460-02-2FCV-622_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2112 | J270-06-1PNL-001 | J460-02-1VAV-639 | Alarm | J460-02-1VAV-639 - Room J6.14 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-639_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-639_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 2113 | J270-06-1PNL-001 | J460-02-1VAV-639 | Setting | J460-02-1VAV-639 - Room J6.14 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-639_Mode | J460-02-1VAV-639_Mode | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2114 | J270-06-1PNL-001 | J460-02-1VAV-639 | Setting | J460-02-1VAV-639 - Room J6.14 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-639_FlwSPShift | J460-02-1VAV-639_FlwSPShift | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2115 | J270-06-1PNL-001 | J460-02-1VAV-639 | Measurement | J460-02-1VAV-639 - Room J6.14 - Supply Air Flow Control Local Alarm | J460-02-1VAV-639_LocAlm | J460-02-1VAV-639_LocAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2116 | J270-06-1PNL-001 | J460-02-1VAV-639 | Alarm | J460-02-1VAV-639 - Room J6.14 - Supply Air Flow Control Local Alarm | J460-02-1VAV-639_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-639_LocAlm_Alm | 2 | Y | - | bar: State 2 to State 64
2.0 | 2117 | J270-06-1PNL-001 | J460-02-1VAV-639 | Measurement | J460-02-1VAV-639 - Room J6.14 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-639_SumAlm | J460-02-1VAV-639_SumAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2118 | J270-06-1PNL-001 | J460-02-1VAV-639 | Alarm | J460-02-1VAV-639 - Room J6.14 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-639_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-639_SumAlm_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 2119 | J270-06-1PNL-001 | J460-02-1VAV-639 | Measurement | J460-02-1VAV-640-641 - Room J6.14 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-640-641_RmEaFlw | J460-02-1VAV-640-641_RmEaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2120 | J270-06-1PNL-001 | J460-02-1VAV-639 | Measurement | J460-02-1VAV-639 - Room J6.14 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-639_RmSaFlw | J460-02-1VAV-639_RmSaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2121 | J270-06-1PNL-001 | J460-02-2TC-615 | Alarm | J460-02-2TC-615 - Room J6.14 - Lab Controller - Communication Failure Alarm | J460-02-2TC-615_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TC-615_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2122 | J460-02-1CP-615 | J460-02-2TT-615 | Measurement | J460-02-2TT-615 - Room J6.14 - Temperature | J460-02-2TT-615_RmTemp | J460-02-2TT-615_RmTemp | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2123 | J460-02-1CP-615 | J460-02-2TT-615 | Alarm | J460-02-2TT-615 - Room J6.14 - Temperature High Alarm | J460-02-2TT-615_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-615_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2124 | J460-02-1CP-615 | J460-02-2TT-615 | Calculated | J460-02-2TT-615 - Room J6.14 - Temperature | J460-02-2TT-615_RmTemp_HASP | J460-02-2TT-615_RmTemp_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2125 | J460-02-1CP-615 | J460-02-2TT-615 | Alarm | J460-02-2TT-615 - Room J6.14 - Temperature Low Alarm | J460-02-2TT-615_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2TT-615_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2126 | J460-02-1CP-615 | J460-02-2TT-615 | Calculated | J460-02-2TT-615 - Room J6.14 - Temperature | J460-02-2TT-615_RmTemp_LASP | J460-02-2TT-615_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2127 | J460-02-1CP-615 | J460-02-2TT-615 | Setting | J460-02-2TT-615 - Room J6.14 - Temperature Setpoint | J460-02-2TT-615_RmTempSetpoint | J460-02-2TT-615_RmTempSetpoint | 20 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2128 | J460-02-1CP-615 | J460-02-2TT-615 | Setting | J460-02-2TT-615 - Room J6.14 - Temperature Proportional Band | J460-02-2TT-615_RmTemp_Set_P_Heat | J460-02-2TT-615_RmTemp_Set_P_Heat | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2129 | J460-02-1CP-615 | J460-02-2TT-615 | Setting | J460-02-2TT-615 - Room J6.14 - Temperature Integral Time | J460-02-2TT-615_RmTemp_Set_I_Heat | J460-02-2TT-615_RmTemp_Set_I_Heat | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2130 | J460-02-1CP-615 | J460-02-2TT-615 | Setting | J460-02-2TT-615 - Room J6.14 - Temperature Derivative Time | J460-02-2TT-615_RmTemp_Set_D_Heat | J460-02-2TT-615_RmTemp_Set_D_Heat | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2131 | J460-02-1CP-615 | J460-02-2TT-615 | Setting | J460-02-2TT-615 - Room J6.14 - Temperature Proportional Band | J460-02-2TT-615_RmTemp_Set_P_Cool | J460-02-2TT-615_RmTemp_Set_P_Cool | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2132 | J460-02-1CP-615 | J460-02-2TT-615 | Setting | J460-02-2TT-615 - Room J6.14 - Temperature Integral Time | J460-02-2TT-615_RmTemp_Set_I_Cool | J460-02-2TT-615_RmTemp_Set_I_Cool | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2133 | J460-02-1CP-615 | J460-02-2TT-615 | Setting | J460-02-2TT-615 - Room J6.14 - Temperature Derivative Time | J460-02-2TT-615_RmTemp_Set_D_Cool | J460-02-2TT-615_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2134 | J460-02-1CP-615 | J460-02-2MT-615 | Measurement | J460-02-2MT-615 - Room J6.14 - Humidity | J460-02-2MT-615_RmHum | J460-02-2MT-615_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2135 | J460-02-1CP-615 | J460-02-2MT-615 | Alarm | J460-02-2MT-615 - Room J6.14 - Humidity High Alarm | J460-02-2MT-615_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-615_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 2136 | J460-02-1CP-615 | J460-02-2MT-615 | Setting | J460-02-2MT-615 - Room J6.14 - Humidity | J460-02-2MT-615_RmHum_HASP | J460-02-2MT-615_RmHum_HASP | - | 70 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2137 | J460-02-1CP-615 | J460-02-2MT-615 | Alarm | J460-02-2MT-615 - Room J6.14 - Humidity Low Alarm | J460-02-2MT-615_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2MT-615_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 2138 | J460-02-1CP-615 | J460-02-2MT-615 | Setting | J460-02-2MT-615 - Room J6.14 - Humidity | J460-02-2MT-615_RmHum_LASP | J460-02-2MT-615_RmHum_LASP | 40 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2139 | J270-06-1PNL-001 | J460-02-2FCV-623 | Alarm | J460-02-2FCV-623 - Room J6.14 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-623_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-623_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2140 | J270-06-1PNL-001 | J460-02-2FCV-623 | Measurement | J460-02-2FCV-623 - Room J6.14 - Reheater Valve Control Forced Position | J460-02-2FCV-623_ForcePos | J460-02-2FCV-623_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2141 | J270-06-1PNL-001 | J460-02-2FCV-623 | Setting | J460-02-2FCV-623 - Room J6.14 - Reheater Valve Control Forced Calibration | J460-02-2FCV-623_ForceCal | J460-02-2FCV-623_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2142 | J270-06-1PNL-001 | J460-02-2FCV-623 | Measurement | J460-02-2FCV-623 - Room J6.14 - Reheater Valve Control Status | J460-02-2FCV-623_MotState | J460-02-2FCV-623_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2143 | J270-06-1PNL-001 | J460-02-2FCV-623 | Measurement | J460-02-2FCV-623 - Room J6.14 - Reheater Valve Control Actual SP | J460-02-2FCV-623_ActSP | J460-02-2FCV-623_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2144 | J270-06-1PNL-001 | J460-02-2FCV-623 | Setting | J460-02-2FCV-623 - Room J6.14 - Reheater Valve Control SP | J460-02-2FCV-623_SP | J460-02-2FCV-623_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2145 | J270-06-1PNL-001 | J460-02-2FCV-623 | Alarm | J460-02-2FCV-623 - Room J6.14 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-623_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-623_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2146 | J270-06-1PNL-001 | J460-02-2FCV-623 | Alarm | J460-02-2FCV-623 - Room J6.14 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-623_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-2FCV-623_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2147 | J270-06-1PNL-001 | J460-02-2FCV-623 | Measurement | J460-02-2FCV-623 - Room J6.14 - Reheater Valve Control Error Code | J460-02-2FCV-623_Err | J460-02-2FCV-623_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2148 | J270-06-1PNL-001 | J460-02-1VAV-642 | Alarm | J460-02-1VAV-642 - Room J6.14 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-642_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-642_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 2149 | J270-06-1PNL-001 | J460-02-1VAV-642 | Setting | J460-02-1VAV-642 - Room J6.14 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-642_Mode | J460-02-1VAV-642_Mode | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2150 | J270-06-1PNL-001 | J460-02-1VAV-642 | Setting | J460-02-1VAV-642 - Room J6.14 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-642_FlwSPShift | J460-02-1VAV-642_FlwSPShift | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2151 | J270-06-1PNL-001 | J460-02-1VAV-642 | Measurement | J460-02-1VAV-642 - Room J6.14 - Supply Air Flow Control Local Alarm | J460-02-1VAV-642_LocAlm | J460-02-1VAV-642_LocAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2152 | J270-06-1PNL-001 | J460-02-1VAV-642 | Alarm | J460-02-1VAV-642 - Room J6.14 - Supply Air Flow Control Local Alarm | J460-02-1VAV-642_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-642_LocAlm_Alm | 2 | Y | - | bar: State 2 to State 64
2.0 | 2153 | J270-06-1PNL-001 | J460-02-1VAV-642 | Measurement | J460-02-1VAV-642 - Room J6.14 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-642_SumAlm | J460-02-1VAV-642_SumAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2154 | J270-06-1PNL-001 | J460-02-1VAV-642 | Alarm | J460-02-1VAV-642 - Room J6.14 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-642_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-02-1VAV-642_SumAlm_Alm | 1 | Y | - | bar: State 2 to State 64
2.1 | 2155 | J270-06-1PNL-001 | J460-02-1VAV-642 | Measurement | J460-02-1VAV-643-664 - Room J6.14 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-643-664_RmEaFlw | J460-02-1VAV-643-664_RmEaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2156 | J270-06-1PNL-001 | J460-02-1VAV-642 | Measurement | J460-02-1VAV-642 - Room J6.14 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-642_RmSaFlw | J460-02-1VAV-642_RmSaFlw | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2157 | J270-06-1PNL-001 | J460-01-2TC-001 | Alarm | J460-01-2TC-001 - Room J0.07 - Room Controller - Communication Failure Alarm | J460-01-2TC-001_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TC-001_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2158 | J460-01-1CP-001 | J460-01-2TT-001 | Measurement | J460-01-2TT-001 - Room J0.07 - Temperature | J460-01-2TT-001_RmTemp | J460-01-2TT-001_RmTemp | 0 | 52 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2159 | J460-01-1CP-001 | J460-01-2TT-001 | Alarm | J460-01-2TT-001 - Room J0.07 - Temperature High Alarm | J460-01-2TT-001_RmTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-001_RmTempHiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2160 | J460-01-1CP-001 | J460-01-2TT-001 | Calculated | J460-01-2TT-001 - Room J0.07 - Temperature | J460-01-2TT-001_RmTemp_HASP | J460-01-2TT-001_RmTemp_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2161 | J460-01-1CP-001 | J460-01-2TT-001 | Alarm | J460-01-2TT-001 - Room J0.07 - Temperature Low Alarm | J460-01-2TT-001_RmTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2TT-001_RmTempLoAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2162 | J460-01-1CP-001 | J460-01-2TT-001 | Calculated | J460-01-2TT-001 - Room J0.07 - Temperature | J460-01-2TT-001_RmTemp_LASP | J460-01-2TT-001_RmTemp_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2163 | J460-01-1CP-001 | J460-01-2TT-001 | Calculated | J460-01-2TT-001 - Room J0.07 - Temperature Effective Setpoint | J460-01-2TT-001_RmTempEffSetpoint | J460-01-2TT-001_RmTempEffSetpoint | Calculated | Calculated | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2164 | J460-01-1CP-001 | J460-01-2TT-001 | Setting | J460-01-2TT-001 - Room J0.07 - Temperature Setpoint CPA | J460-01-2TT-001_RmTempSetpointCPA | J460-01-2TT-001_RmTempSetpointCPA | -3 | 3 | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2165 | J460-01-1CP-001 | J460-01-2TT-001 | Setting | J460-01-2TT-001 - Room J0.07 - Temperature Proportional Band | J460-01-2TT-001_RmTemp_Set_P_Heat | J460-01-2TT-001_RmTemp_Set_P_Heat | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2166 | J460-01-1CP-001 | J460-01-2TT-001 | Setting | J460-01-2TT-001 - Room J0.07 - Temperature Integral Time | J460-01-2TT-001_RmTemp_Set_I_Heat | J460-01-2TT-001_RmTemp_Set_I_Heat | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2167 | J460-01-1CP-001 | J460-01-2TT-001 | Setting | J460-01-2TT-001 - Room J0.07 - Temperature Derivative Time | J460-01-2TT-001_RmTemp_Set_D_Heat | J460-01-2TT-001_RmTemp_Set_D_Heat | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2168 | J460-01-1CP-001 | J460-01-2TT-001 | Setting | J460-01-2TT-001 - Room J0.07 - Temperature Proportional Band | J460-01-2TT-001_RmTemp_Set_P_Cool | J460-01-2TT-001_RmTemp_Set_P_Cool | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2169 | J460-01-1CP-001 | J460-01-2TT-001 | Setting | J460-01-2TT-001 - Room J0.07 - Temperature Integral Time | J460-01-2TT-001_RmTemp_Set_I_Cool | J460-01-2TT-001_RmTemp_Set_I_Cool | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2170 | J460-01-1CP-001 | J460-01-2TT-001 | Setting | J460-01-2TT-001 - Room J0.07 - Temperature Derivative Time | J460-01-2TT-001_RmTemp_Set_D_Cool | J460-01-2TT-001_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2171 | J460-01-1CP-001 | J460-01-2MT-001 | Measurement | J460-01-2MT-001 - Room J0.07 - Humidity | J460-01-2MT-001_RmHum | J460-01-2MT-001_RmHum | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2172 | J460-01-1CP-001 | J460-01-2MT-001 | Alarm | J460-01-2MT-001 - Room J0.07 - Humidity High Alarm | J460-01-2MT-001_RmHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-001_RmHumHiAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 2173 | J460-01-1CP-001 | J460-01-2MT-001 | Setting | J460-01-2MT-001 - Room J0.07 - Humidity | J460-01-2MT-001_RmHum_HASP | J460-01-2MT-001_RmHum_HASP | - | 60 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2174 | J460-01-1CP-001 | J460-01-2MT-001 | Alarm | J460-01-2MT-001 - Room J0.07 - Humidity Low Alarm | J460-01-2MT-001_RmHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2MT-001_RmHumLoAlm | 3 | Y | - | bar: State 2 to State 64
1.0 | 2175 | J460-01-1CP-001 | J460-01-2MT-001 | Setting | J460-01-2MT-001 - Room J0.07 - Humidity | J460-01-2MT-001_RmHum_LASP | J460-01-2MT-001_RmHum_LASP | 30 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2176 | J460-01-1CP-001 | J460-01-2XT-001 | Measurement | J460-01-2XT-001 - Room J0.07 - CO2 Concentration | J460-01-2XT-001_RmCO2 | J460-01-2XT-001_RmCO2 | 0 | 2000 | [11 empty] | - | - | - | - | - | - | 200 | - | ppm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2177 | J460-01-1CP-001 | J460-01-2XT-001 | Alarm | J460-01-2XT-001 - Room J0.07 - CO2 Concentration High Alarm | J460-01-2XT-001_RmCO2HiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2XT-001_RmCO2HiAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2178 | J460-01-1CP-001 | J460-01-2XT-001 | Setting | J460-01-2XT-001 - Room J0.07 - CO2 Concentration | J460-01-2XT-001_RmCO2_HASP | J460-01-2XT-001_RmCO2_HASP | - | 1500 | [11 empty] | - | - | - | - | - | - | 200 | - | ppm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2179 | J460-01-1CP-001 | J460-01-2XT-001 | Setting | J460-01-2XT-001 - Room J0.07 - CO2 Concentration Setpoint | J460-01-2XT-001_RmCO2Setpoint | J460-01-2XT-001_RmCO2Setpoint | - | 800 | [11 empty] | - | - | - | - | - | - | 220 | - | ppm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2180 | J460-01-1CP-001 | J460-01-2XT-001 | Setting | J460-01-2XT-001 - Room J0.07 - CO2 Concentration Proportional Band | J460-01-2XT-001_RmCO2_Set_P | J460-01-2XT-001_RmCO2_Set_P | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2181 | J460-01-1CP-001 | J460-01-2XT-001 | Setting | J460-01-2XT-001 - Room J0.07 - CO2 Concentration Integral Time | J460-01-2XT-001_RmCO2_Set_I | J460-01-2XT-001_RmCO2_Set_I | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2182 | J460-01-1CP-001 | J460-01-2XT-001 | Setting | J460-01-2XT-001 - Room J0.07 - CO2 Concentration Derivative Time | J460-01-2XT-001_RmCO2_Set_D | J460-01-2XT-001_RmCO2_Set_D | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2183 | J460-01-1CP-001 | J460-01-2XT-002 | Measurement | J460-01-2XT-002 - Room J0.07 - Occupied | J460-01-2XT-002_RmOcc | J460-01-2XT-002_RmOcc | UNOCC | OCC | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2184 | J270-06-1PNL-001 | J460-01-2FCV-002 | Alarm | J460-01-2FCV-002 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-002_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-002_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2185 | J270-06-1PNL-001 | J460-01-2FCV-002 | Measurement | J460-01-2FCV-002 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Position | J460-01-2FCV-002_ForcePos | J460-01-2FCV-002_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2186 | J270-06-1PNL-001 | J460-01-2FCV-002 | Setting | J460-01-2FCV-002 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Calibration | J460-01-2FCV-002_ForceCal | J460-01-2FCV-002_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2187 | J270-06-1PNL-001 | J460-01-2FCV-002 | Measurement | J460-01-2FCV-002 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Status | J460-01-2FCV-002_MotState | J460-01-2FCV-002_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2188 | J270-06-1PNL-001 | J460-01-2FCV-002 | Measurement | J460-01-2FCV-002 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Actual SP | J460-01-2FCV-002_ActSP | J460-01-2FCV-002_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2189 | J270-06-1PNL-001 | J460-01-2FCV-002 | Setting | J460-01-2FCV-002 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control SP | J460-01-2FCV-002_SP | J460-01-2FCV-002_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2190 | J270-06-1PNL-001 | J460-01-2FCV-002 | Alarm | J460-01-2FCV-002 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-002_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-002_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2191 | J270-06-1PNL-001 | J460-01-2FCV-002 | Alarm | J460-01-2FCV-002 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-002_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-002_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2192 | J270-06-1PNL-001 | J460-01-2FCV-002 | Measurement | J460-01-2FCV-002 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Error Code | J460-01-2FCV-002_Err | J460-01-2FCV-002_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2193 | J270-06-1PNL-001 | J460-01-2FCV-003 | Alarm | J460-01-2FCV-003 - Room J0.07 - J460-01-1ACU-002 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-003_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-003_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2194 | J270-06-1PNL-001 | J460-01-2FCV-003 | Measurement | J460-01-2FCV-003 - Room J0.07 - J460-01-1ACU-002 Heating Valve Control Forced Position | J460-01-2FCV-003_ForcePos | J460-01-2FCV-003_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2195 | J270-06-1PNL-001 | J460-01-2FCV-003 | Setting | J460-01-2FCV-003 - Room J0.07 - J460-01-1ACU-002 Heating Valve Control Forced Calibration | J460-01-2FCV-003_ForceCal | J460-01-2FCV-003_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2196 | J270-06-1PNL-001 | J460-01-2FCV-003 | Measurement | J460-01-2FCV-003 - Room J0.07 - J460-01-1ACU-002 Heating Valve Control Status | J460-01-2FCV-003_MotState | J460-01-2FCV-003_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2197 | J270-06-1PNL-001 | J460-01-2FCV-003 | Measurement | J460-01-2FCV-003 - Room J0.07 - J460-01-1ACU-002 Heating Valve Control Actual SP | J460-01-2FCV-003_ActSP | J460-01-2FCV-003_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2198 | J270-06-1PNL-001 | J460-01-2FCV-003 | Setting | J460-01-2FCV-003 - Room J0.07 - J460-01-1ACU-002 Heating Valve Control SP | J460-01-2FCV-003_SP | J460-01-2FCV-003_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2199 | J270-06-1PNL-001 | J460-01-2FCV-003 | Alarm | J460-01-2FCV-003 - Room J0.07 - J460-01-1ACU-002 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-003_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-003_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2200 | J270-06-1PNL-001 | J460-01-2FCV-003 | Alarm | J460-01-2FCV-003 - Room J0.07 - J460-01-1ACU-002 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-003_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-003_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2201 | J270-06-1PNL-001 | J460-01-2FCV-003 | Measurement | J460-01-2FCV-003 - Room J0.07 - J460-01-1ACU-002 Heating Valve Control Error Code | J460-01-2FCV-003_Err | J460-01-2FCV-003_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2202 | J270-06-1PNL-001 | J460-01-2FCV-004 | Alarm | J460-01-2FCV-004 - Room J0.07 - J460-01-1ACU-003 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-004_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-004_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2203 | J270-06-1PNL-001 | J460-01-2FCV-004 | Measurement | J460-01-2FCV-004 - Room J0.07 - J460-01-1ACU-003 Heating Valve Control Forced Position | J460-01-2FCV-004_ForcePos | J460-01-2FCV-004_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2204 | J270-06-1PNL-001 | J460-01-2FCV-004 | Setting | J460-01-2FCV-004 - Room J0.07 - J460-01-1ACU-003 Heating Valve Control Forced Calibration | J460-01-2FCV-004_ForceCal | J460-01-2FCV-004_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2205 | J270-06-1PNL-001 | J460-01-2FCV-004 | Measurement | J460-01-2FCV-004 - Room J0.07 - J460-01-1ACU-003 Heating Valve Control Status | J460-01-2FCV-004_MotState | J460-01-2FCV-004_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2206 | J270-06-1PNL-001 | J460-01-2FCV-004 | Measurement | J460-01-2FCV-004 - Room J0.07 - J460-01-1ACU-003 Heating Valve Control Actual SP | J460-01-2FCV-004_ActSP | J460-01-2FCV-004_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2207 | J270-06-1PNL-001 | J460-01-2FCV-004 | Setting | J460-01-2FCV-004 - Room J0.07 - J460-01-1ACU-003 Heating Valve Control SP | J460-01-2FCV-004_SP | J460-01-2FCV-004_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2208 | J270-06-1PNL-001 | J460-01-2FCV-004 | Alarm | J460-01-2FCV-004 - Room J0.07 - J460-01-1ACU-003 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-004_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-004_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2209 | J270-06-1PNL-001 | J460-01-2FCV-004 | Alarm | J460-01-2FCV-004 - Room J0.07 - J460-01-1ACU-003 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-004_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-004_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2210 | J270-06-1PNL-001 | J460-01-2FCV-004 | Measurement | J460-01-2FCV-004 - Room J0.07 - J460-01-1ACU-003 Heating Valve Control Error Code | J460-01-2FCV-004_Err | J460-01-2FCV-004_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2211 | J270-06-1PNL-001 | J460-01-2FCV-005 | Alarm | J460-01-2FCV-005 - Room J0.07 - J460-01-1ACU-004 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-005_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-005_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2212 | J270-06-1PNL-001 | J460-01-2FCV-005 | Measurement | J460-01-2FCV-005 - Room J0.07 - J460-01-1ACU-004 Heating Valve Control Forced Position | J460-01-2FCV-005_ForcePos | J460-01-2FCV-005_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2213 | J270-06-1PNL-001 | J460-01-2FCV-005 | Setting | J460-01-2FCV-005 - Room J0.07 - J460-01-1ACU-004 Heating Valve Control Forced Calibration | J460-01-2FCV-005_ForceCal | J460-01-2FCV-005_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2214 | J270-06-1PNL-001 | J460-01-2FCV-005 | Measurement | J460-01-2FCV-005 - Room J0.07 - J460-01-1ACU-004 Heating Valve Control Status | J460-01-2FCV-005_MotState | J460-01-2FCV-005_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2215 | J270-06-1PNL-001 | J460-01-2FCV-005 | Measurement | J460-01-2FCV-005 - Room J0.07 - J460-01-1ACU-004 Heating Valve Control Actual SP | J460-01-2FCV-005_ActSP | J460-01-2FCV-005_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2216 | J270-06-1PNL-001 | J460-01-2FCV-005 | Setting | J460-01-2FCV-005 - Room J0.07 - J460-01-1ACU-004 Heating Valve Control SP | J460-01-2FCV-005_SP | J460-01-2FCV-005_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2217 | J270-06-1PNL-001 | J460-01-2FCV-005 | Alarm | J460-01-2FCV-005 - Room J0.07 - J460-01-1ACU-004 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-005_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-005_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2218 | J270-06-1PNL-001 | J460-01-2FCV-005 | Alarm | J460-01-2FCV-005 - Room J0.07 - J460-01-1ACU-004 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-005_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-005_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2219 | J270-06-1PNL-001 | J460-01-2FCV-005 | Measurement | J460-01-2FCV-005 - Room J0.07 - J460-01-1ACU-004 Heating Valve Control Error Code | J460-01-2FCV-005_Err | J460-01-2FCV-005_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2220 | J270-06-1PNL-001 | J460-01-2FCV-006 | Alarm | J460-01-2FCV-006 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-006_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-006_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2221 | J270-06-1PNL-001 | J460-01-2FCV-006 | Measurement | J460-01-2FCV-006 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Position | J460-01-2FCV-006_ForcePos | J460-01-2FCV-006_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2222 | J270-06-1PNL-001 | J460-01-2FCV-006 | Setting | J460-01-2FCV-006 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Calibration | J460-01-2FCV-006_ForceCal | J460-01-2FCV-006_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2223 | J270-06-1PNL-001 | J460-01-2FCV-006 | Measurement | J460-01-2FCV-006 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Status | J460-01-2FCV-006_MotState | J460-01-2FCV-006_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2224 | J270-06-1PNL-001 | J460-01-2FCV-006 | Measurement | J460-01-2FCV-006 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Actual SP | J460-01-2FCV-006_ActSP | J460-01-2FCV-006_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2225 | J270-06-1PNL-001 | J460-01-2FCV-006 | Setting | J460-01-2FCV-006 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control SP | J460-01-2FCV-006_SP | J460-01-2FCV-006_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2226 | J270-06-1PNL-001 | J460-01-2FCV-006 | Alarm | J460-01-2FCV-006 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-006_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-006_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2227 | J270-06-1PNL-001 | J460-01-2FCV-006 | Alarm | J460-01-2FCV-006 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-006_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-006_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2228 | J270-06-1PNL-001 | J460-01-2FCV-006 | Measurement | J460-01-2FCV-006 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Error Code | J460-01-2FCV-006_Err | J460-01-2FCV-006_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2229 | J270-06-1PNL-001 | J460-01-2FCV-007 | Alarm | J460-01-2FCV-007 - Room J0.07 - J460-01-1ACU-002 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-007_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-007_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2230 | J270-06-1PNL-001 | J460-01-2FCV-007 | Measurement | J460-01-2FCV-007 - Room J0.07 - J460-01-1ACU-002 Cooling Valve Control Forced Position | J460-01-2FCV-007_ForcePos | J460-01-2FCV-007_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2231 | J270-06-1PNL-001 | J460-01-2FCV-007 | Setting | J460-01-2FCV-007 - Room J0.07 - J460-01-1ACU-002 Cooling Valve Control Forced Calibration | J460-01-2FCV-007_ForceCal | J460-01-2FCV-007_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2232 | J270-06-1PNL-001 | J460-01-2FCV-007 | Measurement | J460-01-2FCV-007 - Room J0.07 - J460-01-1ACU-002 Cooling Valve Control Status | J460-01-2FCV-007_MotState | J460-01-2FCV-007_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2233 | J270-06-1PNL-001 | J460-01-2FCV-007 | Measurement | J460-01-2FCV-007 - Room J0.07 - J460-01-1ACU-002 Cooling Valve Control Actual SP | J460-01-2FCV-007_ActSP | J460-01-2FCV-007_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2234 | J270-06-1PNL-001 | J460-01-2FCV-007 | Setting | J460-01-2FCV-007 - Room J0.07 - J460-01-1ACU-002 Cooling Valve Control SP | J460-01-2FCV-007_SP | J460-01-2FCV-007_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2235 | J270-06-1PNL-001 | J460-01-2FCV-007 | Alarm | J460-01-2FCV-007 - Room J0.07 - J460-01-1ACU-002 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-007_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-007_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2236 | J270-06-1PNL-001 | J460-01-2FCV-007 | Alarm | J460-01-2FCV-007 - Room J0.07 - J460-01-1ACU-002 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-007_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-007_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2237 | J270-06-1PNL-001 | J460-01-2FCV-007 | Measurement | J460-01-2FCV-007 - Room J0.07 - J460-01-1ACU-002 Cooling Valve Control Error Code | J460-01-2FCV-007_Err | J460-01-2FCV-007_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2238 | J270-06-1PNL-001 | J460-01-2FCV-008 | Alarm | J460-01-2FCV-008 - Room J0.07 - J460-01-1ACU-003 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-008_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-008_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2239 | J270-06-1PNL-001 | J460-01-2FCV-008 | Measurement | J460-01-2FCV-008 - Room J0.07 - J460-01-1ACU-003 Cooling Valve Control Forced Position | J460-01-2FCV-008_ForcePos | J460-01-2FCV-008_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2240 | J270-06-1PNL-001 | J460-01-2FCV-008 | Setting | J460-01-2FCV-008 - Room J0.07 - J460-01-1ACU-003 Cooling Valve Control Forced Calibration | J460-01-2FCV-008_ForceCal | J460-01-2FCV-008_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2241 | J270-06-1PNL-001 | J460-01-2FCV-008 | Measurement | J460-01-2FCV-008 - Room J0.07 - J460-01-1ACU-003 Cooling Valve Control Status | J460-01-2FCV-008_MotState | J460-01-2FCV-008_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2242 | J270-06-1PNL-001 | J460-01-2FCV-008 | Measurement | J460-01-2FCV-008 - Room J0.07 - J460-01-1ACU-003 Cooling Valve Control Actual SP | J460-01-2FCV-008_ActSP | J460-01-2FCV-008_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2243 | J270-06-1PNL-001 | J460-01-2FCV-008 | Setting | J460-01-2FCV-008 - Room J0.07 - J460-01-1ACU-003 Cooling Valve Control SP | J460-01-2FCV-008_SP | J460-01-2FCV-008_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2244 | J270-06-1PNL-001 | J460-01-2FCV-008 | Alarm | J460-01-2FCV-008 - Room J0.07 - J460-01-1ACU-003 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-008_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-008_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2245 | J270-06-1PNL-001 | J460-01-2FCV-008 | Alarm | J460-01-2FCV-008 - Room J0.07 - J460-01-1ACU-003 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-008_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-008_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2246 | J270-06-1PNL-001 | J460-01-2FCV-008 | Measurement | J460-01-2FCV-008 - Room J0.07 - J460-01-1ACU-003 Cooling Valve Control Error Code | J460-01-2FCV-008_Err | J460-01-2FCV-008_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2247 | J270-06-1PNL-001 | J460-01-2FCV-009 | Alarm | J460-01-2FCV-009 - Room J0.07 - J460-01-1ACU-004 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-009_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-009_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2248 | J270-06-1PNL-001 | J460-01-2FCV-009 | Measurement | J460-01-2FCV-009 - Room J0.07 - J460-01-1ACU-004 Cooling Valve Control Forced Position | J460-01-2FCV-009_ForcePos | J460-01-2FCV-009_ForcePos | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2249 | J270-06-1PNL-001 | J460-01-2FCV-009 | Setting | J460-01-2FCV-009 - Room J0.07 - J460-01-1ACU-004 Cooling Valve Control Forced Calibration | J460-01-2FCV-009_ForceCal | J460-01-2FCV-009_ForceCal | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2250 | J270-06-1PNL-001 | J460-01-2FCV-009 | Measurement | J460-01-2FCV-009 - Room J0.07 - J460-01-1ACU-004 Cooling Valve Control Status | J460-01-2FCV-009_MotState | J460-01-2FCV-009_MotState | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2251 | J270-06-1PNL-001 | J460-01-2FCV-009 | Measurement | J460-01-2FCV-009 - Room J0.07 - J460-01-1ACU-004 Cooling Valve Control Actual SP | J460-01-2FCV-009_ActSP | J460-01-2FCV-009_ActSP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2252 | J270-06-1PNL-001 | J460-01-2FCV-009 | Setting | J460-01-2FCV-009 - Room J0.07 - J460-01-1ACU-004 Cooling Valve Control SP | J460-01-2FCV-009_SP | J460-01-2FCV-009_SP | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2253 | J270-06-1PNL-001 | J460-01-2FCV-009 | Alarm | J460-01-2FCV-009 - Room J0.07 - J460-01-1ACU-004 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-009_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-009_FTOAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2254 | J270-06-1PNL-001 | J460-01-2FCV-009 | Alarm | J460-01-2FCV-009 - Room J0.07 - J460-01-1ACU-004 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-009_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-009_FTCAlm | 2 | M | - | bar: State 2 to State 64
1.0 | 2255 | J270-06-1PNL-001 | J460-01-2FCV-009 | Measurement | J460-01-2FCV-009 - Room J0.07 - J460-01-1ACU-004 Cooling Valve Control Error Code | J460-01-2FCV-009_Err | J460-01-2FCV-009_Err | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2256 | J270-06-1PNL-001 | J460-01-1VAV-001 | Alarm | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control - Communication Failure Alarm | J460-01-1VAV-001_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-001_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 2257 | J270-06-1PNL-001 | J460-01-1VAV-001 | Setting | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Flow Setpoint | J460-01-1VAV-001_SpRel | J460-01-1VAV-001_SpRel | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2258 | J270-06-1PNL-001 | J460-01-1VAV-001 | Measurement | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Relative Position | J460-01-1VAV-001_RelPos | J460-01-1VAV-001_RelPos | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2259 | J270-06-1PNL-001 | J460-01-1VAV-001 | Measurement | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-001_AbsFlw | J460-01-1VAV-001_AbsFlw | 0 | 650 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2260 | J270-06-1PNL-001 | J460-01-1VAV-001 | Alarm | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-001_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-617_Vnom_LASP | 2 | Y | - | bar: State 2 to State 64
2.0 | 2261 | J270-06-1PNL-001 | J460-01-1VAV-001 | Setting | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-001_AbsFlw_HASP | J460-01-1VAV-001_AbsFlw_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2262 | J270-06-1PNL-001 | J460-01-1VAV-001 | Alarm | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-001_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-001_AbsFlwLoAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 2263 | J270-06-1PNL-001 | J460-01-1VAV-001 | Setting | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-001_AbsFlw_LASP | J460-01-1VAV-001_AbsFlw_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2264 | J270-06-1PNL-001 | J460-01-1VAV-001 | Measurement | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-001_Vmin | J460-01-1VAV-001_Vmin | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2265 | J270-06-1PNL-001 | J460-01-1VAV-001 | Measurement | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Maximum Flow | J460-01-1VAV-001_Vmax | J460-01-1VAV-001_Vmax | 650 | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2266 | J270-06-1PNL-001 | J460-01-1VAV-001 | Measurement | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-001_Vnom | J460-01-1VAV-001_Vnom | 0 | 650 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2267 | J270-06-1PNL-001 | J460-01-1VAV-001 | Measurement | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Summary Status | J460-01-1VAV-001_SumSts | J460-01-1VAV-001_SumSts | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2268 | J270-06-1PNL-001 | J460-01-1VAV-001 | Alarm | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Summary Status Alarm | J460-01-1VAV-001_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-001_SumSts_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 2269 | J270-06-1PNL-001 | J460-01-1VAV-001 | Measurement | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Actuator Status | J460-01-1VAV-001_ActSts | J460-01-1VAV-001_ActSts | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2270 | J270-06-1PNL-001 | J460-01-1VAV-001 | Measurement | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Device Status | J460-01-1VAV-001_DevSts | J460-01-1VAV-001_DevSts | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2271 | J270-06-1PNL-001 | J460-01-1VAV-001 | Setting | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Device Override | J460-01-1VAV-001_Override | J460-01-1VAV-001_Override | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2272 | J270-06-1PNL-001 | J460-01-1VAV-002 | Alarm | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control - Communication Failure Alarm | J460-01-1VAV-002_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-002_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 2273 | J270-06-1PNL-001 | J460-01-1VAV-002 | Setting | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Flow Setpoint | J460-01-1VAV-002_SpRel | J460-01-1VAV-002_SpRel | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2274 | J270-06-1PNL-001 | J460-01-1VAV-002 | Measurement | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Relative Position | J460-01-1VAV-002_RelPos | J460-01-1VAV-002_RelPos | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2275 | J270-06-1PNL-001 | J460-01-1VAV-002 | Measurement | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-002_AbsFlw | J460-01-1VAV-002_AbsFlw | 0 | 650 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2276 | J270-06-1PNL-001 | J460-01-1VAV-002 | Alarm | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-002_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-001_VnomLoAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 2277 | J270-06-1PNL-001 | J460-01-1VAV-002 | Setting | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-002_AbsFlw_HASP | J460-01-1VAV-002_AbsFlw_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2278 | J270-06-1PNL-001 | J460-01-1VAV-002 | Alarm | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-002_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-002_AbsFlwLoAlm | 2 | Y | - | bar: State 2 to State 64
2.0 | 2279 | J270-06-1PNL-001 | J460-01-1VAV-002 | Setting | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Absolute Flow | J460-01-1VAV-002_AbsFlw_LASP | J460-01-1VAV-002_AbsFlw_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2280 | J270-06-1PNL-001 | J460-01-1VAV-002 | Measurement | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-002_Vmin | J460-01-1VAV-002_Vmin | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2281 | J270-06-1PNL-001 | J460-01-1VAV-002 | Measurement | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Maximum Flow | J460-01-1VAV-002_Vmax | J460-01-1VAV-002_Vmax | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2282 | J270-06-1PNL-001 | J460-01-1VAV-002 | Measurement | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-002_Vnom | J460-01-1VAV-002_Vnom | 0 | 650 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2283 | J270-06-1PNL-001 | J460-01-1VAV-002 | Measurement | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Summary Status | J460-01-1VAV-002_SumSts | J460-01-1VAV-002_SumSts | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2284 | J270-06-1PNL-001 | J460-01-1VAV-002 | Alarm | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Summary Status Alarm | J460-01-1VAV-002_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-002_SumSts_Alm | 1 | Y | - | bar: State 2 to State 64
2.0 | 2285 | J270-06-1PNL-001 | J460-01-1VAV-002 | Measurement | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Actuator Status | J460-01-1VAV-002_ActSts | J460-01-1VAV-002_ActSts | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2286 | J270-06-1PNL-001 | J460-01-1VAV-002 | Measurement | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Device Status | J460-01-1VAV-002_DevSts | J460-01-1VAV-002_DevSts | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2287 | J270-06-1PNL-001 | J460-01-1VAV-002 | Setting | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Device Override | J460-01-1VAV-002_Override | J460-01-1VAV-002_Override | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.1 | 2288 | J270-06-1PNL-001 | N/A | Setting | Common Calculated Office Temperature Setpoint | J460-06-2TT-CST_CmRaCalcTempSetpoint | J460-06-2TT-CST_CmRaCalcTempSetpoint | Calculated | Calculated | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2289 | J270-06-1PNL-001 | N/A | Setting | Common Calculated Office Temperature Setpoint (Point Parameter=Max) | J460-06-2TT-CST_CmRaCalcTempSetpoint_Max | J460-06-2TT-CST_CmRaCalcTempSetpoint_Max | 24 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2290 | J270-06-1PNL-001 | N/A | Setting | Common Calculated Office Temperature Setpoint (Point Parameter=Min) | J460-06-2TT-CST_CmRaCalcTempSetpoint_Min | J460-06-2TT-CST_CmRaCalcTempSetpoint_Min | - | 21 | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2291 | J270-06-1PNL-001 | N/A | Setting | Outside Air Temperature Setpoint (Point Parameter=Max) | J460-01-2UT-901_OATemp_Max | J460-01-2UT-901_OATemp_Max | - | 30 | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2292 | J270-06-1PNL-001 | N/A | Setting | Outside Air Temperature Setpoint (Point Parameter=Min) | J460-01-2UT-901_OATemp_Min | J460-01-2UT-901_OATemp_Min | -10 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2293 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | BMS Sixth Floor VAV Occupancy Run Timer | J270-06-3PLC-001_OccTimer | J270-06-3PLC-001_OccTimer | - | - | [11 empty] | - | - | - | - | 300 | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2294 | J270-08-1PNL-001 | J460-01-2UT-901 | Global | J460-01-2UT-901 - Outside Air Relative Humidity | - | G_J460-01-2UT-901_OARelHum | - | - | [11 empty] | - | - | - | - | - | - | - | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2295 | J270-08-1PNL-001 | J460-01-2UT-901 | Global | J460-01-2UT-901 - Outside Air Temperature | - | G_J460-01-2UT-901_OATemp | - | - | [11 empty] | - | - | - | - | - | - | - | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2296 | J460-01-1CP-809 | J460-01-2XA-802 | Global | J460-01-2XA-802 - Room J8.12 - UPS Alarm | - | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | G_J460-01-2XA-802_UPSAlm_Alm | 1 | Y | - | bar: State 2 to State 64
1.0 | 2297 | J270-06-1PNL-001 | N/A | Setting | BMS Sixth Floor Lab Temperature Night Mode Fixed Heating Setpoint | J270-06-3PLC-001_LabTempNgtModFixHtgSP | J270-06-3PLC-001_LabTempNgtModFixHtgSP | 17 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2298 | J270-06-1PNL-001 | N/A | Setting | BMS Sixth Floor Lab Temperature Night Mode Fixed Cooling Setpoint | J270-06-3PLC-001_LabTempNgtModFixClgSP | J270-06-3PLC-001_LabTempNgtModFixClgSP | 24 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2299 | J270-06-1PNL-001 | N/A | Setting | BMS Sixth/Ground Floor Office Temperature Night Mode Fixed Heating Setpoint | J270-06-3PLC-001_OffTempNgtModFixHtgSP | J270-06-3PLC-001_OffTempNgtModFixHtgSP | 17 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2300 | J270-06-1PNL-001 | N/A | Setting | BMS Sixth/Ground Floor Office Temperature Night Mode Fixed Cooling Setpoint | J270-06-3PLC-001_OffTempNgtModFixClgSP | J270-06-3PLC-001_OffTempNgtModFixClgSP | 24 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2301 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | BMS Sixth Floor Lab System Start/Stop | J270-06-3PLC-001_SixFlrLabSystemStart | J270-06-3PLC-001_SixFlrLabSystemStart | STOP | START | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2302 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | BMS Sixth Floor Office System Start/Stop | J270-06-3PLC-001_SixFlrOfficeSystemStart | J270-06-3PLC-001_SixFlrOfficeSystemStart | STOP | START | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2303 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | BMS Sixth Floor System Alarm Reset | J270-06-3PLC-001_SixFlrAlarmReset | J270-06-3PLC-001_SixFlrAlarmReset | OFF | RESET | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2304 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | J270-06-3PLC-001 - Common Alarm Delay Timer | J270-06-3PLC-001_CommonAlmDly | J270-06-3PLC-001_CommonAlmDly | - | - | [11 empty] | - | - | - | - | 5 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2305 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | J270-06-3PLC-001 - Common Calibration Mode Still Active Alarm Delay Timer | J270-06-3PLC-001_CALMDT | J270-06-3PLC-001_CALMDT | - | - | [11 empty] | - | - | - | - | 360 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2306 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | J270-06-3PLC-001 - Common Temp Alarm Delay Timer | J270-06-3PLC-001_TEMPALMDLY | J270-06-3PLC-001_TEMPALMDLY | - | - | [11 empty] | - | - | - | - | 300 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2307 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | J270-06-3PLC-001 - Common CO2 Alarm Delay Timer | J270-06-3PLC-001_CO2ALMDLY | J270-06-3PLC-001_CO2ALMDLY | - | - | [11 empty] | - | - | - | - | 300 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2308 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | J270-06-3PLC-001 - Common Press Alarm Delay Timer | J270-06-3PLC-001_PRESALMDLY | J270-06-3PLC-001_PRESALMDLY | - | - | [11 empty] | - | - | - | - | 600 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2309 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | J270-06-3PLC-001 - Common Hum Alarm Delay Timer | J270-06-3PLC-001_HUMDALMDLY | J270-06-3PLC-001_HUMDALMDLY | - | - | [11 empty] | - | - | - | - | 120 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2310 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | J270-06-3PLC-001 - Common Flow Alarm Delay Timer | J270-06-3PLC-001_FLOWALMDLY | J270-06-3PLC-001_FLOWALMDLY | - | - | [11 empty] | - | - | - | - | 600 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2311 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | J270-06-3PLC-001 - PID Enable Delay Timer | J270-06-3PLC-001_PIDEnblDly | J270-06-3PLC-001_PIDEnblDly | - | - | [11 empty] | - | - | 10 | - | 10 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2312 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | J270-06-3PLC-001 - Alarm Inhibit Delay Timer | J270-06-3PLC-001_AlmInbtDly | J270-06-3PLC-001_AlmInbtDly | - | - | [11 empty] | - | - | - | - | 1800 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2313 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | J270-06-3PLC-001 - Chilled Water Pump Disbale Delay | J270-06-3PLC-001_ChlWtrPmpDisOnDly | J270-06-3PLC-001_ChlWtrPmpDisOnDly | - | - | [11 empty] | - | - | - | - | 60 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2314 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | J270-06-3PLC-001 - Utility Failure Delay Timer | J270-06-3PLC-001_UtlFailDly | J270-06-3PLC-001_UtlFailDly | - | - | [11 empty] | - | - | - | - | 180 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2315 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | BMS Sixth/Ground Floor Valve Fail to Open Alarm Delay Timer | J270-06-3PLC-001_VlvFailtoOpenAlmDly | J270-06-3PLC-001_VlvFailtoOpenAlmDly | - | - | [11 empty] | - | - | - | - | 120 | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2316 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | BMS Sixth/Ground Floor Valve Fail to Close Alarm Delay Timer | J270-06-3PLC-001_VlvFailtoclsAlmDly | J270-06-3PLC-001_VlvFailtoclsAlmDly | - | - | [11 empty] | - | - | - | - | 120 | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2317 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | BMS Sixth/Ground Floor FCU Fail to Start Alarm Delay Timer | J270-06-3PLC-001_FCUFailtoStartAlmDly | J270-06-3PLC-001_FCUFailtoStartAlmDly | - | - | [11 empty] | - | - | - | - | 60 | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2318 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | BMS Sixth/Ground Floor FCU Fail to Stop Alarm Delay Timer | J270-06-3PLC-001_FCUFailtoStopAlmDly | J270-06-3PLC-001_FCUFailtoStopAlmDly | - | - | [11 empty] | - | - | - | - | 60 | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2319 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | BMS Sixth/Ground Floor Pump Fail to Start Alarm Delay Timer | J270-06-3PLC-001_PmpFailtoStartAlmDly | J270-06-3PLC-001_PmpFailtoStartAlmDly | - | - | [11 empty] | - | - | - | - | 60 | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2320 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | BMS Sixth/Ground Floor Pump Fail to Stop Alarm Delay Timer | J270-06-3PLC-001_PmpFailtoStopAlmDly | J270-06-3PLC-001_PmpFailtoStopAlmDly | - | - | [11 empty] | - | - | - | - | 60 | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2321 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | J270-06-3PLC-001 - Room Mode Ground Floor Office | J270-06-3PLC-001_RmMode_GrdFlr_Office | J270-06-3PLC-001_RmMode_GrdFlr_Office | NGHTMODE | DAYMODE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2322 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | J270-06-3PLC-001 - Room Mode Sixth Floor Labs | J270-06-3PLC-001_RmMode_SixFlr_Labs | J270-06-3PLC-001_RmMode_SixFlr_Labs | NGHTMODE | DAYMODE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2323 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | J270-06-3PLC-001 - Room Mode Sixth Floor Offices | J270-06-3PLC-001_RmMode_SixFlr_Offices | J270-06-3PLC-001_RmMode_SixFlr_Offices | NGHTMODE | DAYMODE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2324 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Central Time Program for Lab | J270-06-3PLC-001_CTP_MD_LAB | G_J270-06-3PLC-001_CTP_MD_LAB | NGHTMODE | DAYMODE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2325 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Central Time Program for Office | J270-06-3PLC-001_CTP_MD_OFC | G_J270-06-3PLC-001_CTP_MD_OFC | NGHTMODE | DAYMODE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2326 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | J270-06-3PLC-001 - Periodic Pump Pulse Time Setpoint | J270-06-3PLC-001_PerPmpPulseTimeSP | J270-06-3PLC-001_PerPmpPulseTimeSP | - | - | [11 empty] | - | - | - | - | 300 | - | 220 | - | Hr | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2327 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | J270-06-3PLC-001 - Periodic Pump Pulse Enable | J270-06-3PLC-001_PerPmpPulseEna | J270-06-3PLC-001_PerPmpPulseEna | DISABLE | ENABLE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2328 | J270-06-1PNL-001 | N/A | Global | Common Calculated Office Temperature Setpoint | - | G_J460-06-2TT-CST_CmRaCalcTempSetpoint | Calculated | Calculated | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2329 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | BMS Sixth Floor VAV Occupancy Run Timer | - | G_J270-06-3PLC-001_OccTimer | - | - | [11 empty] | - | - | - | - | 300 | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2330 | J270-06-1PNL-001 | N/A | Global | BMS Sixth Floor Lab Temperature Night Mode Fixed Heating Setpoint | - | G_J270-06-3PLC-001_LabTempNgtModFixHtgSP | 17 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2331 | J270-06-1PNL-001 | N/A | Global | BMS Sixth Floor Lab Temperature Night Mode Fixed Cooling Setpoint | - | G_J270-06-3PLC-001_LabTempNgtModFixClgSP | 24 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2332 | J270-06-1PNL-001 | N/A | Global | BMS Sixth/Ground Floor Office Temperature Night Mode Fixed Heating Setpoint | - | G_J270-06-3PLC-001_OffTempNgtModFixHtgSP | 17 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2333 | J270-06-1PNL-001 | N/A | Global | BMS Sixth/Ground Floor Office Temperature Night Mode Fixed Cooling Setpoint | - | G_J270-06-3PLC-001_OffTempNgtModFixClgSP | 24 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2334 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | BMS Sixth Floor System Start/Stop | - | G_J270-06-3PLC-001_SixFlrSystemStart | STOP | START | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2335 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | BMS Ground Floor System Start/Stop | - | G_J270-06-3PLC-001_GrndFlrSystemStart | STOP | START | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2336 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | BMS Sixth Floor System Alarm Reset | - | G_J270-06-3PLC-001_SixFlrAlarmReset | OFF | RESET | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2337 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | BMS Ground Floor System Alarm Reset | - | G_J270-06-3PLC-001_GrndFlrAlarmReset | OFF | RESET | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2338 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Common Alarm Delay Timer | - | G_J270-06-3PLC-001_CommonAlmDly | - | - | [11 empty] | - | - | - | - | 5 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2339 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Common Calibration Mode Still Active Alarm Delay Timer | - | G_J270-06-3PLC-001_CALMDT | - | - | [11 empty] | - | - | - | - | 360 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2340 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Common Temp Alarm Delay Timer | - | G_J270-06-3PLC-001_TEMPALMDLY | - | - | [11 empty] | - | - | - | - | 300 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2341 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Common CO2 Alarm Delay Timer | - | G_J270-06-3PLC-001_CO2ALMDLY | - | - | [11 empty] | - | - | - | - | 300 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2342 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Common Press Alarm Delay Timer | - | G_J270-06-3PLC-001_PRESALMDLY | - | - | [11 empty] | - | - | - | - | 600 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2343 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Common Hum Alarm Delay Timer | - | G_J270-06-3PLC-001_HUMDALMDLY | - | - | [11 empty] | - | - | - | - | 120 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2344 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Common Flow Alarm Delay Timer | - | G_J270-06-3PLC-001_FLOWALMDLY | - | - | [11 empty] | - | - | - | - | 600 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2345 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - PID Enable Delay Timer | - | G_J270-06-3PLC-001_PIDEnblDly | - | - | [11 empty] | - | - | - | - | 10 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2346 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Alarm Inhibit Delay Timer | - | G_J270-06-3PLC-001_AlmInbtDly | - | - | [11 empty] | - | - | - | - | 1800 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2347 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Chilled Water Pump Disbale Delay | - | G_J270-06-3PLC-001_ChlWtrPmpDisOnDly | - | - | [11 empty] | - | - | - | - | 60 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2348 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Utility Failure Delay Timer | - | G_J270-06-3PLC-001_UtlFailDly | - | - | [11 empty] | - | - | - | - | 180 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2349 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | BMS Sixth/Ground Floor Valve Fail to Open Alarm Delay Timer | - | G_J270-06-3PLC-001_VlvFailtoOpenAlmDly | - | - | [11 empty] | - | - | - | - | 120 | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2350 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | BMS Sixth/Ground Floor Valve Fail to Close Alarm Delay Timer | - | G_J270-06-3PLC-001_VlvFailtoclsAlmDly | - | - | [11 empty] | - | - | - | - | 120 | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2351 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | BMS Sixth/Ground Floor FCU Fail to Start Alarm Delay Timer | - | G_J270-06-3PLC-001_FCUFailtoStartAlmDly | - | - | [11 empty] | - | - | - | - | 60 | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2352 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | BMS Sixth/Ground Floor FCU Fail to Stop Alarm Delay Timer | - | G_J270-06-3PLC-001_FCUFailtoStopAlmDly | - | - | [11 empty] | - | - | - | - | 60 | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2353 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | BMS Sixth/Ground Floor Pump Fail to Start Alarm Delay Timer | - | G_J270-06-3PLC-001_PmpFailtoStartAlmDly | - | - | [11 empty] | - | - | - | - | 60 | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2354 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | BMS Sixth/Ground Floor Pump Fail to Stop Alarm Delay Timer | - | G_J270-06-3PLC-001_PmpFailtoStopAlmDly | - | - | [11 empty] | - | - | - | - | 60 | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2355 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Room Mode Ground Floor Labs | - | G_J270-06-3PLC-001_RmMode_GrndFlr_Labs | NGHTMODE | DAYMODE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2356 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Room Mode Sixth Floor Labs | - | G_J270-06-3PLC-001_RmMode_SixFlr_Labs | NGHTMODE | DAYMODE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2357 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Room Mode Sixth Floor Offices | - | G_J270-06-3PLC-001_RmMode_SixFlr_Offices | NGHTMODE | DAYMODE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2358 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Periodic Pump Pulse Time | - | G_J270-06-3PLC-001_PerPmpPulseTime | - | - | [11 empty] | - | - | - | - | 300 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2359 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Periodic Pump Pulse Enable | - | G_J270-06-3PLC-001_PerPmpPulseEna | DISABLE | ENABLE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2360 | J270-06-1PNL-001 | J460-01-1VAV-613 | Setting | J270-06-3PLC-001 - Room VAV Supply Air Flow Control Minimum Open Flow Setpoint | J270-06-3PLC-001_VAVCmdVocc | J270-06-3PLC-001_VAVCmdVocc | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2361 | J270-06-1PNL-001 | J270-06-3PLC-002 | Global | J270-06-3PLC-002 - Central Time Program for Office | - | G_J270-06-3PLC-002_CTP_MD_OFC | 0 | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2362 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | J270-06-3PLC-001 - Periodic Pump Pulse Duration | J270-06-3PLC-001_PdcPmpPls_Duration | J270-06-3PLC-001_PdcPmpPls_Duration | 0 | 60 | [11 empty] | - | - | - | - | - | - | 220 | - | Min | HMI Station | - | 4 | - | bar: State 2 to State 64
Deleted points
| 2328 | J270-06-1PNL-001 | J460-01-2FCV-643 | Measurement | J460-01-2FCV-643 - Chilled Water Valve - Speed | J460-01-2FCV-643_Spd | J460-01-2FCV-643_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2329 | J270-06-1PNL-001 | J460-01-1VAV-601 | Alarm | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-601_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-601_VminHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2330 | J270-06-1PNL-001 | J460-01-1VAV-601 | Setting | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Minimum Flow | J460-01-1VAV-601_Vmin_HASP | J460-01-1VAV-601_Vmin_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2331 | J270-06-1PNL-001 | J460-01-1VAV-601 | Alarm | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-601_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-601_VminLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2332 | J270-06-1PNL-001 | J460-01-1VAV-601 | Setting | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Minimum Flow | J460-01-1VAV-601_Vmin_LASP | J460-01-1VAV-601_Vmin_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2333 | J270-06-1PNL-001 | J460-01-1VAV-601 | Alarm | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-601_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-601_VnomHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2334 | J270-06-1PNL-001 | J460-01-1VAV-601 | Setting | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Nominal Flow | J460-01-1VAV-601_Vnom_HASP | J460-01-1VAV-601_Vnom_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2335 | J270-06-1PNL-001 | J460-01-1VAV-601 | Alarm | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-601_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-601_VnomLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2336 | J270-06-1PNL-001 | J460-01-1VAV-601 | Setting | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Nominal Flow | J460-01-1VAV-601_Vnom_LASP | J460-01-1VAV-601_Vnom_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2337 | J270-06-1PNL-001 | J460-01-1VAV-602 | Alarm | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-602_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-602_VminHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2338 | J270-06-1PNL-001 | J460-01-1VAV-602 | Setting | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Minimum Flow | J460-01-1VAV-602_Vmin_HASP | J460-01-1VAV-602_Vmin_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2339 | J270-06-1PNL-001 | J460-01-1VAV-602 | Alarm | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-602_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-602_VminLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2340 | J270-06-1PNL-001 | J460-01-1VAV-602 | Setting | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Minimum Flow | J460-01-1VAV-602_Vmin_LASP | J460-01-1VAV-602_Vmin_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2341 | J270-06-1PNL-001 | J460-01-1VAV-602 | Alarm | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-602_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-602_VnomHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2342 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Chilled Water Pump Disbale Delay | - | G_J270-06-3PLC-001_ChlWtrPmpDisOnDly | - | - | [11 empty] | - | - | - | - | 60 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2342 | J270-06-1PNL-001 | J460-01-1VAV-602 | Setting | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Nominal Flow | J460-01-1VAV-602_Vnom_HASP | J460-01-1VAV-602_Vnom_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2343 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Utility Failure Delay Timer | - | G_J270-06-3PLC-001_UtlFailDly | - | - | [11 empty] | - | - | - | - | 180 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2343 | J270-06-1PNL-001 | J460-01-1VAV-602 | Alarm | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-602_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-602_VnomLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2344 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | BMS Sixth/Ground Floor Valve Fail to Open Alarm Delay Timer | - | G_J270-06-3PLC-001_VlvFailtoOpenAlmDly | - | - | [11 empty] | - | - | - | - | 120 | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2344 | J270-06-1PNL-001 | J460-01-1VAV-602 | Setting | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Nominal Flow | J460-01-1VAV-602_Vnom_LASP | J460-01-1VAV-602_Vnom_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2345 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | BMS Sixth/Ground Floor Valve Fail to Close Alarm Delay Timer | - | G_J270-06-3PLC-001_VlvFailtoclsAlmDly | - | - | [11 empty] | - | - | - | - | 120 | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2345 | J270-06-1PNL-001 | J460-01-1VAV-603 | Alarm | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-603_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-603_VminHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2346 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | BMS Sixth/Ground Floor FCU Fail to Start Alarm Delay Timer | - | G_J270-06-3PLC-001_FCUFailtoStartAlmDly | - | - | [11 empty] | - | - | - | - | 60 | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2346 | J270-06-1PNL-001 | J460-01-1VAV-603 | Setting | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-603_Vmin_HASP | J460-01-1VAV-603_Vmin_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2347 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | BMS Sixth/Ground Floor FCU Fail to Stop Alarm Delay Timer | - | G_J270-06-3PLC-001_FCUFailtoStopAlmDly | - | - | [11 empty] | - | - | - | - | 60 | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2347 | J270-06-1PNL-001 | J460-01-1VAV-603 | Alarm | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-603_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-603_VminLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2348 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | BMS Sixth/Ground Floor Pump Fail to Start Alarm Delay Timer | - | G_J270-06-3PLC-001_PmpFailtoStartAlmDly | - | - | [11 empty] | - | - | - | - | 60 | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2348 | J270-06-1PNL-001 | J460-01-1VAV-603 | Setting | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-603_Vmin_LASP | J460-01-1VAV-603_Vmin_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2349 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | BMS Sixth/Ground Floor Pump Fail to Stop Alarm Delay Timer | - | G_J270-06-3PLC-001_PmpFailtoStopAlmDly | - | - | [11 empty] | - | - | - | - | 60 | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2349 | J270-06-1PNL-001 | J460-01-1VAV-603 | Alarm | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-603_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-603_VnomHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2350 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Room Mode Ground Floor Labs | - | G_J270-06-3PLC-001_RmMode_GrndFlr_Labs | NGHTMODE | DAYMODE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2350 | J270-06-1PNL-001 | J460-01-1VAV-603 | Setting | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-603_Vnom_HASP | J460-01-1VAV-603_Vnom_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2351 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Room Mode Sixth Floor Labs | - | G_J270-06-3PLC-001_RmMode_SixFlr_Labs | NGHTMODE | DAYMODE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2351 | J270-06-1PNL-001 | J460-01-1VAV-603 | Alarm | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-603_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-603_VnomLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2352 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Room Mode Sixth Floor Offices | - | G_J270-06-3PLC-001_RmMode_SixFlr_Offices | NGHTMODE | DAYMODE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2352 | J270-06-1PNL-001 | J460-01-1VAV-603 | Setting | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-603_Vnom_LASP | J460-01-1VAV-603_Vnom_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2353 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Periodic Pump Pulse Time | - | G_J270-06-3PLC-001_PerPmpPulseTime | - | - | [11 empty] | - | - | - | - | 300 | - | 220 | - | Sec | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2353 | J270-06-1PNL-001 | J460-01-1VAV-603 | Setting | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Proportional Band | J460-01-1VAV-603_SupAirFlow_Set_P | J460-01-1VAV-603_SupAirFlow_Set_P | 2 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2353 | J270-06-1PNL-001 | J270-06-3PLC-002 | Global | J270-06-3PLC-002 - Central Time Program for Lab | - | G_J270-06-3PLC-002_CTP_MD_LAB | 0 | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2354 | J270-06-1PNL-001 | J270-06-3PLC-001 | Global | J270-06-3PLC-001 - Periodic Pump Pulse Enable | - | G_J270-06-3PLC-001_PerPmpPulseEna | DISABLE | ENABLE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2354 | J270-06-1PNL-001 | J460-01-1VAV-603 | Setting | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Integral Time | J460-01-1VAV-603_SupAirFlow_Set_I | J460-01-1VAV-603_SupAirFlow_Set_I | 60 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2354 | J270-06-1PNL-001 | J270-06-3PLC-002 | Global | J270-06-3PLC-002 - Central Time Program for Office | - | G_J270-06-3PLC-002_CTP_MD_OFC | 0 | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2355 | J270-06-1PNL-001 | J460-01-1VAV-603 | Setting | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Derivative Time | J460-01-1VAV-603_SupAirFlow_Set_D | J460-01-1VAV-603_SupAirFlow_Set_D | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2356 | J270-06-1PNL-001 | J460-01-1VAV-604 | Alarm | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-604_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-604_VminHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2357 | J270-06-1PNL-001 | J460-01-1VAV-604 | Setting | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Minimum Flow | J460-01-1VAV-604_Vmin_HASP | J460-01-1VAV-604_Vmin_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2358 | J270-06-1PNL-001 | J460-01-1VAV-604 | Alarm | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-604_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-604_VminLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2359 | J270-06-1PNL-001 | J460-01-1VAV-604 | Setting | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Minimum Flow | J460-01-1VAV-604_Vmin_LASP | J460-01-1VAV-604_Vmin_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2360 | J270-06-1PNL-001 | J460-01-1VAV-604 | Alarm | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-604_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-604_VnomHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2361 | J270-06-1PNL-001 | J460-01-1VAV-604 | Setting | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Nominal Flow | J460-01-1VAV-604_Vnom_HASP | J460-01-1VAV-604_Vnom_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2362 | J270-06-1PNL-001 | J460-01-1VAV-604 | Alarm | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-604_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-604_VnomLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2363 | J270-06-1PNL-001 | J460-01-1VAV-604 | Setting | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Nominal Flow | J460-01-1VAV-604_Vnom_LASP | J460-01-1VAV-604_Vnom_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2364 | J270-06-1PNL-001 | J460-01-1VAV-605 | Alarm | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-605_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-605_VminHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2365 | J270-06-1PNL-001 | J460-01-1VAV-605 | Setting | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-605_Vmin_HASP | J460-01-1VAV-605_Vmin_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2366 | J270-06-1PNL-001 | J460-01-1VAV-605 | Alarm | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-605_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-605_VminLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2367 | J270-06-1PNL-001 | J460-01-1VAV-605 | Setting | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-605_Vmin_LASP | J460-01-1VAV-605_Vmin_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2368 | J270-06-1PNL-001 | J460-01-1VAV-605 | Alarm | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-605_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-605_VnomHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2369 | J270-06-1PNL-001 | J460-01-1VAV-605 | Setting | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-605_Vnom_HASP | J460-01-1VAV-605_Vnom_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2370 | J270-06-1PNL-001 | J460-01-1VAV-605 | Alarm | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-605_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-605_VnomLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2371 | J270-06-1PNL-001 | J460-01-1VAV-605 | Setting | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-605_Vnom_LASP | J460-01-1VAV-605_Vnom_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2372 | J270-06-1PNL-001 | J460-01-1VAV-605 | Setting | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Proportional Band | J460-01-1VAV-605_SupAirFlow_Set_P | J460-01-1VAV-605_SupAirFlow_Set_P | 2 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2373 | J270-06-1PNL-001 | J460-01-1VAV-605 | Setting | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Integral Time | J460-01-1VAV-605_SupAirFlow_Set_I | J460-01-1VAV-605_SupAirFlow_Set_I | 60 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2374 | J270-06-1PNL-001 | J460-01-1VAV-605 | Setting | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Derivative Time | J460-01-1VAV-605_SupAirFlow_Set_D | J460-01-1VAV-605_SupAirFlow_Set_D | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2375 | J270-06-1PNL-001 | J460-01-1VAV-606 | Alarm | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-606_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-606_VminHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2376 | J270-06-1PNL-001 | J460-01-1VAV-606 | Setting | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-606_Vmin_HASP | J460-01-1VAV-606_Vmin_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2377 | J270-06-1PNL-001 | J460-01-1VAV-606 | Alarm | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-606_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-606_VminLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2378 | J270-06-1PNL-001 | J460-01-1VAV-606 | Setting | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-606_Vmin_LASP | J460-01-1VAV-606_Vmin_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2379 | J270-06-1PNL-001 | J460-01-1VAV-606 | Alarm | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-606_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-606_VnomHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2380 | J270-06-1PNL-001 | J460-01-1VAV-606 | Setting | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-606_Vnom_HASP | J460-01-1VAV-606_Vnom_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2381 | J270-06-1PNL-001 | J460-01-1VAV-606 | Alarm | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-606_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-606_VnomLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2382 | J270-06-1PNL-001 | J460-01-1VAV-606 | Setting | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-606_Vnom_LASP | J460-01-1VAV-606_Vnom_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2383 | J270-06-1PNL-001 | J460-01-1VAV-608 | Alarm | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-608_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-608_VminHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2384 | J270-06-1PNL-001 | J460-01-1VAV-608 | Setting | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-608_Vmin_HASP | J460-01-1VAV-608_Vmin_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2385 | J270-06-1PNL-001 | J460-01-1VAV-608 | Alarm | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-608_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-608_VminLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2386 | J270-06-1PNL-001 | J460-01-1VAV-608 | Setting | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-608_Vmin_LASP | J460-01-1VAV-608_Vmin_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2387 | J270-06-1PNL-001 | J460-01-1VAV-608 | Alarm | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-608_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-608_VnomHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2388 | J270-06-1PNL-001 | J460-01-1VAV-608 | Setting | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-608_Vnom_HASP | J460-01-1VAV-608_Vnom_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2389 | J270-06-1PNL-001 | J460-01-1VAV-608 | Alarm | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-608_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-608_VnomLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2390 | J270-06-1PNL-001 | J460-01-1VAV-608 | Setting | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-608_Vnom_LASP | J460-01-1VAV-608_Vnom_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2391 | J270-06-1PNL-001 | J460-01-1VAV-607 | Alarm | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-607_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-607_VminHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2392 | J270-06-1PNL-001 | J460-01-1VAV-607 | Setting | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Minimum Flow | J460-01-1VAV-607_Vmin_HASP | J460-01-1VAV-607_Vmin_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2393 | J270-06-1PNL-001 | J460-01-1VAV-607 | Alarm | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-607_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-607_VminLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2394 | J270-06-1PNL-001 | J460-01-1VAV-607 | Setting | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Minimum Flow | J460-01-1VAV-607_Vmin_LASP | J460-01-1VAV-607_Vmin_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2395 | J270-06-1PNL-001 | J460-01-1VAV-607 | Alarm | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-607_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-607_VnomHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2396 | J270-06-1PNL-001 | J460-01-1VAV-607 | Setting | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Nominal Flow | J460-01-1VAV-607_Vnom_HASP | J460-01-1VAV-607_Vnom_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2397 | J270-06-1PNL-001 | J460-01-1VAV-607 | Alarm | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-607_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-607_VnomLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2398 | J270-06-1PNL-001 | J460-01-1VAV-607 | Setting | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Nominal Flow | J460-01-1VAV-607_Vnom_LASP | J460-01-1VAV-607_Vnom_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2399 | J270-06-1PNL-001 | J460-01-1VAV-609 | Alarm | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-609_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-609_VminHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2400 | J270-06-1PNL-001 | J460-01-1VAV-609 | Setting | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-609_Vmin_HASP | J460-01-1VAV-609_Vmin_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2401 | J270-06-1PNL-001 | J460-01-1VAV-609 | Alarm | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-609_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-609_VminLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2402 | J270-06-1PNL-001 | J460-01-1VAV-609 | Setting | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-609_Vmin_LASP | J460-01-1VAV-609_Vmin_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2403 | J270-06-1PNL-001 | J460-01-1VAV-609 | Alarm | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-609_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-609_VnomHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2404 | J270-06-1PNL-001 | J460-01-1VAV-609 | Setting | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-609_Vnom_HASP | J460-01-1VAV-609_Vnom_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2405 | J270-06-1PNL-001 | J460-01-1VAV-609 | Alarm | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-609_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-609_VnomLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2406 | J270-06-1PNL-001 | J460-01-1VAV-609 | Setting | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-609_Vnom_LASP | J460-01-1VAV-609_Vnom_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2407 | J270-06-1PNL-001 | J460-01-1VAV-609 | Setting | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Proportional Band | J460-01-1VAV-609_SupAirFlow_Set_P | J460-01-1VAV-609_SupAirFlow_Set_P | 2 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2408 | J270-06-1PNL-001 | J460-01-1VAV-609 | Setting | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Integral Time | J460-01-1VAV-609_SupAirFlow_Set_I | J460-01-1VAV-609_SupAirFlow_Set_I | 60 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2409 | J270-06-1PNL-001 | J460-01-1VAV-609 | Setting | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Derivative Time | J460-01-1VAV-609_SupAirFlow_Set_D | J460-01-1VAV-609_SupAirFlow_Set_D | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2410 | J270-06-1PNL-001 | J460-01-1VAV-610 | Alarm | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-610_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-610_VminHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2410 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | J460-01-1PMP-601 - Pump Runtime Setpoint | J460-01-1PMP-601_PumpRunTime | J460-01-1PMP-601_PumpRunTime | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | hr | HMI/Station | - | 4 | - | bar: State 2 to State 64
3 | 2411 | J270-06-1PNL-001 | J460-01-1VAV-610 | Setting | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Minimum Flow | J460-01-1VAV-610_Vmin_HASP | J460-01-1VAV-610_Vmin_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2411 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | J460-01-1PMP-601 - Periodic Pump Pulse Duration | J460-01-1PMP-601_PdcPmpPls_Duration | J460-01-1PMP-601_PdcPmpPls_Duration | 0 | 60 | [11 empty] | - | - | - | - | - | - | 220 | - | Min | HMI Station | - | 4 | - | bar: State 2 to State 64
3 | 2412 | J270-06-1PNL-001 | J460-01-1VAV-610 | Alarm | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-610_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-610_VminLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2412 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | J460-01-1PMP-001 - Pump Runtime Setpoint | J460-01-1PMP-001_PumpRunTime | J460-01-1PMP-001_PumpRunTime | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | hr | HMI/Station | - | 4 | - | bar: State 2 to State 64
3 | 2413 | J270-06-1PNL-001 | J460-01-1VAV-610 | Setting | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Minimum Flow | J460-01-1VAV-610_Vmin_LASP | J460-01-1VAV-610_Vmin_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2413 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | J460-01-1PMP-001 - Periodic Pump Pulse Duration | J460-01-1PMP-001_PdcPmpPls_Duration | J460-01-1PMP-001_PdcPmpPls_Duration | 0 | 60 | [11 empty] | - | - | - | - | - | - | 220 | - | Min | HMI Station | - | 4 | - | bar: State 2 to State 64
3 | 2414 | J270-06-1PNL-001 | J460-01-1VAV-610 | Alarm | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-610_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-610_VnomHiAlm | 2 | Y | - | bar: State 2 to State 64
3 | 2415 | J270-06-1PNL-001 | J460-01-1VAV-610 | Setting | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Nominal Flow | J460-01-1VAV-610_Vnom_HASP | J460-01-1VAV-610_Vnom_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
3 | 2416 | J270-06-1PNL-001 | J460-01-1VAV-610 | Alarm | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-610_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-610_VnomLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2417 | J270-06-1PNL-001 | J460-01-1VAV-610 | Setting | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Nominal Flow | J460-01-1VAV-610_Vnom_LASP | J460-01-1VAV-610_Vnom_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2418 | J270-06-1PNL-001 | J460-01-1VAV-611 | Alarm | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-611_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-611_VminHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2419 | J270-06-1PNL-001 | J460-01-1VAV-611 | Setting | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-611_Vmin_HASP | J460-01-1VAV-611_Vmin_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2420 | J270-06-1PNL-001 | J460-01-1VAV-611 | Alarm | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-611_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-611_VminLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2421 | J270-06-1PNL-001 | J460-01-1VAV-611 | Setting | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-611_Vmin_LASP | J460-01-1VAV-611_Vmin_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2422 | J270-06-1PNL-001 | J460-01-1VAV-611 | Alarm | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-611_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-611_VnomHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2423 | J270-06-1PNL-001 | J460-01-1VAV-611 | Setting | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-611_Vnom_HASP | J460-01-1VAV-611_Vnom_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2424 | J270-06-1PNL-001 | J460-01-1VAV-611 | Alarm | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-611_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-611_VnomLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2425 | J270-06-1PNL-001 | J460-01-1VAV-611 | Setting | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-611_Vnom_LASP | J460-01-1VAV-611_Vnom_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2426 | J270-06-1PNL-001 | J460-01-1VAV-613 | Alarm | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-613_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-613_VminHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2427 | J270-06-1PNL-001 | J460-01-1VAV-613 | Setting | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-613_Vmin_HASP | J460-01-1VAV-613_Vmin_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2428 | J270-06-1PNL-001 | J460-01-1VAV-613 | Alarm | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-613_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-613_VminLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2429 | J270-06-1PNL-001 | J460-01-1VAV-613 | Setting | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-613_Vmin_LASP | J460-01-1VAV-613_Vmin_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2430 | J270-06-1PNL-001 | J460-01-1VAV-613 | Alarm | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-613_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-613_VnomHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2431 | J270-06-1PNL-001 | J460-01-1VAV-613 | Setting | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-613_Vnom_HASP | J460-01-1VAV-613_Vnom_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2432 | J270-06-1PNL-001 | J460-01-1VAV-613 | Alarm | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-613_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-613_VnomLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2433 | J270-06-1PNL-001 | J460-01-1VAV-613 | Setting | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-613_Vnom_LASP | J460-01-1VAV-613_Vnom_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2434 | J270-06-1PNL-001 | J460-01-1VAV-613 | Setting | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Proportional Band | J460-01-1VAV-613_SupAirFlow_Set_P | J460-01-1VAV-613_SupAirFlow_Set_P | 2 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2435 | J270-06-1PNL-001 | J460-01-1VAV-613 | Setting | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Integral Time | J460-01-1VAV-613_SupAirFlow_Set_I | J460-01-1VAV-613_SupAirFlow_Set_I | 60 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2436 | J270-06-1PNL-001 | J460-01-1VAV-613 | Setting | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Derivative Time | J460-01-1VAV-613_SupAirFlow_Set_D | J460-01-1VAV-613_SupAirFlow_Set_D | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2437 | J270-06-1PNL-001 | J460-01-1VAV-612 | Alarm | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-612_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-612_VminHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2438 | J270-06-1PNL-001 | J460-01-1VAV-612 | Setting | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Minimum Flow | J460-01-1VAV-612_Vmin_HASP | J460-01-1VAV-612_Vmin_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2439 | J270-06-1PNL-001 | J460-01-1VAV-612 | Alarm | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-612_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-612_VminLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2440 | J270-06-1PNL-001 | J460-01-1VAV-612 | Setting | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Minimum Flow | J460-01-1VAV-612_Vmin_LASP | J460-01-1VAV-612_Vmin_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2441 | J270-06-1PNL-001 | J460-01-1VAV-612 | Alarm | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-612_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-612_VnomHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2442 | J270-06-1PNL-001 | J460-01-1VAV-612 | Setting | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Nominal Flow | J460-01-1VAV-612_Vnom_HASP | J460-01-1VAV-612_Vnom_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2443 | J270-06-1PNL-001 | J460-01-1VAV-612 | Alarm | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-612_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-612_VnomLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2444 | J270-06-1PNL-001 | J460-01-1VAV-612 | Setting | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Nominal Flow | J460-01-1VAV-612_Vnom_LASP | J460-01-1VAV-612_Vnom_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2445 | J270-06-1PNL-001 | J460-01-1VAV-615 | Alarm | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-615_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-615_VminHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2446 | J270-06-1PNL-001 | J460-01-1VAV-615 | Setting | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-615_Vmin_HASP | J460-01-1VAV-615_Vmin_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2447 | J270-06-1PNL-001 | J460-01-1VAV-615 | Alarm | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-615_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-615_VminLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2448 | J270-06-1PNL-001 | J460-01-1VAV-615 | Setting | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-615_Vmin_LASP | J460-01-1VAV-615_Vmin_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2449 | J270-06-1PNL-001 | J460-01-1VAV-615 | Alarm | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-615_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-615_VnomHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2450 | J270-06-1PNL-001 | J460-01-1VAV-615 | Setting | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-615_Vnom_HASP | J460-01-1VAV-615_Vnom_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2451 | J270-06-1PNL-001 | J460-01-1VAV-615 | Alarm | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-615_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-615_VnomLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2452 | J270-06-1PNL-001 | J460-01-1VAV-615 | Setting | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-615_Vnom_LASP | J460-01-1VAV-615_Vnom_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2453 | J270-06-1PNL-001 | J460-01-1VAV-615 | Setting | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Proportional Band | J460-01-1VAV-615_SupAirFlow_Set_P | J460-01-1VAV-615_SupAirFlow_Set_P | 2 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2454 | J270-06-1PNL-001 | J460-01-1VAV-615 | Setting | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Integral Time | J460-01-1VAV-615_SupAirFlow_Set_I | J460-01-1VAV-615_SupAirFlow_Set_I | 60 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2455 | J270-06-1PNL-001 | J460-01-1VAV-615 | Setting | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Derivative Time | J460-01-1VAV-615_SupAirFlow_Set_D | J460-01-1VAV-615_SupAirFlow_Set_D | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2456 | J270-06-1PNL-001 | J460-01-1VAV-614 | Alarm | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-614_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-614_VminHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2457 | J270-06-1PNL-001 | J460-01-1VAV-614 | Setting | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Minimum Flow | J460-01-1VAV-614_Vmin_HASP | J460-01-1VAV-614_Vmin_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2458 | J270-06-1PNL-001 | J460-01-1VAV-614 | Alarm | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-614_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-614_VminLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2459 | J270-06-1PNL-001 | J460-01-1VAV-614 | Setting | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Minimum Flow | J460-01-1VAV-614_Vmin_LASP | J460-01-1VAV-614_Vmin_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2460 | J270-06-1PNL-001 | J460-01-1VAV-614 | Alarm | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-614_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-614_VnomHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2461 | J270-06-1PNL-001 | J460-01-1VAV-614 | Setting | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Nominal Flow | J460-01-1VAV-614_Vnom_HASP | J460-01-1VAV-614_Vnom_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2462 | J270-06-1PNL-001 | J460-01-1VAV-614 | Alarm | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-614_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-614_VnomLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2463 | J270-06-1PNL-001 | J460-01-1VAV-614 | Setting | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Nominal Flow | J460-01-1VAV-614_Vnom_LASP | J460-01-1VAV-614_Vnom_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2464 | J270-06-1PNL-001 | J460-01-1VAV-616 | Alarm | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-616_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-616_VminHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2465 | J270-06-1PNL-001 | J460-01-1VAV-616 | Setting | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-616_Vmin_HASP | J460-01-1VAV-616_Vmin_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2466 | J270-06-1PNL-001 | J460-01-1VAV-616 | Alarm | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-616_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-616_VminLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2467 | J270-06-1PNL-001 | J460-01-1VAV-616 | Setting | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-616_Vmin_LASP | J460-01-1VAV-616_Vmin_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2468 | J270-06-1PNL-001 | J460-01-1VAV-616 | Alarm | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-616_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-616_VnomHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2469 | J270-06-1PNL-001 | J460-01-1VAV-616 | Setting | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-616_Vnom_HASP | J460-01-1VAV-616_Vnom_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2470 | J270-06-1PNL-001 | J460-01-1VAV-616 | Alarm | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-616_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-616_VnomLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2471 | J270-06-1PNL-001 | J460-01-1VAV-616 | Setting | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-616_Vnom_LASP | J460-01-1VAV-616_Vnom_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2472 | J270-06-1PNL-001 | J460-01-1VAV-616 | Setting | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Proportional Band | J460-01-1VAV-616_SupAirFlow_Set_P | J460-01-1VAV-616_SupAirFlow_Set_P | 2 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2473 | J270-06-1PNL-001 | J460-01-1VAV-616 | Setting | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Integral Time | J460-01-1VAV-616_SupAirFlow_Set_I | J460-01-1VAV-616_SupAirFlow_Set_I | 60 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2474 | J270-06-1PNL-001 | J460-01-1VAV-616 | Setting | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Derivative Time | J460-01-1VAV-616_SupAirFlow_Set_D | J460-01-1VAV-616_SupAirFlow_Set_D | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2475 | J270-06-1PNL-001 | J460-01-1VAV-617 | Alarm | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-617_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-617_VminHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2476 | J270-06-1PNL-001 | J460-01-1VAV-617 | Setting | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Minimum Flow | J460-01-1VAV-617_Vmin_HASP | J460-01-1VAV-617_Vmin_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2477 | J270-06-1PNL-001 | J460-01-1VAV-617 | Alarm | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-617_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-617_VminLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2478 | J270-06-1PNL-001 | J460-01-1VAV-617 | Setting | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Minimum Flow | J460-01-1VAV-617_Vmin_LASP | J460-01-1VAV-617_Vmin_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2479 | J270-06-1PNL-001 | J460-01-1VAV-617 | Alarm | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-617_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-617_VnomHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2480 | J270-06-1PNL-001 | J460-01-1VAV-617 | Setting | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Nominal Flow | J460-01-1VAV-617_Vnom_HASP | J460-01-1VAV-617_Vnom_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2481 | J270-06-1PNL-001 | J460-01-1VAV-617 | Alarm | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-617_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-617_VnomLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2482 | J270-06-1PNL-001 | J460-01-1VAV-617 | Setting | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Nominal Flow | J460-01-1VAV-617_Vnom_LASP | J460-01-1VAV-617_Vnom_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2483 | J270-06-1PNL-001 | J460-01-1VAV-001 | Alarm | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-001_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-001_VminHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2484 | J270-06-1PNL-001 | J460-01-1VAV-001 | Setting | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-001_Vmin_HASP | J460-01-1VAV-001_Vmin_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2485 | J270-06-1PNL-001 | J460-01-1VAV-001 | Alarm | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-001_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-001_VminLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2486 | J270-06-1PNL-001 | J460-01-1VAV-001 | Setting | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-001_Vmin_LASP | J460-01-1VAV-001_Vmin_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2487 | J270-06-1PNL-001 | J460-01-1VAV-001 | Alarm | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-001_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-001_VnomHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2488 | J270-06-1PNL-001 | J460-01-1VAV-001 | Setting | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-001_Vnom_HASP | J460-01-1VAV-001_Vnom_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2489 | J270-06-1PNL-001 | J460-01-1VAV-001 | Alarm | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-001_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-001_VnomLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2490 | J270-06-1PNL-001 | J460-01-1VAV-001 | Setting | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-001_Vnom_LASP | J460-01-1VAV-001_Vnom_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2491 | J270-06-1PNL-001 | J460-01-1VAV-002 | Alarm | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-002_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-002_VminHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2492 | J270-06-1PNL-001 | J460-01-1VAV-002 | Setting | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-002_Vmin_HASP | J460-01-1VAV-002_Vmin_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2493 | J270-06-1PNL-001 | J460-01-1VAV-002 | Alarm | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-002_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-002_VminLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2494 | J270-06-1PNL-001 | J460-01-1VAV-002 | Setting | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Minimum Flow | J460-01-1VAV-002_Vmin_LASP | J460-01-1VAV-002_Vmin_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2495 | J270-06-1PNL-001 | J460-01-1VAV-002 | Alarm | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-002_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-002_VnomHiAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2496 | J270-06-1PNL-001 | J460-01-1VAV-002 | Setting | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-002_Vnom_HASP | J460-01-1VAV-002_Vnom_HASP | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2497 | J270-06-1PNL-001 | J460-01-1VAV-002 | Alarm | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-002_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-002_VnomLoAlm | 2 | Y | - | bar: State 2 to State 64
A.03 | 2498 | J270-06-1PNL-001 | J460-01-1VAV-002 | Setting | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Nominal Flow | J460-01-1VAV-002_Vnom_LASP | J460-01-1VAV-002_Vnom_LASP | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2499 | J270-06-1PNL-001 | J460-01-1VAV-002 | Setting | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Proportional Band | J460-01-1VAV-002_SupAirFlow_Set_P | J460-01-1VAV-002_SupAirFlow_Set_P | 2 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2500 | J270-06-1PNL-001 | J460-01-1VAV-002 | Setting | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Integral Time | J460-01-1VAV-002_SupAirFlow_Set_I | J460-01-1VAV-002_SupAirFlow_Set_I | 60 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2501 | J270-06-1PNL-001 | J460-01-1VAV-002 | Setting | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Derivative Time | J460-01-1VAV-002_SupAirFlow_Set_D | J460-01-1VAV-002_SupAirFlow_Set_D | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2503 | J270-06-1PNL-001 | J270-06-3PLC-001 | Communication | J270-06-3PLC-001 - BMS Controller Alarm | - | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI Station | - | 2 | Y | bar: State 2 to State 64
2.0 | 2504 | J270-06-1PNL-001 | J270-06-3PLC-001 | Alarm | J270-06-3PLC-001- BMS Controller Common Alarm | J270-06-3PLC-001_CPUAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI Station | J270-06-3PLC-001_CPUAlm | 2 | Y | bar: State 2 to State 64
2.0 | 2505 | J270-06-1PNL-001 | J270-06-3PLC-001 | Alarm | J270-06-3PLC-001 - BMS IO Channel / Module Fail Alarm | J270-06-3PLC-001_IOAlm | - | OK | FAIL | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI Station | J270-06-3PLC-001_IOAlm | 2 | Y | bar: State 2 to State 64
2.0 | 2506 | J270-06-1PNL-001 | J270-06-3PLC-002 | Communication | J270-06-3PLC-002 - BMS Controller Alarm | - | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI Station | - | 2 | Y | bar: State 2 to State 64
2.0 | 2507 | J270-06-1PNL-001 | J270-06-3PLC-002 | Alarm | J270-06-3PLC-002 - BMS Controller Common Alarm | J270-06-3PLC-002_CPUAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI Station | J270-06-3PLC-002_CPUAlm | 2 | Y | bar: State 2 to State 64
2.0 | 2508 | J270-06-1PNL-001 | J270-06-3PLC-001 | Setting | BMS Ground Floor System Alarm Reset | J270-06-3PLC-001_GrndFlrAlarmReset | J270-06-3PLC-001_GrndFlrAlarmReset | OFF | RESET | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2509 | J270-06-1PNL-001 | J460-01-1VAV-601 | Setting | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-601_MinOpnFlwSP | J460-01-1VAV-601_MinOpnFlwSP | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2510 | J270-06-1PNL-001 | J460-01-1VAV-602 | Setting | J460-01-1VAV-602 - Room J6.06 - Return Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-602_MinOpnFlwSP | J460-01-1VAV-602_MinOpnFlwSP | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2511 | J270-06-1PNL-001 | J460-01-1VAV-603 | Setting | J460-01-1VAV-603 - Room J6.06 - Supply Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-603_MinOpnFlwSP | J460-01-1VAV-603_MinOpnFlwSP | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2512 | J270-06-1PNL-001 | J460-01-1VAV-604 | Setting | J460-01-1VAV-604 - Room J6.06 - Return Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-604_MinOpnFlwSP | J460-01-1VAV-604_MinOpnFlwSP | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2513 | J270-06-1PNL-001 | J460-01-1VAV-605 | Setting | J460-01-1VAV-605 - Room J6.07 - Supply Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-605_MinOpnFlwSP | J460-01-1VAV-605_MinOpnFlwSP | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2514 | J270-06-1PNL-001 | J460-01-1VAV-606 | Setting | J460-01-1VAV-606 - Room J6.07 - Return Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-606_MinOpnFlwSP | J460-01-1VAV-606_MinOpnFlwSP | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2515 | J270-06-1PNL-001 | J460-01-1VAV-608 | Setting | J460-01-1VAV-608 - Room J6.06 - Supply Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-608_MinOpnFlwSP | J460-01-1VAV-608_MinOpnFlwSP | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2516 | J270-06-1PNL-001 | J460-01-1VAV-607 | Setting | J460-01-1VAV-607 - Room J6.06 - Return Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-607_MinOpnFlwSP | J460-01-1VAV-607_MinOpnFlwSP | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2517 | J270-06-1PNL-001 | J460-01-1VAV-609 | Setting | J460-01-1VAV-609 - Room J6.05 - Supply Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-609_MinOpnFlwSP | J460-01-1VAV-609_MinOpnFlwSP | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2518 | J270-06-1PNL-001 | J460-01-1VAV-610 | Setting | J460-01-1VAV-610 - Room J6.05 - Return Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-610_MinOpnFlwSP | J460-01-1VAV-610_MinOpnFlwSP | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2519 | J270-06-1PNL-001 | J460-01-1VAV-611 | Setting | J460-01-1VAV-611 - Room J6.06 - Supply Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-611_MinOpnFlwSP | J460-01-1VAV-611_MinOpnFlwSP | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2520 | J270-06-1PNL-001 | J460-01-1VAV-613 | Setting | J460-01-1VAV-613 - Room J6.09 - Supply Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-613_MinOpnFlwSP | J460-01-1VAV-613_MinOpnFlwSP | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2521 | J270-06-1PNL-001 | J460-01-1VAV-612 | Setting | J460-01-1VAV-612 - Room J6.09 - Return Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-612_MinOpnFlwSP | J460-01-1VAV-612_MinOpnFlwSP | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2522 | J270-06-1PNL-001 | J460-01-1VAV-615 | Setting | J460-01-1VAV-615 - Room J6.11 - Supply Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-615_MinOpnFlwSP | J460-01-1VAV-615_MinOpnFlwSP | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2523 | J270-06-1PNL-001 | J460-01-1VAV-614 | Setting | J460-01-1VAV-614 - Room J6.11 - Return Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-614_MinOpnFlwSP | J460-01-1VAV-614_MinOpnFlwSP | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2524 | J270-06-1PNL-001 | J460-01-1VAV-616 | Setting | J460-01-1VAV-616 - Room J6.13 - Supply Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-616_MinOpnFlwSP | J460-01-1VAV-616_MinOpnFlwSP | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2525 | J270-06-1PNL-001 | J460-01-1VAV-617 | Setting | J460-01-1VAV-617 - Room J6.13 - Return Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-617_MinOpnFlwSP | J460-01-1VAV-617_MinOpnFlwSP | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2526 | J270-06-1PNL-001 | J460-01-1VAV-001 | Setting | J460-01-1VAV-001 - Room J0.07 - Return Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-001_MinOpnFlwSP | J460-01-1VAV-001_MinOpnFlwSP | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2527 | J270-06-1PNL-001 | J460-01-1VAV-002 | Setting | J460-01-1VAV-002 - Room J0.07 - Supply Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-002_MinOpnFlwSP | J460-01-1VAV-002_MinOpnFlwSP | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2528 | J270-06-1PNL-001 | J460-01-2FCV-001 | Measurement | J460-01-2FCV-001 - Chilled Water Valve - Speed | J460-01-2FCV-001_Spd | J460-01-2FCV-001_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2529 | J270-06-1PNL-001 | J460-02-2FCV-624 | Measurement | J460-02-2FCV-624 - Chilled Water Valve - Speed | J460-02-2FCV-624_Spd | J460-02-2FCV-624_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2530 | J270-06-1PNL-001 | J460-01-2FCV-601 | Measurement | J460-01-2FCV-601 - Room J6.02 - Reheater Valve Control Speed | J460-01-2FCV-601_Spd | J460-01-2FCV-601_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2531 | J270-06-1PNL-001 | J460-01-2FCV-602 | Measurement | J460-01-2FCV-602 - Room J6.03 - Reheater Valve Control Speed | J460-01-2FCV-602_Spd | J460-01-2FCV-602_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2532 | J270-06-1PNL-001 | J460-01-2FCV-603 | Measurement | J460-01-2FCV-603 - Room J6.06 - J460-01-1ACU-601 Heating Valve Control Speed | J460-01-2FCV-603_Spd | J460-01-2FCV-603_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2533 | J270-06-1PNL-001 | J460-01-2FCV-604 | Measurement | J460-01-2FCV-604 - Room J6.06 - J460-01-1ACU-601 Heating Valve Control Speed | J460-01-2FCV-604_Spd | J460-01-2FCV-604_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2534 | J270-06-1PNL-001 | J460-01-2FCV-605 | Measurement | J460-01-2FCV-605 - Room J6.06 - J460-01-1ACU-603 Heating Valve Control Speed | J460-01-2FCV-605_Spd | J460-01-2FCV-605_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2535 | J270-06-1PNL-001 | J460-01-2FCV-606 | Measurement | J460-01-2FCV-606 - Room J6.06 - J460-01-1ACU-604 Heating Valve Control Speed | J460-01-2FCV-606_Spd | J460-01-2FCV-606_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2536 | J270-06-1PNL-001 | J460-01-2FCV-607 | Measurement | J460-01-2FCV-607 - Room J6.06 - J460-01-1ACU-601 Cooling Valve Control Speed | J460-01-2FCV-607_Spd | J460-01-2FCV-607_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2537 | J270-06-1PNL-001 | J460-01-2FCV-608 | Measurement | J460-01-2FCV-608 - Room J6.06 - J460-01-1ACU-601 Cooling Valve Control Speed | J460-01-2FCV-608_Spd | J460-01-2FCV-608_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2538 | J270-06-1PNL-001 | J460-01-2FCV-609 | Measurement | J460-01-2FCV-609 - Room J6.06 - J460-01-1ACU-603 Cooling Valve Control Speed | J460-01-2FCV-609_Spd | J460-01-2FCV-609_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2539 | J270-06-1PNL-001 | J460-01-2FCV-610 | Measurement | J460-01-2FCV-610 - Room J6.06 - J460-01-1ACU-604 Cooling Valve Control Speed | J460-01-2FCV-610_Spd | J460-01-2FCV-610_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2540 | J270-06-1PNL-001 | J460-01-2FCV-611 | Measurement | J460-01-2FCV-611 - Room J6.07 - Reheater Valve Control Speed | J460-01-2FCV-611_Spd | J460-01-2FCV-611_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2541 | J270-06-1PNL-001 | J460-01-2FCV-612 | Measurement | J460-01-2FCV-612 - Room J6.06 - J460-01-1ACU-605 Heating Valve Control Speed | J460-01-2FCV-612_Spd | J460-01-2FCV-612_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2542 | J270-06-1PNL-001 | J460-01-2FCV-613 | Measurement | J460-01-2FCV-613 - Room J6.06 - J460-01-1ACU-606 Heating Valve Control Speed | J460-01-2FCV-613_Spd | J460-01-2FCV-613_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2543 | J270-06-1PNL-001 | J460-01-2FCV-614 | Measurement | J460-01-2FCV-614 - Room J6.06 - J460-01-1ACU-607 Heating Valve Control Speed | J460-01-2FCV-614_Spd | J460-01-2FCV-614_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2544 | J270-06-1PNL-001 | J460-01-2FCV-615 | Measurement | J460-01-2FCV-615 - Room J6.06 - J460-01-1ACU-608 Heating Valve Control Speed | J460-01-2FCV-615_Spd | J460-01-2FCV-615_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2545 | J270-06-1PNL-001 | J460-01-2FCV-616 | Measurement | J460-01-2FCV-616 - Room J6.06 - J460-01-1ACU-605 Cooling Valve Control Speed | J460-01-2FCV-616_Spd | J460-01-2FCV-616_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2546 | J270-06-1PNL-001 | J460-01-2FCV-617 | Measurement | J460-01-2FCV-617 - Room J6.06 - J460-01-1ACU-606 Cooling Valve Control Speed | J460-01-2FCV-617_Spd | J460-01-2FCV-617_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2547 | J270-06-1PNL-001 | J460-01-2FCV-618 | Measurement | J460-01-2FCV-618 - Room J6.06 - J460-01-1ACU-607 Cooling Valve Control Speed | J460-01-2FCV-618_Spd | J460-01-2FCV-618_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2548 | J270-06-1PNL-001 | J460-01-2FCV-619 | Measurement | J460-01-2FCV-619 - Room J6.06 - J460-01-1ACU-608 Cooling Valve Control Speed | J460-01-2FCV-619_Spd | J460-01-2FCV-619_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2549 | J270-06-1PNL-001 | J460-01-2FCV-620 | Measurement | J460-01-2FCV-620 - Room J6.05 - Reheater Valve Control Speed | J460-01-2FCV-620_Spd | J460-01-2FCV-620_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2550 | J270-06-1PNL-001 | J460-01-2FCV-621 | Measurement | J460-01-2FCV-621 - Room J6.06 - J460-01-1ACU-609 Heating Valve Control Speed | J460-01-2FCV-621_Spd | J460-01-2FCV-621_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2551 | J270-06-1PNL-001 | J460-01-2FCV-622 | Measurement | J460-01-2FCV-622 - Room J6.06 - J460-01-1ACU-609 Cooling Valve Control Speed | J460-01-2FCV-622_Spd | J460-01-2FCV-622_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2552 | J270-06-1PNL-001 | J460-01-2FCV-623 | Measurement | J460-01-2FCV-623 - Room J6.08 - Reheater Valve Control Speed | J460-01-2FCV-623_Spd | J460-01-2FCV-623_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2553 | J270-06-1PNL-001 | J460-01-2FCV-624 | Measurement | J460-01-2FCV-624 - Room J6.09 - J460-01-1ACU-610 Heating Valve Control Speed | J460-01-2FCV-624_Spd | J460-01-2FCV-624_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2554 | J270-06-1PNL-001 | J460-01-2FCV-625 | Measurement | J460-01-2FCV-625 - Room J6.09 - J460-01-1ACU-611 Heating Valve Control Speed | J460-01-2FCV-625_Spd | J460-01-2FCV-625_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2555 | J270-06-1PNL-001 | J460-01-2FCV-626 | Measurement | J460-01-2FCV-626 - Room J6.09 - J460-01-1ACU-612 Heating Valve Control Speed | J460-01-2FCV-626_Spd | J460-01-2FCV-626_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2556 | J270-06-1PNL-001 | J460-01-2FCV-627 | Measurement | J460-01-2FCV-627 - Room J6.09 - J460-01-1ACU-613 Heating Valve Control Speed | J460-01-2FCV-627_Spd | J460-01-2FCV-627_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2557 | J270-06-1PNL-001 | J460-01-2FCV-628 | Measurement | J460-01-2FCV-628 - Room J6.09 - J460-01-1ACU-610 Cooling Valve Control Speed | J460-01-2FCV-628_Spd | J460-01-2FCV-628_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2558 | J270-06-1PNL-001 | J460-01-2FCV-629 | Measurement | J460-01-2FCV-629 - Room J6.09 - J460-01-1ACU-611 Cooling Valve Control Speed | J460-01-2FCV-629_Spd | J460-01-2FCV-629_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2559 | J270-06-1PNL-001 | J460-01-2FCV-630 | Measurement | J460-01-2FCV-630 - Room J6.09 - J460-01-1ACU-612 Cooling Valve Control Speed | J460-01-2FCV-630_Spd | J460-01-2FCV-630_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2560 | J270-06-1PNL-001 | J460-01-2FCV-631 | Measurement | J460-01-2FCV-631 - Room J6.09 - J460-01-1ACU-613 Cooling Valve Control Speed | J460-01-2FCV-631_Spd | J460-01-2FCV-631_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2561 | J270-06-1PNL-001 | J460-01-2FCV-632 | Measurement | J460-01-2FCV-632 - Room J6.10 - Reheater Valve Control Speed | J460-01-2FCV-632_Spd | J460-01-2FCV-632_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2562 | J270-06-1PNL-001 | J460-01-2FCV-633 | Measurement | J460-01-2FCV-633 - Room J6.11 - J460-01-1ACU-614 Heating Valve Control Speed | J460-01-2FCV-633_Spd | J460-01-2FCV-633_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2563 | J270-06-1PNL-001 | J460-01-2FCV-634 | Measurement | J460-01-2FCV-634 - Room J6.11 - J460-01-1ACU-615 Heating Valve Control Speed | J460-01-2FCV-634_Spd | J460-01-2FCV-634_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2564 | J270-06-1PNL-001 | J460-01-2FCV-635 | Measurement | J460-01-2FCV-635 - Room J6.11 - J460-01-1ACU-616 Heating Valve Control Speed | J460-01-2FCV-635_Spd | J460-01-2FCV-635_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2565 | J270-06-1PNL-001 | J460-01-2FCV-636 | Measurement | J460-01-2FCV-636 - Room J6.11 - J460-01-1ACU-617 Heating Valve Control Speed | J460-01-2FCV-636_Spd | J460-01-2FCV-636_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2566 | J270-06-1PNL-001 | J460-01-2FCV-637 | Measurement | J460-01-2FCV-637 - Room J6.11 - J460-01-1ACU-614 Cooling Valve Control Speed | J460-01-2FCV-637_Spd | J460-01-2FCV-637_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2567 | J270-06-1PNL-001 | J460-01-2FCV-638 | Measurement | J460-01-2FCV-638 - Room J6.11 - J460-01-1ACU-615 Cooling Valve Control Speed | J460-01-2FCV-638_Spd | J460-01-2FCV-638_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2568 | J270-06-1PNL-001 | J460-01-2FCV-639 | Measurement | J460-01-2FCV-639 - Room J6.11 - J460-01-1ACU-616 Cooling Valve Control Speed | J460-01-2FCV-639_Spd | J460-01-2FCV-639_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2569 | J270-06-1PNL-001 | J460-01-2FCV-640 | Measurement | J460-01-2FCV-640 - Room J6.11 - J460-01-1ACU-617 Cooling Valve Control Speed | J460-01-2FCV-640_Spd | J460-01-2FCV-640_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2570 | J270-06-1PNL-001 | J460-01-2FCV-641 | Measurement | J460-01-2FCV-641 - Room J6.13 - Reheater Valve Control Speed | J460-01-2FCV-641_Spd | J460-01-2FCV-641_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2571 | J270-06-1PNL-001 | J460-01-2FCV-642 | Measurement | J460-01-2FCV-642 - Room J6.12 - Reheater Valve Control Speed | J460-01-2FCV-642_Spd | J460-01-2FCV-642_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2572 | J270-06-1PNL-001 | J460-02-2FCV-601 | Measurement | J460-02-2FCV-601 - Room J6.20 - Reheater Valve Control Speed | J460-02-2FCV-601_Spd | J460-02-2FCV-601_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2573 | J270-06-1PNL-001 | J460-02-2FCV-602 | Measurement | J460-02-2FCV-602 - Room J6.20 - J460-02-1ACU-602 Cooling Valve Control Speed | J460-02-2FCV-602_Spd | J460-02-2FCV-602_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2574 | J270-06-1PNL-001 | J460-02-2FCV-603 | Measurement | J460-02-2FCV-603 - Room J6.22 - J460-02-1ACU-601 Cooling Valve Control Speed | J460-02-2FCV-603_Spd | J460-02-2FCV-603_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2575 | J270-06-1PNL-001 | J460-02-2FCV-604 | Measurement | J460-02-2FCV-604 - Room J6.22 - J460-02-1ACU-601 Heating Valve Control Speed | J460-02-2FCV-604_Spd | J460-02-2FCV-604_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2576 | J270-06-1PNL-001 | J460-02-2FCV-605 | Measurement | J460-02-2FCV-605 - Room J6.23 - Reheater Valve Control Speed | J460-02-2FCV-605_Spd | J460-02-2FCV-605_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2577 | J270-06-1PNL-001 | J460-02-2FCV-606 | Measurement | J460-02-2FCV-606 - Room J6.23 - Reheater Valve Control Speed | J460-02-2FCV-606_Spd | J460-02-2FCV-606_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2578 | J270-06-1PNL-001 | J460-02-2FCV-607 | Measurement | J460-02-2FCV-607 - Room J6.23 - J460-02-1ACU-603 Cooling Valve Control Speed | J460-02-2FCV-607_Spd | J460-02-2FCV-607_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2579 | J270-06-1PNL-001 | J460-02-2FCV-608 | Measurement | J460-02-2FCV-608 - Room J6.23 - Reheater Valve Control Speed | J460-02-2FCV-608_Spd | J460-02-2FCV-608_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2580 | J270-06-1PNL-001 | J460-02-2FCV-609 | Measurement | J460-02-2FCV-609 - Room J6.23 - J460-02-1ACU-604 Cooling Valve Control Speed | J460-02-2FCV-609_Spd | J460-02-2FCV-609_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2581 | J270-06-1PNL-001 | J460-02-2FCV-610 | Measurement | J460-02-2FCV-610 - Room J6.23 - Reheater Valve Control Speed | J460-02-2FCV-610_Spd | J460-02-2FCV-610_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2582 | J270-06-1PNL-001 | J460-02-2FCV-611 | Measurement | J460-02-2FCV-611 - Room J6.23 - J460-02-1ACU-605 Cooling Valve Control Speed | J460-02-2FCV-611_Spd | J460-02-2FCV-611_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2583 | J270-06-1PNL-001 | J460-02-2FCV-612 | Measurement | J460-02-2FCV-612 - Room J6.24 - Reheater Valve Control Speed | J460-02-2FCV-612_Spd | J460-02-2FCV-612_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2584 | J270-06-1PNL-001 | J460-02-2FCV-613 | Measurement | J460-02-2FCV-613 - Room J6.24 - J460-02-1ACU-606 Cooling Valve Control Speed | J460-02-2FCV-613_Spd | J460-02-2FCV-613_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2585 | J270-06-1PNL-001 | J460-02-2FCV-614 | Measurement | J460-02-2FCV-614 - Room J6.24 - Reheater Valve Control Speed | J460-02-2FCV-614_Spd | J460-02-2FCV-614_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2586 | J270-06-1PNL-001 | J460-02-2FCV-615 | Measurement | J460-02-2FCV-615 - Room J6.24 - J460-02-1ACU-607 Cooling Valve Control Speed | J460-02-2FCV-615_Spd | J460-02-2FCV-615_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2587 | J270-06-1PNL-001 | J460-02-2FCV-616 | Measurement | J460-02-2FCV-616 - Room J6.20 - Reheater Valve Control Speed | J460-02-2FCV-616_Spd | J460-02-2FCV-616_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2588 | J270-06-1PNL-001 | J460-02-2FCV-617 | Measurement | J460-02-2FCV-617 - Room J6.20 - Reheater Valve Control Speed | J460-02-2FCV-617_Spd | J460-02-2FCV-617_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2589 | J270-06-1PNL-001 | J460-02-2FCV-618 | Measurement | J460-02-2FCV-618 - Room J6.20 - J460-02-1ACU-609 Cooling Valve Control Speed | J460-02-2FCV-618_Spd | J460-02-2FCV-618_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2590 | J270-06-1PNL-001 | J460-02-2FCV-619 | Measurement | J460-02-2FCV-619 - Room J6.17 - Reheater Valve Control Speed | J460-02-2FCV-619_Spd | J460-02-2FCV-619_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2591 | J270-06-1PNL-001 | J460-02-2FCV-620 | Measurement | J460-02-2FCV-620 - Room J6.17 - Reheater Valve Control Speed | J460-02-2FCV-620_Spd | J460-02-2FCV-620_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2592 | J270-06-1PNL-001 | J460-02-2FCV-621 | Measurement | J460-02-2FCV-621 - Room J6.17 - Reheater Valve Control Speed | J460-02-2FCV-621_Spd | J460-02-2FCV-621_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2593 | J270-06-1PNL-001 | J460-02-2FCV-622 | Measurement | J460-02-2FCV-622 - Room J6.14 - Reheater Valve Control Speed | J460-02-2FCV-622_Spd | J460-02-2FCV-622_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2594 | J270-06-1PNL-001 | J460-02-2FCV-623 | Measurement | J460-02-2FCV-623 - Room J6.14 - Reheater Valve Control Speed | J460-02-2FCV-623_Spd | J460-02-2FCV-623_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2595 | J270-06-1PNL-001 | J460-01-2FCV-002 | Measurement | J460-01-2FCV-002 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Speed | J460-01-2FCV-002_Spd | J460-01-2FCV-002_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2596 | J270-06-1PNL-001 | J460-01-2FCV-003 | Measurement | J460-01-2FCV-003 - Room J0.07 - J460-01-1ACU-002 Heating Valve Control Speed | J460-01-2FCV-003_Spd | J460-01-2FCV-003_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2597 | J270-06-1PNL-001 | J460-01-2FCV-004 | Measurement | J460-01-2FCV-004 - Room J0.07 - J460-01-1ACU-003 Heating Valve Control Speed | J460-01-2FCV-004_Spd | J460-01-2FCV-004_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2598 | J270-06-1PNL-001 | J460-01-2FCV-005 | Measurement | J460-01-2FCV-005 - Room J0.07 - J460-01-1ACU-004 Heating Valve Control Speed | J460-01-2FCV-005_Spd | J460-01-2FCV-005_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2599 | J270-06-1PNL-001 | J460-01-2FCV-006 | Measurement | J460-01-2FCV-006 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Speed | J460-01-2FCV-006_Spd | J460-01-2FCV-006_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2600 | J270-06-1PNL-001 | J460-01-2FCV-007 | Measurement | J460-01-2FCV-007 - Room J0.07 - J460-01-1ACU-002 Cooling Valve Control Speed | J460-01-2FCV-007_Spd | J460-01-2FCV-007_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2601 | J270-06-1PNL-001 | J460-01-2FCV-008 | Measurement | J460-01-2FCV-008 - Room J0.07 - J460-01-1ACU-003 Cooling Valve Control Speed | J460-01-2FCV-008_Spd | J460-01-2FCV-008_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2602 | J270-06-1PNL-001 | J460-01-2FCV-009 | Measurement | J460-01-2FCV-009 - Room J0.07 - J460-01-1ACU-004 Cooling Valve Control Speed | J460-01-2FCV-009_Spd | J460-01-2FCV-009_Spd | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2603 | J270-06-1PNL-001 | J229-06-1QIT-001 | Alarm | J229-06-1QIT-001 - SVK-6H - Energy Meter Communication Failure Alarm | J229-06-1QIT-001_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J229-06-1QIT-001_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2604 | J270-06-1PNL-001 | J229-06-1QIT-002 | Alarm | J229-06-1QIT-002 - VK-6H-1 - Energy Meter - Communication Failure Alarm | J229-06-1QIT-002_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J229-06-1QIT-002_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2605 | J270-06-1PNL-001 | J229-06-1QIT-003 | Alarm | J229-06-1QIT-003 - VK-6H-2 - Energy Meter - Communication Failure Alarm | J229-06-1QIT-003_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J229-06-1QIT-003_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2606 | J270-06-1PNL-001 | J229-06-1QIT-004 | Alarm | J229-06-1QIT-004 - VK-6H-3 - Energy Meter - Communication Failure Alarm | J229-06-1QIT-004_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J229-06-1QIT-004_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2607 | J270-06-1PNL-001 | J229-06-1QIT-005 | Alarm | J229-06-1QIT-005 - VK-6H-4 - Energy Meter - Communication Failure Alarm | J229-06-1QIT-005_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J229-06-1QIT-005_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2608 | J270-06-1PNL-001 | J232-06-1UPS-001 | Alarm | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor - Communication Failure Alarm | J232-06-1UPS-001_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station | J232-06-1UPS-001_CommFailAlm | 2 | Y | - | bar: State 2 to State 64
1.0 | 2609 | J460-01-1CP-604 | J460-01-2TT-604 | Setting | J460-01-2TT-604 - Room J6.07 - Temperature Proportional Band | J460-01-2TT-604_RmTemp_Set_P_Cool | J460-01-2TT-604_RmTemp_Set_P_Cool | 2 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2610 | J460-01-1CP-604 | J460-01-2TT-604 | Setting | J460-01-2TT-604 - Room J6.07 - Temperature Integral Time | J460-01-2TT-604_RmTemp_Set_I_Cool | J460-01-2TT-604_RmTemp_Set_I_Cool | 60 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2611 | J460-01-1CP-604 | J460-01-2TT-604 | Setting | J460-01-2TT-604 - Room J6.07 - Temperature Derivative Time | J460-01-2TT-604_RmTemp_Set_D_Cool | J460-01-2TT-604_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2612 | J460-01-1CP-605 | J460-01-2TT-605 | Setting | J460-01-2TT-605 - Room J6.05 - Temperature Proportional Band | J460-01-2TT-605_RmTemp_Set_P_Cool | J460-01-2TT-605_RmTemp_Set_P_Cool | 2 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2613 | J460-01-1CP-605 | J460-01-2TT-605 | Setting | J460-01-2TT-605 - Room J6.05 - Temperature Integral Time | J460-01-2TT-605_RmTemp_Set_I_Cool | J460-01-2TT-605_RmTemp_Set_I_Cool | 60 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2614 | J460-01-1CP-605 | J460-01-2TT-605 | Setting | J460-01-2TT-605 - Room J6.05 - Temperature Derivative Time | J460-01-2TT-605_RmTemp_Set_D_Cool | J460-01-2TT-605_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2615 | J460-01-1CP-610 | J460-01-2TT-610 | Setting | J460-01-2TT-610 - Room J6.13 - Temperature Proportional Band | J460-01-2TT-610_RmTemp_Set_P_Cool | J460-01-2TT-610_RmTemp_Set_P_Cool | 2 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2616 | J460-01-1CP-610 | J460-01-2TT-610 | Setting | J460-01-2TT-610 - Room J6.13 - Temperature Integral Time | J460-01-2TT-610_RmTemp_Set_I_Cool | J460-01-2TT-610_RmTemp_Set_I_Cool | 60 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2617 | J460-01-1CP-610 | J460-01-2TT-610 | Setting | J460-01-2TT-610 - Room J6.13 - Temperature Derivative Time | J460-01-2TT-610_RmTemp_Set_D_Cool | J460-01-2TT-610_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2618 | J460-02-1CP-605 | J460-02-2TT-605 | Setting | J460-02-2TT-605 - Room J6.17 - Temperature Proportional Band | J460-02-2TT-605_RmTemp_Set_P_Cool | J460-02-2TT-605_RmTemp_Set_P_Cool | 2 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2619 | J460-02-1CP-605 | J460-02-2TT-605 | Setting | J460-02-2TT-605 - Room J6.17 - Temperature Integral Time | J460-02-2TT-605_RmTemp_Set_I_Cool | J460-02-2TT-605_RmTemp_Set_I_Cool | 60 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2620 | J460-02-1CP-605 | J460-02-2TT-605 | Setting | J460-02-2TT-605 - Room J6.17 - Temperature Derivative Time | J460-02-2TT-605_RmTemp_Set_D_Cool | J460-02-2TT-605_RmTemp_Set_D_Cool | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2502
End of Document
Note on AB13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Please confirm if the control level 220 is correct. We have considered 220 as this alarm (LASP) will close the valve & turn the pump OFF.
Note on G55: Patil, Vishal: Spd changed to Cntr
Note on F132: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Please confirm the M-Bus point tags & description.
Note on F166: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Please confirm the M-Bus point tags & description.
Note on G442: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: J460-01-2XS-001_ChlWtrCirPmpEna
Note on G443: Patil, Vishal: Spd changed to Cntr
Note on G444: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: J460-01-2XA-001_ChlWtrCirPmpAlm
Note on G446: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: J460-01-2SS-001_ChlWtrCirPmpSts
Note on G449: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: J460-01-2HSI-001_ChlWtrCirPmpMS
Note on F624: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Replaced ACU 601 to 602
Note on F625: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Replaced ACU 601 to 602
Note on F626: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Replaced ACU 601 to 602
Note on F627: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Replaced ACU 601 to 602
Note on F628: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Replaced ACU 601 to 602
Note on F629: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Replaced ACU 601 to 602
Note on F630: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Replaced ACU 601 to 602
Note on F631: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Replaced ACU 601 to 602
Note on F632: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Replaced ACU 601 to 602
Note on F660: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Replaced ACU 601 to 602
Note on F661: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Replaced ACU 601 to 602
Note on F662: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Replaced ACU 601 to 602
Note on F663: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Replaced ACU 601 to 602
Note on F664: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Replaced ACU 601 to 602
Note on F665: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Replaced ACU 601 to 602
Note on F666: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Replaced ACU 601 to 602
Note on F667: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Replaced ACU 601 to 602
Note on F668: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Replaced ACU 601 to 602
Note on G820: Patil, Vishal: _Heat Added
Note on G821: Patil, Vishal: _Heat Added
Note on G822: Patil, Vishal: _Heat Added
Note on G823: Patil, Vishal: _Heat Added
Note on G824: Patil, Vishal: _Heat Added
Note on G825: Patil, Vishal: _Heat Added
Note on G992: Patil, Vishal: _Heat Added
Note on G993: Patil, Vishal: _Heat Added
Note on G994: Patil, Vishal: _Heat Added
Note on G995: Patil, Vishal: _Cool Added
Note on G996: Patil, Vishal: _Cool Added
Note on G997: Patil, Vishal: _Cool Added
Note on G1411: Patil, Vishal: _Heat Added
Note on G1412: Patil, Vishal: _Heat Added
Note on G1413: Patil, Vishal: _Heat Added
Note on G1414: Patil, Vishal: _Cool Added
Note on G1415: Patil, Vishal: _Cool Added
Note on G1416: Patil, Vishal: _Cool Added
Note on F1612: Patil, Vishal: Effective added.
Note on G1612: Patil, Vishal: Eff added
Note on F1928: Patil, Vishal: effective added
Note on G1928: Patil, Vishal: Eff added
Note on G2021: Patil, Vishal: _Heat added
Note on G2024: Patil, Vishal: _Cool Added
Note on G2057: Patil, Vishal: _Heat Added
Note on G2060: Patil, Vishal: _Cool Added
Note on G2093: Patil, Vishal: Added _Heat
Note on G2094: Patil, Vishal: Added _Heat
Note on G2095: Patil, Vishal: Added _Heat
Note on G2096: Patil, Vishal: Added _Cool
Note on G2097: Patil, Vishal: Added _Cool
Note on G2098: Patil, Vishal: Added _Cool
Note on G2129: Patil, Vishal: _Heat Added
Note on G2132: Patil, Vishal: _Cool Added
Note on G2322: Patil, Vishal: OLD Tag - J270-06-3PLC-001_RmMode_GrndFlr_Labs
Note on AA2370: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirm on the Hysteresis for Flow
Note on AA2374: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirm on the Hysteresis for Flow
Note on AA2378: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirm on the Hysteresis for Flow
Note on AA2385: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirm on the Hysteresis for Flow
Note on AA2412: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirm on the Hysteresis for Flow
Note on AA2416: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirm on the Hysteresis for Flow
Note on AA2431: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirm on the Hysteresis for Flow
Note on AA2435: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirm on the Hysteresis for Flow
Note on AA2447: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirm on the Hysteresis for Flow
Note on AA2451: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirm on the Hysteresis for Flow
Note on AA2469: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirm on the Hysteresis for Flow
Note on AA2474: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirm on the Hysteresis for Flow
Note on AA2497: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirm on the Hysteresis for Flow
Note on AA2501: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirm on the Hysteresis for Flow
Note on AA2516: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirm on the Hysteresis for Flow
Note on AA2520: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirm on the Hysteresis for Flow
Note on AA2535: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirm on the Hysteresis for Flow
Note on AA2539: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirm on the Hysteresis for Flow
Note on AA2543: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirm on the Hysteresis for Flow
Note on AA2547: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirm on the Hysteresis for Flow
Note on G2665: Patil, Vishal: _Heat Added
Note on G2666: Patil, Vishal: _Heat Added
Note on G2667: Patil, Vishal: _Heat Added
Note on G2668: Patil, Vishal: _Cool Added
Note on G2669: Patil, Vishal: _Cool Added
Note on G2670: Patil, Vishal: _Cool Added
Note on G2671: Patil, Vishal: _Cool Added
Note on G2672: Patil, Vishal: _Cool Added
Note on G2673: Patil, Vishal: _Cool Added

## Instructions
Alarm Notification Value | EBI priority | GMP Alarm Guideline
1 | Urgent (U 00) | A1 [Used for Alarm Pager]
2 | High (H 00) | A3
3 | Low (L 00) | A5
4 | Journal (J 00) | -

## RackPositioning (hidden)
7448-15-1PNL-001 |  | 7448-15-1PNL-001 Expansion
Description | Module Quantity | Description | Module Quantity
Analog Input (8 channel) | 0 | Analog Input (8 channel) | 0
Analog Input hi level (16 ch) | 5 | Analog Input hi level (16 ch) | 0
Analog Outputs 0 to 20mA (8 channel, 5 modules/rack) | 0 | Analog Outputs 0 to 20mA (8 channel, 5 modules/rack) | 0
Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 2 | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 2
Digital Input, 24VDC (32 channel) | 3 | Digital Input, 24VDC (32 channel) | 0
Digital Output, Relays ( 8 channel) | 2 | Digital Output, Relays ( 8 channel) | 1
| 12 |  | 3
Module assignement for this panel |  | Module assignement for this panel
Discription | Rack slot | Discription | Rack slot
Controller C70 CPU | 0 | I/O Scanner | 0
Power Supply 120/240VAC, 60W | 0 | Power Supply 120/240VAC, 60W | 0
Digital Input, 24VDC (32 channel) | 1 | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 1
Digital Input, 24VDC (32 channel) | 2 | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 2
Digital Input, 24VDC (32 channel) | 3 | Digital Output, Relays ( 8 channel) | 3
Analog Input hi level (16 ch) | 4 | SPARE | 4
Analog Input hi level (16 ch) | 5
Analog Input hi level (16 ch) | 6
Analog Input hi level (16 ch) | 7
Analog Input hi level (16 ch) | 8
Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 9
Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 10
Digital Output, Relays ( 8 channel) | 11
Digital Output, Relays ( 8 channel) | 12

## Doc Revision History
*** END OF DOCUMENT ***
Document Revision History
Version Number | Section | Description of Change | Justification of Change
1.0 | All | New Document | CC#2249686
2 | All | Software changes implemented | CC#2249686
2.1 | All | Updated point description, ACU points and Ranges | CC#2249686

## Vault Data (hidden)
Vault Data |  | Vault Data
Cell Tokens | Value | (Default/Odd) Frontsheet Header | (Default/Odd) Frontsheet Header Configure Token
${vault:major} | 1 | Left Header
${vault:minor} | 1 | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
${vault:subtype__v} | Design | Right Header
${vault:document_owning_facility__vr.name__v} | Leiden JBV | (Default/Odd) Frontsheet Footer | (Default/Odd) Frontsheet Footer Configure Token
${vault:document_owning_facility__vr.id} | 00F000000003361 | Left Footer
${vault:owning_facility__v} | Leiden JBV | Central Footer
${vault:title__v} | J270-06 BMS 6th Floor Alarm and Parameter list J-Building | Right Footer
${vault:type__v} | Technical Document | (Even) Frontsheet Header | (Even) Frontsheet Header Configure Token
${vault:document_facility__vr.name__v} | Leiden JBV | Left Header
${vault:document_facility__vr.id} | 00F000000003361 | Central Header
${vault:version} | 2 | Right Header
${vault:document_impacted_facilities__vr.name__v} | Leiden JBV | (Even) Frontsheet Footer | (Even) Frontsheet Footer Configure Token
${vault:document_impacted_facilities__vr.id} | 00F000000003361 | Left Footer
Central Footer
Right Footer
|  | (First Page) Frontsheet Header | (First Page) Frontsheet Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) Frontsheet Footer | (First Page) Frontsheet Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) J270-06 Header | (Default/Odd) J270-06 Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) J270-06 Footer | (Default/Odd) J270-06 Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) J270-06 Header | (Even) J270-06 Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) J270-06 Footer | (Even) J270-06 Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) J270-06 Header | (First Page) J270-06 Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) J270-06 Footer | (First Page) J270-06 Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) Instructions Header | (Default/Odd) Instructions Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) Instructions Footer | (Default/Odd) Instructions Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) Instructions Header | (Even) Instructions Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) Instructions Footer | (Even) Instructions Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) Instructions Header | (First Page) Instructions Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) Instructions Footer | (First Page) Instructions Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) RackPositioning Header | (Default/Odd) RackPositioning Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) RackPositioning Footer | (Default/Odd) RackPositioning Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) RackPositioning Header | (Even) RackPositioning Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) RackPositioning Footer | (Even) RackPositioning Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) RackPositioning Header | (First Page) RackPositioning Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) RackPositioning Footer | (First Page) RackPositioning Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) Doc Revision History Header | (Default/Odd) Doc Revision History Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) Doc Revision History Footer | (Default/Odd) Doc Revision History Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) Doc Revision History Header | (Even) Doc Revision History Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) Doc Revision History Footer | (Even) Doc Revision History Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) Doc Revision History Header | (First Page) Doc Revision History Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) Doc Revision History Footer | (First Page) Doc Revision History Footer Configure Token
Left Footer
Central Footer
Right Footer