## Frontsheet
Janssen Kappa Pollux QC
BMS 6th Floor Office And Lab Room Control Alarm & Parameter List
Document Number: J270-06-APL-001
BMS Alarm & Parameter List
Version: 2.1
BMS Panel : J270-06-1PNL-001 Controller:J270-06-3PLC-001, J270-06-3PLC-002

## Instructions
Alarm Notification Value | EBI priority | GMP Alarm Guideline
1 | Urgent (U 00) | A1 [Used for Alarm Pager]
2 | High (H 00) | A3
3 | Low (L 00) | A5
4 | Journal (J 00) | -

## RackPositioning
7448-15-1PNL-001 |  | 7448-15-1PNL-001 Expansion
Description | Module Quantity | Description | Module Quantity
Analog Input (8 channel) | 0 | Analog Input (8 channel) | 0
Analog Input hi level (16 ch) | 5 | Analog Input hi level (16 ch) | 0
Analog Outputs 0 to 20mA (8 channel, 5 modules/rack) | 0 | Analog Outputs 0 to 20mA (8 channel, 5 modules/rack) | 0
Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 2 | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 2
Digital Input, 24VDC (32 channel) | 3 | Digital Input, 24VDC (32 channel) | 0
Digital Output, Relays ( 8 channel) | 2 | Digital Output, Relays ( 8 channel) | 1
Module assignement for this panel |  | Module assignement for this panel
Discription | Rack slot | Discription | Rack slot
Controller C70 CPU | 0 | I/O Scanner | 0
Power Supply 120/240VAC, 60W | 0 | Power Supply 120/240VAC, 60W | 0
Digital Input, 24VDC (32 channel) | 1 | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 1
Digital Input, 24VDC (32 channel) | 2 | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 2
Digital Input, 24VDC (32 channel) | 3 | Digital Output, Relays ( 8 channel) | 3
Analog Input hi level (16 ch) | 4 | SPARE | 4
Analog Input hi level (16 ch) | 5
Analog Input hi level (16 ch) | 6
Analog Input hi level (16 ch) | 7
Analog Input hi level (16 ch) | 8
Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 9
Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 10
Digital Output, Relays ( 8 channel) | 11
Digital Output, Relays ( 8 channel) | 12

## Doc Revision History
*** END OF DOCUMENT ***
Document Revision History
Version Number | Section | Description of Change | Justification of Change
1.0 | All | New Document | CC#2249686
2 | All | Software changes implemented | CC#2249686
2.1 | All | Updated point description, ACU points and Ranges | CC#2249686

## Vault Data
Vault Data |  | Vault Data
Cell Tokens | Value | (Default/Odd) Frontsheet Header | (Default/Odd) Frontsheet Header Configure Token
${vault:major} | 1 | Left Header
${vault:minor} | 1 | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
${vault:subtype__v} | Design | Right Header
${vault:document_owning_facility__vr.name__v} | Leiden JBV | (Default/Odd) Frontsheet Footer | (Default/Odd) Frontsheet Footer Configure Token
${vault:document_owning_facility__vr.id} | 00F000000003361 | Left Footer
${vault:owning_facility__v} | Leiden JBV | Central Footer
${vault:title__v} | J270-06 BMS 6th Floor Alarm and Parameter list J-Building | Right Footer
${vault:type__v} | Technical Document | (Even) Frontsheet Header | (Even) Frontsheet Header Configure Token
${vault:document_facility__vr.name__v} | Leiden JBV | Left Header
${vault:document_facility__vr.id} | 00F000000003361 | Central Header
${vault:version} | 2 | Right Header
${vault:document_impacted_facilities__vr.name__v} | Leiden JBV | (Even) Frontsheet Footer | (Even) Frontsheet Footer Configure Token
${vault:document_impacted_facilities__vr.id} | 00F000000003361 | Left Footer
Central Footer
Right Footer
|  | (First Page) Frontsheet Header | (First Page) Frontsheet Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) Frontsheet Footer | (First Page) Frontsheet Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) J270-06 Header | (Default/Odd) J270-06 Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) J270-06 Footer | (Default/Odd) J270-06 Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) J270-06 Header | (Even) J270-06 Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) J270-06 Footer | (Even) J270-06 Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) J270-06 Header | (First Page) J270-06 Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) J270-06 Footer | (First Page) J270-06 Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) Instructions Header | (Default/Odd) Instructions Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) Instructions Footer | (Default/Odd) Instructions Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) Instructions Header | (Even) Instructions Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) Instructions Footer | (Even) Instructions Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) Instructions Header | (First Page) Instructions Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) Instructions Footer | (First Page) Instructions Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) RackPositioning Header | (Default/Odd) RackPositioning Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) RackPositioning Footer | (Default/Odd) RackPositioning Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) RackPositioning Header | (Even) RackPositioning Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) RackPositioning Footer | (Even) RackPositioning Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) RackPositioning Header | (First Page) RackPositioning Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) RackPositioning Footer | (First Page) RackPositioning Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) Doc Revision History Header | (Default/Odd) Doc Revision History Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) Doc Revision History Footer | (Default/Odd) Doc Revision History Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) Doc Revision History Header | (Even) Doc Revision History Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) Doc Revision History Footer | (Even) Doc Revision History Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) Doc Revision History Header | (First Page) Doc Revision History Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) Doc Revision History Footer | (First Page) Doc Revision History Footer Configure Token
Left Footer
Central Footer
Right Footer

## J270-06-demo
Rev Nr | Nr | Outstation | Device Tag | Function | Point Description | EBI Tag | JACE Tag | Range (Low) / State 0 | Range (High) / State 1 | State 2 | State 3 | State 4 | State 5 | State 6 | State 7 | State 8 | State 9 | State 16 | State 32 | State 64 | State 128 | State 8192 | State 16384 | State 32768 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
1.0 | 9 | J270-06-1PNL-001 | J460-01-2TT-612 | Measurement | J460-01-2TT-612 - Chilled Water - Supply Temperature | J460-01-2TT-612_ChlWtrSupTemp |  | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 10 | J270-06-1PNL-001 | J460-01-2TT-612 | Measurement | J460-01-2TT-612 - Chilled Water - Supply Temperature Field | J460-01-2TT-612_ChlWtrSupTemp_Field |  | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 11 | J270-06-1PNL-001 | J460-01-2TT-612 | Alarm | J460-01-2TT-612 - Chilled Water - Supply Temperature High Alarm | J460-01-2TT-612_ChlWtrSupTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 12 | J270-06-1PNL-001 | J460-01-2TT-612 | Setting | J460-01-2TT-612 - Chilled Water - Supply Temperature | J460-01-2TT-612_ChlWtrSupTemp_HASP |  | - | 16 | [11 empty] | - | - | - | - | - | 0.5 | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 13 | J270-06-1PNL-001 | J460-01-2TT-612 | Alarm | J460-01-2TT-612 - Chilled Water - Supply Temperature Low Alarm | J460-01-2TT-612_ChlWtrSupTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 14 | J270-06-1PNL-001 | J460-01-2TT-612 | Setting | J460-01-2TT-612 - Chilled Water - Supply Temperature | J460-01-2TT-612_ChlWtrSupTemp_LASP |  | 6 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 15 | J270-06-1PNL-001 | J460-01-2TT-612 | Setting | J460-01-2TT-612 - Chilled Water - Supply Temperature Calibration Mode Selection | J460-01-2TT-612_ChlWtrSupTempCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 16 | J270-06-1PNL-001 | J460-01-2TT-612 | Alarm | J460-01-2TT-612 - Chilled Water - Supply Temperature Calibration Still Active Alarm | J460-01-2TT-612_ChlWtrSupTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 17 | J270-06-1PNL-001 | J460-01-2TT-612 | Setting | J460-01-2TT-612 - Chilled Water - Supply Temperature Setpoint | J460-01-2TT-612_ChlWtrSupTempSetpoint |  | 16 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 20 | J270-06-1PNL-001 | J460-01-2TT-612 | Setting | J460-01-2TT-612 - Chilled Water - Supply Temperature Proportional Band | J460-01-2TT-612_ChlWtrSupTemp_Set_P |  | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 21 | J270-06-1PNL-001 | J460-01-2TT-612 | Setting | J460-01-2TT-612 - Chilled Water - Supply Temperature Integral Time | J460-01-2TT-612_ChlWtrSupTemp_Set_I |  | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 22 | J270-06-1PNL-001 | J460-01-2TT-612 | Setting | J460-01-2TT-612 - Chilled Water - Supply Temperature Derivative Time | J460-01-2TT-612_ChlWtrSupTemp_Set_D |  | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 23 | J270-06-1PNL-001 | J460-01-2TT-613 | Measurement | J460-01-2TT-613 - Chilled Water - Return Temperature | J460-01-2TT-613_ChlWtrRetTemp |  | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 24 | J270-06-1PNL-001 | J460-01-2TT-613 | Measurement | J460-01-2TT-613 - Chilled Water - Return Temperature Field | J460-01-2TT-613_ChlWtrRetTemp_Field |  | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 25 | J270-06-1PNL-001 | J460-01-2TT-613 | Alarm | J460-01-2TT-613 - Chilled Water - Return Temperature High Alarm | J460-01-2TT-613_ChlWtrRetTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 26 | J270-06-1PNL-001 | J460-01-2TT-613 | Setting | J460-01-2TT-613 - Chilled Water - Return Temperature | J460-01-2TT-613_ChlWtrRetTemp_HASP |  | - | 18.5 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 3 to State 64
1.0 | 27 | J270-06-1PNL-001 | J460-01-2TT-613 | Alarm | J460-01-2TT-613 - Chilled Water - Return Temperature Low Alarm | J460-01-2TT-613_ChlWtrRetTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 28 | J270-06-1PNL-001 | J460-01-2TT-613 | Setting | J460-01-2TT-613 - Chilled Water - Return Temperature | J460-01-2TT-613_ChlWtrRetTemp_LASP |  | 12 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 29 | J270-06-1PNL-001 | J460-01-2TT-613 | Setting | J460-01-2TT-613 - Chilled Water - Return Temperature Calibration Mode Selection | J460-01-2TT-613_ChlWtrRetTempCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 30 | J270-06-1PNL-001 | J460-01-2TT-613 | Alarm | J460-01-2TT-613 - Chilled Water - Return Temperature Calibration Still Active Alarm | J460-01-2TT-613_ChlWtrRetTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 61 | J270-06-1PNL-001 | J460-01-2FT-601 | Alarm | J460-01-2FT-601 - Chilled Water - Energy Meter Communication Failure Alarm | J460-01-2FT-601_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 62 | J270-06-1PNL-001 | J460-01-2FT-601 | Measurement | J460-01-2FT-601 - Chilled Water - Energy Meter Flow | J460-01-2FT-601_Flow |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 63 | J270-06-1PNL-001 | J460-01-2FT-601 | Measurement | J460-01-2FT-601 - Chilled Water - Energy Meter Actual Power | J460-01-2FT-601_ActPwr |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | GJ | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 64 | J270-06-1PNL-001 | J460-01-2FT-601 | Measurement | J460-01-2FT-601 - Chilled Water - Energy Meter Inlet Temperature | J460-01-2FT-601_InlTemp |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 65 | J270-06-1PNL-001 | J460-01-2FT-601 | Measurement | J460-01-2FT-601 - Chilled Water - Energy Meter Outlet Temperature | J460-01-2FT-601_OutlTemp |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 66 | J270-06-1PNL-001 | J460-01-2FT-601 | Measurement | J460-01-2FT-601 - Chilled Water - Energy Meter Differential Temperature | J460-01-2FT-601_DiffTemp |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °K | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 67 | J270-06-1PNL-001 | J460-01-2FT-601 | Measurement | J460-01-2FT-601 - Chilled Water - Energy Meter Pressure | J460-01-2FT-601_Press |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 68 | J270-06-1PNL-001 | J460-01-2FT-601 | Measurement | J460-01-2FT-601 - Chilled Water - Energy Meter Heating Energy | J460-01-2FT-601_HtgEnergy |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kWh | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 69 | J270-06-1PNL-001 | J460-01-2FT-601 | Measurement | J460-01-2FT-601 - Chilled Water - Energy Meter Cooling Energy | J460-01-2FT-601_ClgEnergy |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kWh | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 70 | J270-06-1PNL-001 | J460-01-2FT-601 | Measurement | J460-01-2FT-601 - Chilled Water - Energy Meter Volume | J460-01-2FT-601_Volume |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³ | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 71 | J270-06-1PNL-001 | J460-01-2FT-601 | Measurement | J460-01-2FT-601 - Chilled Water - Energy Meter Runtime | J460-01-2FT-601_RunTime |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 72 | J270-06-1PNL-001 | J460-01-2FT-602 | Alarm | J460-01-2FT-602 - Hot Water - Energy Meter Communication Failure Alarm | J460-01-2FT-602_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 73 | J270-06-1PNL-001 | J460-01-2FT-602 | Measurement | J460-01-2FT-602 - Hot Water - Energy Meter Flow | J460-01-2FT-602_Flow |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 74 | J270-06-1PNL-001 | J460-01-2FT-602 | Measurement | J460-01-2FT-602 - Hot Water - Energy Meter Actual Power | J460-01-2FT-602_ActPwr |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | GJ | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 75 | J270-06-1PNL-001 | J460-01-2FT-602 | Measurement | J460-01-2FT-602 - Hot Water - Energy Meter Inlet Temperature | J460-01-2FT-602_InlTemp |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 76 | J270-06-1PNL-001 | J460-01-2FT-602 | Measurement | J460-01-2FT-602 - Hot Water - Energy Meter Outlet Temperature | J460-01-2FT-602_OutlTemp |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 77 | J270-06-1PNL-001 | J460-01-2FT-602 | Measurement | J460-01-2FT-602 - Hot Water - Energy Meter Differential Temperature | J460-01-2FT-602_DiffTemp |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °K | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 78 | J270-06-1PNL-001 | J460-01-2FT-602 | Measurement | J460-01-2FT-602 - Hot Water - Energy Meter Pressure | J460-01-2FT-602_Press |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 79 | J270-06-1PNL-001 | J460-01-2FT-602 | Measurement | J460-01-2FT-602 - Hot Water - Energy Meter Heating Energy | J460-01-2FT-602_HtgEnergy |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kWh | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 80 | J270-06-1PNL-001 | J460-01-2FT-602 | Measurement | J460-01-2FT-602 - Hot Water - Energy Meter Cooling Energy | J460-01-2FT-602_ClgEnergy |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kWh | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 81 | J270-06-1PNL-001 | J460-01-2FT-602 | Measurement | J460-01-2FT-602 - Hot Water - Energy Meter Volume | J460-01-2FT-602_Volume |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³ | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 82 | J270-06-1PNL-001 | J460-01-2FT-602 | Measurement | J460-01-2FT-602 - Hot Water - Energy Meter Runtime | J460-01-2FT-602_RunTime |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 107 | J270-06-1PNL-001 | J460-01-2TT-616 | Measurement | J460-01-2TT-616 - 61LBK3 - Return Air Temperature | J460-01-2TT-616_RetAirTemp |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 108 | J270-06-1PNL-001 | J460-01-2TT-616 | Measurement | J460-01-2TT-616 - 61LBK3 - Return Air Temperature Field | J460-01-2TT-616_RetAirTemp_Field |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 109 | J270-06-1PNL-001 | J460-01-2TT-616 | Alarm | J460-01-2TT-616 - 61LBK3 - Return Air Temperature High Alarm | J460-01-2TT-616_RetAirTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 110 | J270-06-1PNL-001 | J460-01-2TT-616 | Setting | J460-01-2TT-616 - 61LBK3 - Return Air Temperature | J460-01-2TT-616_RetAirTemp_HASP |  | - | 26 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 111 | J270-06-1PNL-001 | J460-01-2TT-616 | Alarm | J460-01-2TT-616 - 61LBK3 - Return Air Temperature Low Alarm | J460-01-2TT-616_RetAirTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 112 | J270-06-1PNL-001 | J460-01-2TT-616 | Setting | J460-01-2TT-616 - 61LBK3 - Return Air Temperature | J460-01-2TT-616_RetAirTemp_LASP |  | 16 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 113 | J270-06-1PNL-001 | J460-01-2TT-616 | Setting | J460-01-2TT-616 - 61LBK3 - Return Air Temperature Calibration Mode Selection | J460-01-2TT-616_RetAirTempCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 114 | J270-06-1PNL-001 | J460-01-2TT-616 | Alarm | J460-01-2TT-616 - 61LBK3 - Return Air Temperature Calibration Still Active Alarm | J460-01-2TT-616_RetAirTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 99 | J270-06-1PNL-001 | J460-01-2TT-614 | Measurement | J460-01-2TT-614 - 61LBK3 - Supply Air Temperature | J460-01-2TT-614_SupAirTemp |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 100 | J270-06-1PNL-001 | J460-01-2TT-614 | Measurement | J460-01-2TT-614 - 61LBK3 - Supply Air Temperature Field | J460-01-2TT-614_SupAirTemp_Field |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 101 | J270-06-1PNL-001 | J460-01-2TT-614 | Alarm | J460-01-2TT-614 - 61LBK3 - Supply Air Temperature High Alarm | J460-01-2TT-614_SupAirTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 102 | J270-06-1PNL-001 | J460-01-2TT-614 | Setting | J460-01-2TT-614 - 61LBK3 - Supply Air Temperature | J460-01-2TT-614_SupAirTemp_HASP |  | - | 21 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 103 | J270-06-1PNL-001 | J460-01-2TT-614 | Alarm | J460-01-2TT-614 - 61LBK3 - Supply Air Temperature Low Alarm | J460-01-2TT-614_SupAirTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 104 | J270-06-1PNL-001 | J460-01-2TT-614 | Setting | J460-01-2TT-614 - 61LBK3 - Supply Air Temperature | J460-01-2TT-614_SupAirTemp_LASP |  | 15 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 105 | J270-06-1PNL-001 | J460-01-2TT-614 | Setting | J460-01-2TT-614 - 61LBK3 - Supply Air Temperature Calibration Mode Selection | J460-01-2TT-614_SupAirTempCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 106 | J270-06-1PNL-001 | J460-01-2TT-614 | Alarm | J460-01-2TT-614 - 61LBK3 - Supply Air Temperature Calibration Still Active Alarm | J460-01-2TT-614_SupAirTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 123 | J270-06-1PNL-001 | J100-06-2TT-001 | Measurement | J100-06-2TT-001 - Potable Water - Temperature | J100-06-2TT-001_PotWtrSupTemp |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 124 | J270-06-1PNL-001 | J100-06-2TT-001 | Measurement | J100-06-2TT-001 - Potable Water - Temperature Field | J100-06-2TT-001_PotWtrSupTemp_Field |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 125 | J270-06-1PNL-001 | J100-06-2TT-001 | Alarm | J100-06-2TT-001 - Potable Water - Temperature High Alarm | J100-06-2TT-001_PotWtrSupTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 126 | J270-06-1PNL-001 | J100-06-2TT-001 | Setting | J100-06-2TT-001 - Potable Water - Temperature | J100-06-2TT-001_PotWtrSupTemp_HASP |  | - | 30 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 127 | J270-06-1PNL-001 | J100-06-2TT-001 | Alarm | J100-06-2TT-001 - Potable Water - Temperature Low Alarm | J100-06-2TT-001_PotWtrSupTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 128 | J270-06-1PNL-001 | J100-06-2TT-001 | Setting | J100-06-2TT-001 - Potable Water - Temperature | J100-06-2TT-001_PotWtrSupTemp_LASP |  | 15 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 129 | J270-06-1PNL-001 | J100-06-2TT-001 | Setting | J100-06-2TT-001 - Potable Water - Temperature Calibration Mode Selection | J100-06-2TT-001_PotWtrSupTempCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 130 | J270-06-1PNL-001 | J100-06-2TT-001 | Alarm | J100-06-2TT-001 - Potable Water - Temperature Calibration Still Active Alarm | J100-06-2TT-001_PotWtrSupTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 131 | J270-06-1PNL-001 | J100-06-2FT-001 | Alarm | J100-06-2FT-001 - Potable Water - Flow Communication Failure Alarm | J100-06-2FT-001_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 132 | J270-06-1PNL-001 | J100-06-2FT-001 | Measurement | J100-06-2FT-001 - Potable Water - Flow Fabrication Number | J100-06-2FT-001_FabNo |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 133 | J270-06-1PNL-001 | J100-06-2FT-001 | Measurement | J100-06-2FT-001 - Potable Water - Flow Cust. ID | J100-06-2FT-001_CustID |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 134 | J270-06-1PNL-001 | J100-06-2FT-001 | Measurement | J100-06-2FT-001 - Potable Water - Flow Time Point | J100-06-2FT-001_TimePt |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 135 | J270-06-1PNL-001 | J100-06-2FT-001 | Measurement | J100-06-2FT-001 - Potable Water - Flow Bat. time | J100-06-2FT-001_BatTime |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 136 | J270-06-1PNL-001 | J100-06-2FT-001 | Measurement | J100-06-2FT-001 - Potable Water - Flow Volume | J100-06-2FT-001_Vol1 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 137 | J270-06-1PNL-001 | J100-06-2FT-001 | Measurement | J100-06-2FT-001 - Potable Water - Flow Volume [l]/Next VIFE Manufacturer specific | J100-06-2FT-001_NextVIFE |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 138 | J270-06-1PNL-001 | J100-06-2FT-001 | Measurement | J100-06-2FT-001 - Potable Water - Flow Volume | J100-06-2FT-001_Vol2 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 139 | J270-06-1PNL-001 | J100-06-2FT-001 | Measurement | J100-06-2FT-001 - Potable Water - Flow Manufacturer specific data structure | J100-06-2FT-001_Data |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 140 | J270-06-1PNL-001 | J100-06-2TT-002 | Measurement | J100-06-2TT-002 - Potable Hot Water - Inlet Temperature Heater | J100-06-2TT-002_HotWtrInlTmp |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 141 | J270-06-1PNL-001 | J100-06-2TT-002 | Measurement | J100-06-2TT-002 - Potable Hot Water - Inlet Temperature Heater Field | J100-06-2TT-002_HotWtrInlTmp_Field |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 142 | J270-06-1PNL-001 | J100-06-2TT-002 | Alarm | J100-06-2TT-002 - Potable Hot Water - Inlet Temperature Heater High Alarm | J100-06-2TT-002_HotWtrInlTmpHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 143 | J270-06-1PNL-001 | J100-06-2TT-002 | Setting | J100-06-2TT-002 - Potable Hot Water - Inlet Temperature Heater | J100-06-2TT-002_HotWtrInlTmp_HASP |  | - | 35 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 144 | J270-06-1PNL-001 | J100-06-2TT-002 | Alarm | J100-06-2TT-002 - Potable Hot Water - Inlet Temperature Heater Low Alarm | J100-06-2TT-002_HotWtrInlTmpLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 145 | J270-06-1PNL-001 | J100-06-2TT-002 | Setting | J100-06-2TT-002 - Potable Hot Water - Inlet Temperature Heater | J100-06-2TT-002_HotWtrInlTmp_LASP |  | 25 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 146 | J270-06-1PNL-001 | J100-06-2TT-002 | Setting | J100-06-2TT-002 - Potable Hot Water - Inlet Temperature Heater Calibration Mode Selection | J100-06-2TT-002_HotWtrInlTmpCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 147 | J270-06-1PNL-001 | J100-06-2TT-002 | Alarm | J100-06-2TT-002 - Potable Hot Water - Inlet Temperature Heater Calibration Still Active Alarm | J100-06-2TT-002_HotWtrInlTmpCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 123 | J270-06-1PNL-001 | J130-06-2TT-001 | Measurement | J130-06-2TT-001 - Potable Water - Temperature | J130-06-2TT-001_PotWtrSupTemp |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 124 | J270-06-1PNL-001 | J130-06-2TT-001 | Measurement | J130-06-2TT-001 - Potable Water - Temperature Field | J130-06-2TT-001_PotWtrSupTemp_Field |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 125 | J270-06-1PNL-001 | J130-06-2TT-001 | Alarm | J130-06-2TT-001 - Potable Water - Temperature High Alarm | J130-06-2TT-001_PotWtrSupTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 126 | J270-06-1PNL-001 | J130-06-2TT-001 | Setting | J130-06-2TT-001 - Potable Water - Temperature | J130-06-2TT-001_PotWtrSupTemp_HASP |  | - | 30 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 127 | J270-06-1PNL-001 | J130-06-2TT-001 | Alarm | J130-06-2TT-001 - Potable Water - Temperature Low Alarm | J130-06-2TT-001_PotWtrSupTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 128 | J270-06-1PNL-001 | J130-06-2TT-001 | Setting | J130-06-2TT-001 - Potable Water - Temperature | J130-06-2TT-001_PotWtrSupTemp_LASP |  | 15 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 129 | J270-06-1PNL-001 | J130-06-2TT-001 | Setting | J130-06-2TT-001 - Potable Water - Temperature Calibration Mode Selection | J130-06-2TT-001_PotWtrSupTempCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 130 | J270-06-1PNL-001 | J130-06-2TT-001 | Alarm | J130-06-2TT-001 - Potable Water - Temperature Calibration Still Active Alarm | J130-06-2TT-001_PotWtrSupTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 174 | J270-06-1PNL-001 | J305-06-2FT-001 | Alarm | J305-06-2FT-001 - Compressed Air - Flow Meter Communication Failure Alarm | J305-06-2FT-001_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 175 | J270-06-1PNL-001 | J305-06-2FT-001 | Measurement | J305-06-2FT-001 - Compressed Air - Reset Alarm | J305-06-2FT-001_Reset |  | NORESET | RSTCNTR | RSTALM | RSTCNTR | RDISCNTR | RSTFWPRG | RAIERBIT | RAIWNBIT | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 176 | J270-06-1PNL-001 | J305-06-2FT-001 | Measurement | J305-06-2FT-001 - Compressed Air - Gas Flow Percentage | J305-06-2FT-001_FlowPerc |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 177 | J270-06-1PNL-001 | J305-06-2FT-001 | Measurement | J305-06-2FT-001 - Compressed Air - Gas Flow | J305-06-2FT-001_Flow |  | 4 | 750 | [11 empty] | - | - | - | - | - | - | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 178 | J270-06-1PNL-001 | J305-06-2FT-001 | Measurement | J305-06-2FT-001 - Compressed Air - Gas Flow Alarm | J305-06-2FT-001_Alm |  | - | ERROR | WARNING | - | MINALM | - | - | - | MAXALM | - | BCNTRALM | PWRUPALM | MSALARM | HWALARM | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 174 | J270-06-1PNL-001 | J320-06-2FT-001 | Alarm | J320-06-2FT-001 - Compressed Air - Flow Meter Communication Failure Alarm | J320-06-2FT-001_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 175 | J270-06-1PNL-001 | J320-06-2FT-001 | Measurement | J320-06-2FT-001 - Compressed Air - Reset Alarm | J320-06-2FT-001_Reset |  | NORESET | RSTCNTR | RSTALM | RSTCNTR | RDISCNTR | RSTFWPRG | RAIERBIT | RAIWNBIT | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 176 | J270-06-1PNL-001 | J320-06-2FT-001 | Measurement | J320-06-2FT-001 - Compressed Air - Gas Flow Percentage | J320-06-2FT-001_FlowPerc |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 177 | J270-06-1PNL-001 | J320-06-2FT-001 | Measurement | J320-06-2FT-001 - Compressed Air - Gas Flow | J320-06-2FT-001_Flow |  | 4 | 750 | [11 empty] | - | - | - | - | - | - | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 178 | J270-06-1PNL-001 | J320-06-2FT-001 | Measurement | J320-06-2FT-001 - Compressed Air - Gas Flow Alarm | J320-06-2FT-001_Alm |  | - | ERROR | WARNING | - | MINALM | - | - | - | MAXALM | - | BCNTRALM | PWRUPALM | MSALARM | HWALARM | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 209 | J270-06-1PNL-001 | J330-06-2FT-001 | Measurement | J330-06-2FT-001 - Nitrogen Gas - Reset Alarm | J330-06-2FT-001_Reset |  | NORESET | RSTCNTR | RSTALM | RSTCNTR | RDISCNTR | RSTFWPRG | RAIERBIT | RAIWNBIT | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 210 | J270-06-1PNL-001 | J330-06-2FT-001 | Measurement | J330-06-2FT-001 - Nitrogen Gas - Gas Flow Percentage | J330-06-2FT-001_FlowPerc |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 211 | J270-06-1PNL-001 | J330-06-2FT-001 | Measurement | J330-06-2FT-001 - Nitrogen Gas - Gas Flow | J330-06-2FT-001_Flow |  | 0.6 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 212 | J270-06-1PNL-001 | J330-06-2FT-001 | Measurement | J330-06-2FT-001 - Nitrogen Gas - Gas Flow Alarm | J330-06-2FT-001_Alm |  | - | ERROR | WARNING | - | MINALM | - | - | - | MAXALM | - | BCNTRALM | PWRUPALM | MSALARM | HWALARM | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 107 | J270-06-1PNL-001 | J460-02-2TT-608 | Measurement | J460-02-2TT-608 - 61LBK3 - Return Air Temperature | J460-02-2TT-608_RetAirTemp |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 108 | J270-06-1PNL-001 | J460-02-2TT-608 | Measurement | J460-02-2TT-608 - 61LBK3 - Return Air Temperature Field | J460-02-2TT-608_RetAirTemp_Field |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 109 | J270-06-1PNL-001 | J460-02-2TT-608 | Alarm | J460-02-2TT-608 - 61LBK3 - Return Air Temperature High Alarm | J460-02-2TT-608_RetAirTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 110 | J270-06-1PNL-001 | J460-02-2TT-608 | Setting | J460-02-2TT-608 - 61LBK3 - Return Air Temperature | J460-02-2TT-608_RetAirTemp_HASP |  | - | 26 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 111 | J270-06-1PNL-001 | J460-02-2TT-608 | Alarm | J460-02-2TT-608 - 61LBK3 - Return Air Temperature Low Alarm | J460-02-2TT-608_RetAirTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 112 | J270-06-1PNL-001 | J460-02-2TT-608 | Setting | J460-02-2TT-608 - 61LBK3 - Return Air Temperature | J460-02-2TT-608_RetAirTemp_LASP |  | 16 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 113 | J270-06-1PNL-001 | J460-02-2TT-608 | Setting | J460-02-2TT-608 - 61LBK3 - Return Air Temperature Calibration Mode Selection | J460-02-2TT-608_RetAirTempCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 114 | J270-06-1PNL-001 | J460-02-2TT-608 | Alarm | J460-02-2TT-608 - 61LBK3 - Return Air Temperature Calibration Still Active Alarm | J460-02-2TT-608_RetAirTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 99 | J270-06-1PNL-001 | J460-02-2TT-607 | Measurement | J460-02-2TT-607 - 61LBK3 - Supply Air Temperature | J460-02-2TT-607_SupAirTemp |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 100 | J270-06-1PNL-001 | J460-02-2TT-607 | Measurement | J460-02-2TT-607 - 61LBK3 - Supply Air Temperature Field | J460-02-2TT-607_SupAirTemp_Field |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 101 | J270-06-1PNL-001 | J460-02-2TT-607 | Alarm | J460-02-2TT-607 - 61LBK3 - Supply Air Temperature High Alarm | J460-02-2TT-607_SupAirTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 102 | J270-06-1PNL-001 | J460-02-2TT-607 | Setting | J460-02-2TT-607 - 61LBK3 - Supply Air Temperature | J460-02-2TT-607_SupAirTemp_HASP |  | - | 21 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 103 | J270-06-1PNL-001 | J460-02-2TT-607 | Alarm | J460-02-2TT-607 - 61LBK3 - Supply Air Temperature Low Alarm | J460-02-2TT-607_SupAirTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 104 | J270-06-1PNL-001 | J460-02-2TT-607 | Setting | J460-02-2TT-607 - 61LBK3 - Supply Air Temperature | J460-02-2TT-607_SupAirTemp_LASP |  | 15 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 105 | J270-06-1PNL-001 | J460-02-2TT-607 | Setting | J460-02-2TT-607 - 61LBK3 - Supply Air Temperature Calibration Mode Selection | J460-02-2TT-607_SupAirTempCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 106 | J270-06-1PNL-001 | J460-02-2TT-607 | Alarm | J460-02-2TT-607 - 61LBK3 - Supply Air Temperature Calibration Still Active Alarm | J460-02-2TT-607_SupAirTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 23 | J270-06-1PNL-001 | J460-01-2TT-003 | Measurement | J460-01-2TT-003 - Chilled Water - Return Temperature | J460-01-2TT-003_ChlWtrRetTemp |  | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 24 | J270-06-1PNL-001 | J460-01-2TT-003 | Measurement | J460-01-2TT-003 - Chilled Water - Return Temperature Field | J460-01-2TT-003_ChlWtrRetTemp_Field |  | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 25 | J270-06-1PNL-001 | J460-01-2TT-003 | Alarm | J460-01-2TT-003 - Chilled Water - Return Temperature High Alarm | J460-01-2TT-003_ChlWtrRetTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 26 | J270-06-1PNL-001 | J460-01-2TT-003 | Setting | J460-01-2TT-003 - Chilled Water - Return Temperature | J460-01-2TT-003_ChlWtrRetTemp_HASP |  | - | 18.5 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 3 to State 64
1.0 | 27 | J270-06-1PNL-001 | J460-01-2TT-003 | Alarm | J460-01-2TT-003 - Chilled Water - Return Temperature Low Alarm | J460-01-2TT-003_ChlWtrRetTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 28 | J270-06-1PNL-001 | J460-01-2TT-003 | Setting | J460-01-2TT-003 - Chilled Water - Return Temperature | J460-01-2TT-003_ChlWtrRetTemp_LASP |  | 12 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 29 | J270-06-1PNL-001 | J460-01-2TT-003 | Setting | J460-01-2TT-003 - Chilled Water - Return Temperature Calibration Mode Selection | J460-01-2TT-003_ChlWtrRetTempCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 30 | J270-06-1PNL-001 | J460-01-2TT-003 | Alarm | J460-01-2TT-003 - Chilled Water - Return Temperature Calibration Still Active Alarm | J460-01-2TT-003_ChlWtrRetTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 9 | J270-06-1PNL-001 | J460-01-2TT-002 | Measurement | J460-01-2TT-002 - Chilled Water - Supply Temperature | J460-01-2TT-002_ChlWtrSupTemp |  | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 10 | J270-06-1PNL-001 | J460-01-2TT-002 | Measurement | J460-01-2TT-002 - Chilled Water - Supply Temperature Field | J460-01-2TT-002_ChlWtrSupTemp_Field |  | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 11 | J270-06-1PNL-001 | J460-01-2TT-002 | Alarm | J460-01-2TT-002 - Chilled Water - Supply Temperature High Alarm | J460-01-2TT-002_ChlWtrSupTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 12 | J270-06-1PNL-001 | J460-01-2TT-002 | Setting | J460-01-2TT-002 - Chilled Water - Supply Temperature | J460-01-2TT-002_ChlWtrSupTemp_HASP |  | - | 16 | [11 empty] | - | - | - | - | - | 0.5 | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 13 | J270-06-1PNL-001 | J460-01-2TT-002 | Alarm | J460-01-2TT-002 - Chilled Water - Supply Temperature Low Alarm | J460-01-2TT-002_ChlWtrSupTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 14 | J270-06-1PNL-001 | J460-01-2TT-002 | Setting | J460-01-2TT-002 - Chilled Water - Supply Temperature | J460-01-2TT-002_ChlWtrSupTemp_LASP |  | 6 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 15 | J270-06-1PNL-001 | J460-01-2TT-002 | Setting | J460-01-2TT-002 - Chilled Water - Supply Temperature Calibration Mode Selection | J460-01-2TT-002_ChlWtrSupTempCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 16 | J270-06-1PNL-001 | J460-01-2TT-002 | Alarm | J460-01-2TT-002 - Chilled Water - Supply Temperature Calibration Still Active Alarm | J460-01-2TT-002_ChlWtrSupTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 17 | J270-06-1PNL-001 | J460-01-2TT-002 | Setting | J460-01-2TT-002 - Chilled Water - Supply Temperature Setpoint | J460-01-2TT-002_ChlWtrSupTempSetpoint |  | 16 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 20 | J270-06-1PNL-001 | J460-01-2TT-002 | Setting | J460-01-2TT-002 - Chilled Water - Supply Temperature Proportional Band | J460-01-2TT-002_ChlWtrSupTemp_Set_P |  | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 21 | J270-06-1PNL-001 | J460-01-2TT-002 | Setting | J460-01-2TT-002 - Chilled Water - Supply Temperature Integral Time | J460-01-2TT-002_ChlWtrSupTemp_Set_I |  | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 22 | J270-06-1PNL-001 | J460-01-2TT-002 | Setting | J460-01-2TT-002 - Chilled Water - Supply Temperature Derivative Time | J460-01-2TT-002_ChlWtrSupTemp_Set_D |  | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 449 | J270-06-1PNL-001 | J140-06-2FT-002 | Measurement | J140-06-2FT-002 - Demi Water - Supply Flow | J140-06-2FT-002_DmiWtrSupFlow |  | 2 | 40 | [11 empty] | - | - | - | - | - | - | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 450 | J270-06-1PNL-001 | J140-06-2FT-002 | Measurement | J140-06-2FT-002 - Demi Water - Supply Flow Field | J140-06-2FT-002_DmiWtrSupFlow_Field |  | 2 | 40 | [11 empty] | - | - | - | - | - | - | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 451 | J270-06-1PNL-001 | J140-06-2FT-002 | Alarm | J140-06-2FT-002 - Demi Water - Supply Flow High Alarm | J140-06-2FT-002_DmiWtrSupFlowHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 452 | J270-06-1PNL-001 | J140-06-2FT-002 | Setting | J140-06-2FT-002 - Demi Water - Supply Flow | J140-06-2FT-002_DmiWtrSupFlow_HASP |  | - | 30 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 453 | J270-06-1PNL-001 | J140-06-2FT-002 | Alarm | J140-06-2FT-002 - Demi Water - Supply Flow Low Alarm | J140-06-2FT-002_DmiWtrSupFlowLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 454 | J270-06-1PNL-001 | J140-06-2FT-002 | Setting | J140-06-2FT-002 - Demi Water - Supply Flow | J140-06-2FT-002_DmiWtrSupFlow_LASP |  | 10 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 455 | J270-06-1PNL-001 | J140-06-2FT-002 | Setting | J140-06-2FT-002 - Demi Water - Supply Flow Calibration Mode Selection | J140-06-2FT-002_DmiWtrSupFlowCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 456 | J270-06-1PNL-001 | J140-06-2FT-002 | Alarm | J140-06-2FT-002 - Demi Water - Supply Flow Calibration Still Active Alarm | J140-06-2FT-002_DmiWtrSupFlowCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 449 | J270-06-1PNL-001 | J140-06-2FT-001 | Measurement | J140-06-2FT-001 - Demi Water - Supply Flow | J140-06-2FT-001_DmiWtrSupFlow |  | 2 | 40 | [11 empty] | - | - | - | - | - | - | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 450 | J270-06-1PNL-001 | J140-06-2FT-001 | Measurement | J140-06-2FT-001 - Demi Water - Supply Flow Field | J140-06-2FT-001_DmiWtrSupFlow_Field |  | 2 | 40 | [11 empty] | - | - | - | - | - | - | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 451 | J270-06-1PNL-001 | J140-06-2FT-001 | Alarm | J140-06-2FT-001 - Demi Water - Supply Flow High Alarm | J140-06-2FT-001_DmiWtrSupFlowHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 452 | J270-06-1PNL-001 | J140-06-2FT-001 | Setting | J140-06-2FT-001 - Demi Water - Supply Flow | J140-06-2FT-001_DmiWtrSupFlow_HASP |  | - | 30 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 453 | J270-06-1PNL-001 | J140-06-2FT-001 | Alarm | J140-06-2FT-001 - Demi Water - Supply Flow Low Alarm | J140-06-2FT-001_DmiWtrSupFlowLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 454 | J270-06-1PNL-001 | J140-06-2FT-001 | Setting | J140-06-2FT-001 - Demi Water - Supply Flow | J140-06-2FT-001_DmiWtrSupFlow_LASP |  | 10 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 455 | J270-06-1PNL-001 | J140-06-2FT-001 | Setting | J140-06-2FT-001 - Demi Water - Supply Flow Calibration Mode Selection | J140-06-2FT-001_DmiWtrSupFlowCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 456 | J270-06-1PNL-001 | J140-06-2FT-001 | Alarm | J140-06-2FT-001 - Demi Water - Supply Flow Calibration Still Active Alarm | J140-06-2FT-001_DmiWtrSupFlowCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 23 | J270-06-1PNL-001 | J460-02-2TT-617 | Measurement | J460-02-2TT-617 - Chilled Water - Return Temperature | J460-02-2TT-617_ChlWtrRetTemp |  | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 24 | J270-06-1PNL-001 | J460-02-2TT-617 | Measurement | J460-02-2TT-617 - Chilled Water - Return Temperature Field | J460-02-2TT-617_ChlWtrRetTemp_Field |  | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 25 | J270-06-1PNL-001 | J460-02-2TT-617 | Alarm | J460-02-2TT-617 - Chilled Water - Return Temperature High Alarm | J460-02-2TT-617_ChlWtrRetTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 26 | J270-06-1PNL-001 | J460-02-2TT-617 | Setting | J460-02-2TT-617 - Chilled Water - Return Temperature | J460-02-2TT-617_ChlWtrRetTemp_HASP |  | - | 18.5 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 3 to State 64
1.0 | 27 | J270-06-1PNL-001 | J460-02-2TT-617 | Alarm | J460-02-2TT-617 - Chilled Water - Return Temperature Low Alarm | J460-02-2TT-617_ChlWtrRetTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 28 | J270-06-1PNL-001 | J460-02-2TT-617 | Setting | J460-02-2TT-617 - Chilled Water - Return Temperature | J460-02-2TT-617_ChlWtrRetTemp_LASP |  | 12 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 29 | J270-06-1PNL-001 | J460-02-2TT-617 | Setting | J460-02-2TT-617 - Chilled Water - Return Temperature Calibration Mode Selection | J460-02-2TT-617_ChlWtrRetTempCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 30 | J270-06-1PNL-001 | J460-02-2TT-617 | Alarm | J460-02-2TT-617 - Chilled Water - Return Temperature Calibration Still Active Alarm | J460-02-2TT-617_ChlWtrRetTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 9 | J270-06-1PNL-001 | J460-02-2TT-616 | Measurement | J460-02-2TT-616 - Chilled Water - Supply Temperature | J460-02-2TT-616_ChlWtrSupTemp |  | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 10 | J270-06-1PNL-001 | J460-02-2TT-616 | Measurement | J460-02-2TT-616 - Chilled Water - Supply Temperature Field | J460-02-2TT-616_ChlWtrSupTemp_Field |  | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 11 | J270-06-1PNL-001 | J460-02-2TT-616 | Alarm | J460-02-2TT-616 - Chilled Water - Supply Temperature High Alarm | J460-02-2TT-616_ChlWtrSupTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 12 | J270-06-1PNL-001 | J460-02-2TT-616 | Setting | J460-02-2TT-616 - Chilled Water - Supply Temperature | J460-02-2TT-616_ChlWtrSupTemp_HASP |  | - | 16 | [11 empty] | - | - | - | - | - | 0.5 | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 13 | J270-06-1PNL-001 | J460-02-2TT-616 | Alarm | J460-02-2TT-616 - Chilled Water - Supply Temperature Low Alarm | J460-02-2TT-616_ChlWtrSupTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 14 | J270-06-1PNL-001 | J460-02-2TT-616 | Setting | J460-02-2TT-616 - Chilled Water - Supply Temperature | J460-02-2TT-616_ChlWtrSupTemp_LASP |  | 6 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 15 | J270-06-1PNL-001 | J460-02-2TT-616 | Setting | J460-02-2TT-616 - Chilled Water - Supply Temperature Calibration Mode Selection | J460-02-2TT-616_ChlWtrSupTempCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 16 | J270-06-1PNL-001 | J460-02-2TT-616 | Alarm | J460-02-2TT-616 - Chilled Water - Supply Temperature Calibration Still Active Alarm | J460-02-2TT-616_ChlWtrSupTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 17 | J270-06-1PNL-001 | J460-02-2TT-616 | Setting | J460-02-2TT-616 - Chilled Water - Supply Temperature Setpoint | J460-02-2TT-616_ChlWtrSupTempSetpoint |  | 16 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 20 | J270-06-1PNL-001 | J460-02-2TT-616 | Setting | J460-02-2TT-616 - Chilled Water - Supply Temperature Proportional Band | J460-02-2TT-616_ChlWtrSupTemp_Set_P |  | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 21 | J270-06-1PNL-001 | J460-02-2TT-616 | Setting | J460-02-2TT-616 - Chilled Water - Supply Temperature Integral Time | J460-02-2TT-616_ChlWtrSupTemp_Set_I |  | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 22 | J270-06-1PNL-001 | J460-02-2TT-616 | Setting | J460-02-2TT-616 - Chilled Water - Supply Temperature Derivative Time | J460-02-2TT-616_ChlWtrSupTemp_Set_D |  | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64