## Frontsheet
Janssen Biologics BV Leiden
BMS Building QC Kappa - Instrument List
Document Number: J270-07-DVL-001
Version 2.0
BMS Panel : J270-07-1PNL-001
PLC: J270-07-3PLC-001, J270-07-3PLC-002

## Floormanager
IO CPNX/JACE
Version | Nr | Outstation | Device Tag | Point Descriptor | PID Nr | IO Type | Description | Power | Signal Type | Converter | Splitter | Range (Low) | Range (High) | Unit | Accuracy | Mfgr | Model | Cal Cert Req | Tech Datasheet Nr | Signal Type (CPNX/JACE) | Range (Low) (CPNX/JACE) | Range (High) (CPNX/JACE) | Unit (CPNX/JACE) | Remark (CPNX/JACE) | EBI Point Descriptor | EBI Tag | JACE Tag | Remarks | Room Number | JACE | RS485 COM | Module No | Channel No
1.0 | 1 | J270-07-1PNL-001 | J270-07-2XA-001 | J270-07-2XA-001 - J270-07-1PNL-001 - 230VAC Thermal Fault Signal | - | DI | Electrical Panel - 230VAC Thermal Fault | - | PVC | - | - | ALARM | NORMAL | - | - | Schneider Electric | iC60N | - | N/A | PVC | NORMAL | ALARM | - | INVERTED | J270-07-2XA-001 - J270-07-1PNL-001 - 230VAC Thermal Fault Signal | J270-07-2XA-001_230VACThemFlt | J270-07-2XA-001_230VACThemFlt | - |  | 1 | 1 | 1 | 1
1.0 | 2 | J270-07-1PNL-001 | J270-07-2XA-002 | J270-07-2XA-002 - J270-07-1PNL-001 - 24VDC Thermal Fault Signal | - | DI | Electrical Panel - 24VDC Thermal Fault | - | PVC | - | - | ALARM | NORMAL | - | - | Schneider Electric | iC60N | - | N/A | PVC | NORMAL | ALARM | - | INVERTED | J270-07-2XA-002 - J270-07-1PNL-001 - 24VDC Thermal Fault Signal | J270-07-2XA-002_24VDCThemFlt | J270-07-2XA-002_24VDCThemFlt | - |  | 1 | 1 | 1 | 2
1.0 | 3 | J270-07-1PNL-001 | J270-07-2XA-004 | J270-07-2XA-004 - J270-07-1PNL-001 - Surge Voltage Arrester Signal | - | DI | Electrical Panel - Surge Voltage Arrester | - | PVC | - | - | FAULT | NORMAL | - | - | Phoenix Contact | VAL-CP-MCB-1S-350/40/FM | - | N/A | PVC | NORMAL | FAULT | - | INVERTED | J270-07-2XA-004 - J270-07-1PNL-001 - Surge Voltage Arrester Signal | J270-07-2XA-004_SurgeVoltArr | J270-07-2XA-004_SurgeVoltArr | - |  | 1 | 1 | 1 | 3
1.0 | 4 | J270-07-1PNL-001 | J270-07-2XA-005 | J270-07-2XA-005 - J270-07-1PNL-001 Common Fire Alarm | - | DI | Electrical Panel - Common Fire Alarm from Fire Panel | - | PVC | - | - | ALARM | NORMAL | - | - | - | - | - | N/A | PVC | NORMAL | ALARM | - | INVERTED | J270-07-2XA-005 - J270-07-1PNL-001 Common Fire Alarm | J270-07-2XA-005_ExtFireCom | J270-07-2XA-005_ExtFireCom | - |  | 1 | 1 | 1 | 4
1.0 | 5 | J270-07-1PNL-001 | J229-07-2XA-101 | J229-07-2XA-101 - SVK-7H - Voltage Surge Arrestor | J229-07-29-01 | DI | J229-07-2XA-101 - SVK-7H - Voltage Surge Arrestor | - | PVC | - | - | FAULT | NORMAL | - | - | - | - | - | - | PVC | NORMAL | FAULT | - | INVERTED | J229-07-2XA-101 - SVK-7H - Voltage Surge Arrestor | J229-07-2XA-101_SurgeVoltArr | J229-07-2XA-101_SurgeVoltArr | - |  | 1 | 1 | 1 | 5
1.0 | 6 | J270-07-1PNL-001 | J229-07-2XA-102 | J229-07-2XA-102 - SVK-7H - Circuit Breaker Tripped | J229-07-29-01 | DI | J229-07-2XA-102 - SVK-7H - Circuit Breaker Tripped | - | PVC | - | - | ALARM | NORMAL | - | - | - | - | - | - | PVC | NORMAL | ALARM | - | INVERTED | J229-07-2XA-102 - SVK-7H - Circuit Breaker Tripped | J229-07-2XA-102_CirBrkTrip | J229-07-2XA-102_CirBrkTrip | - |  | 1 | 1 | 1 | 6
1.0 | 7 | J270-07-1PNL-001 | J229-07-2XA-103 | J229-07-2XA-103 - VK-7H-1 - Voltage Surge Arrestor | J229-07-29-02 | DI | J229-07-2XA-103 - VK-7H-1 - Voltage Surge Arrestor | - | PVC | - | - | FAULT | NORMAL | - | - | - | - | - | - | PVC | NORMAL | FAULT | - | INVERTED | J229-07-2XA-103 - VK-7H-1 - Voltage Surge Arrestor | J229-07-2XA-103_SurgeVoltArr | J229-07-2XA-103_SurgeVoltArr | - |  | 1 | 1 | 1 | 7
1.0 | 8 | J270-07-1PNL-001 | J229-07-2XA-104 | J229-07-2XA-104 - VK-7H-1 - Circuit Breaker Tripped | J229-07-29-02 | DI | J229-07-2XA-104 - VK-7H-1 - Circuit Breaker Tripped | - | PVC | - | - | ALARM | NORMAL | - | - | - | - | - | - | PVC | NORMAL | ALARM | - | INVERTED | J229-07-2XA-104 - VK-7H-1 - Circuit Breaker Tripped | J229-07-2XA-104_CirBrkTrip | J229-07-2XA-104_CirBrkTrip | - |  | 1 | 1 | 1 | 8
1.0 | 9 | J270-07-1PNL-001 | J229-07-2XA-105 | J229-07-2XA-105 - VK-7H-2 - Voltage Surge Arrestor | J229-07-29-03 | DI | J229-07-2XA-105 - VK-7H-2 - Voltage Surge Arrestor | - | PVC | - | - | FAULT | NORMAL | - | - | - | - | - | - | PVC | NORMAL | FAULT | - | INVERTED | J229-07-2XA-105 - VK-7H-2 - Voltage Surge Arrestor | J229-07-2XA-105_SurgeVoltArr | J229-07-2XA-105_SurgeVoltArr | - |  | 1 | 1 | 1 | 9
1.0 | 10 | J270-07-1PNL-001 | J229-07-2XA-106 | J229-07-2XA-106 - VK-7H-2 - Circuit Breaker Tripped | J229-07-29-03 | DI | J229-07-2XA-106 - VK-7H-2 - Circuit Breaker Tripped | - | PVC | - | - | ALARM | NORMAL | - | - | - | - | - | - | PVC | NORMAL | ALARM | - | INVERTED | J229-07-2XA-106 - VK-7H-2 - Circuit Breaker Tripped | J229-07-2XA-106_CirBrkTrip | J229-07-2XA-106_CirBrkTrip | - |  | 1 | 1 | 1 | 10
1.0 | 11 | J270-07-1PNL-001 | J229-07-2XA-107 | J229-07-2XA-107 - VK-7H-3 - Voltage Surge Arrestor | J229-07-29-04 | DI | J229-07-2XA-107 - VK-7H-3 - Voltage Surge Arrestor | - | PVC | - | - | FAULT | NORMAL | - | - | - | - | - | - | PVC | NORMAL | FAULT | - | INVERTED | J229-07-2XA-107 - VK-7H-3 - Voltage Surge Arrestor | J229-07-2XA-107_SurgeVoltArr | J229-07-2XA-107_SurgeVoltArr | - |  | 1 | 1 | 1 | 11
1.0 | 12 | J270-07-1PNL-001 | J229-07-2XA-108 | J229-07-2XA-108 - VK-7H-3 - Circuit Breaker Tripped | J229-07-29-04 | DI | J229-07-2XA-108 - VK-7H-3 - Circuit Breaker Tripped | - | PVC | - | - | ALARM | NORMAL | - | - | - | - | - | - | PVC | NORMAL | ALARM | - | INVERTED | J229-07-2XA-108 - VK-7H-3 - Circuit Breaker Tripped | J229-07-2XA-108_CirBrkTrip | J229-07-2XA-108_CirBrkTrip | - |  | 1 | 1 | 1 | 12
2 | 13 | J270-07-1PNL-001 | J229-07-2XA-109 | J229-07-2XA-109 - VK-7H-4 - Voltage Surge Arrestor | J229-07-29-05 | DI | J229-07-2XA-109 - VK-7H-4 - Voltage Surge Arrestor | - | PVC | - | - | FAULT | NORMAL | - | - | - | - | - | - | PVC | NORMAL | FAULT | - | INVERTED | J229-07-2XA-109 - VK-7H-4 - Voltage Surge Arrestor | J229-07-2XA-109_SurgeVoltArr | J229-07-2XA-109_SurgeVoltArr | - |  | 1 | 1 | 2 | 1
2 | 14 | J270-07-1PNL-001 | J229-07-2XA-110 | J229-07-2XA-110 - VK-7H-4 - Circuit Breaker Tripped | J229-07-29-05 | DI | J229-07-2XA-110 - VK-7H-4 - Circuit Breaker Tripped | - | PVC | - | - | ALARM | NORMAL | - | - | - | - | - | - | PVC | NORMAL | ALARM | - | INVERTED | J229-07-2XA-110 - VK-7H-4 - Circuit Breaker Tripped | J229-07-2XA-110_CirBrkTrip | J229-07-2XA-110_CirBrkTrip | - |  | 1 | 1 | 2 | 2
2 | 15 | J270-07-1PNL-001 | J460-02-2KS-703 | J460-02-2KS-703 - Labs Day Extension Timer - Timer | J460-02-11-06-001 | DI | Vedotec DOT-U/1, 24VDC | 24VDC | PVC | - | - | OFF | ON | - | - | Royal | DOT-U/1 | NO |  | PVC | OFF | ON | - |  | J460-02-2KS-703 - Labs Day Extension Timer - Timer | J460-02-2KS-703_DET | J460-02-2KS-703_DET |  |  | 1 | 1 | 2 | 3
2 | 16 | J270-07-1PNL-001 | J460-02-2XI-703 | J460-02-2XI-703 - Labs Day Extension Timer - Indicator | J460-02-11-06-001 | DO | Jung, LEDKO6TX24, DC 24 V | 24VDC | 24VDC | - | - | OFF | ON | - | - | Jung | LEDKO6TX24 | NO |  | 24VDC | OFF | ON | - |  | J460-02-2XI-703 - Labs Day Extension Timer - Indicator | J460-02-2XI-703_DETLamp | J460-02-2XI-703_DETLamp |  |  | 1 | 1 | 9 | 1
2 | 17 | J270-07-1PNL-001 | J460-02-2XS-703 | J460-02-2XS-703 - Labs Day Extension Timer - Enable | J460-02-11-06-001 | DO | Vedotec DOT-U/1, 24VDC | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | Royal | DOT-U/1 | NO |  | 24DC | DISABLE | ENABLE | - |  | J460-02-2XS-703 - Labs Day Extension Timer - Enable | J460-02-2XS-703_DETEna | J460-02-2XS-703_DETEna |  |  | 1 | 1 | 9 | 2
1.0 | 18 | J270-07-1PNL-001 | J229-07-1QIT-001 | J229-07-1QIT-001 - SVK-7H - Energy Meter | J229-07-29-01 | MODBUS-IP | Shnieder Electric PM8240
1.0 | 19 | J270-07-1PNL-001 | J229-07-1QIT-002 | J229-07-1QIT-002 - VK-7H-1 - Energy Meter | J229-07-29-02 | MODBUS-IP | Shnieder Electric PM8240
1.0 | 20 | J270-07-1PNL-001 | J229-07-1QIT-003 | J229-07-1QIT-003 - VK-7H-2 - Energy Meter | J229-07-29-03 | MODBUS-IP | Shnieder Electric PM8240
1.0 | 21 | J270-07-1PNL-001 | J229-07-1QIT-004 | J229-07-1QIT-004 - VK-7H-3 - Energy Meter | J229-07-29-04 | MODBUS-IP | Shnieder Electric PM8240
1.0 | 22 | J270-07-1PNL-001 | J232-07-1UPS-001 | J232-07-1UPS-001 - Parameters UPS MDF room 7th floor | J232-07-11-01 | MODBUS-IP | J232-07-1UPS-001 - Parameters UPS MDF room 7th floor
2 | 23 | J270-07-1PNL-001 | J460-01-2TT-712 | J460-01-2TT-712 - Chilled Water - Supply Temperature | J460-01-11-07-001 | AI | Rotronic TF532 Temperature sensor, 4-20mA, -40°C/60°C + 111103 + 102122 | 24VDC | 4-20mA | 500Ω | - | -40 | 60 | °C | 0.2K @ 23°C ±5°C | Rotronic | TF532-WT3X1 | NO | HM_Rotronic_TF5 | 2-10V | -40 | 60 | °C |  | J460-01-2TT-712 - Chilled Water - Supply Temperature | J460-01-2TT-712_ChlWtrSupTemp | J460-01-2TT-712_ChlWtrSupTemp |  |  | 1 | 1 | 4 | 1
2 | 24 | J270-07-1PNL-001 | J460-01-2TT-713 | J460-01-2TT-713 - Chilled Water - Return Temperature | J460-01-11-07-001 | AI | Rotronic TF532 Temperature sensor, 4-20mA, -40°C/60°C + 111103 + 102122 | 24VDC | 4-20mA | 500Ω | - | -40 | 60 | °C | 0.2K @ 23°C ±5°C | Rotronic | TF532-WT3X1 | NO | HM_Rotronic_TF5 | 2-10V | -40 | 60 | °C |  | J460-01-2TT-713 - Chilled Water - Return Temperature | J460-01-2TT-713_ChlWtrRetTemp | J460-01-2TT-713_ChlWtrRetTemp |  |  | 1 | 1 | 4 | 2
1.0 | 25 | J270-07-1PNL-001 | J460-01-2FCV-743 | J460-01-2FCV-743 - Chilled Water Valve - Control | J460-01-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  |  | 1 | 3
2.1 | 26 | J270-07-1PNL-001 | J460-01-1PMP-701 | J460-01-1PMP-701 - Chilled water Circulation pump Controller | J460-01-11-07-001 | BACNET | Grundfos Magna 3 32-120 F; CIM\CIU 300 BACnet MSTP | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  | 1 | 3
2 | 27 | J270-07-1PNL-001 | J460-01-1PMP-701 | J460-01-2XA-701 - Chilled Water Circulation Pump J460-01-1PMP-701 - Alarm | J460-01-11-07-001 | DI | Grundfos Magna 3 32-120 F | PVC | PVC | - | - | ALARM | NORMAL | - | - | Grundfos | Magna 3 32-120 F | NO | TF-W-007 | PVC | NORMAL | ALARM | - | INVERTED | J460-01-2XA-701 - Chilled Water Circulation Pump J460-01-1PMP-701 - Alarm | J460-01-2XA-701_ChlWtrCirPmpAlm | J460-01-2XA-701_ChlWtrCirPmpAlm |  |  | 1 | 1 | 2 | 4
2 | 28 | J270-07-1PNL-001 | J460-01-1PMP-701 | J460-01-2SS-701 - Chilled water Circulation pump J460-01-1PMP-701 - Status | J460-01-11-07-001 | DI | Grundfos Magna 3 32-120 F | PVC | PVC | - | - | STOP | RUN | - | - | Grundfos | Magna 3 32-120 F | NO | TF-W-007 | PVC | STOP | RUN | - | - | J460-01-2SS-701 - Chilled water Circulation pump J460-01-1PMP-701 - Status | J460-01-2SS-701_ChlWtrCirPmpSts | J460-01-2SS-701_ChlWtrCirPmpSts |  |  | 1 | 1 | 2 | 5
1.0 | 29 | J270-07-1PNL-001 | J460-01-1PMP-701 | J460-01-2SC-701 - Chilled water Circulation pump J460-01-1PMP-701 - Control Signal | J460-01-11-07-001 | AO | Grundfos Magna 3 32-120 F | - | 0-10V | - | - | 0 | 100 | % | - | Grundfos | Magna 3 32-120 F | NO | TF-W-007 | 0-10V | 0 | 100% | - | - | J460-01-2SC-701 - Chilled water Circulation pump J460-01-1PMP-701 - Control Signal | J460-01-2SC-701_ChlWtrPmpCntr | J460-01-2SC-701_ChlWtrPmpCntr |  |  | 1 | 1 | 8 | 1
2 | 30 | J270-07-1PNL-001 | J460-01-1PMP-701 | J460-01-2XS-701 - Chilled water Circulation pump J460-01-1PMP-701 - Enable | J460-01-11-07-001 | DO | Grundfos Magna 3 32-120 F | PVC | PVC | - | - | DISABLE | ENABLE | - | - | Grundfos | Magna 3 32-120 F | NO | TF-W-007 | PVC | DISABLE | ENABLE | - | - | J460-01-2XS-701 - Chilled water Circulation pump J460-01-1PMP-701 - Enable | J460-01-2XS-701_ChlWtrCirPmpEna | J460-01-2XS-701_ChlWtrCirPmpEna |  |  | 1 | 1 | 9 | 3
2 | 31 | J270-07-1PNL-001 | J460-01-1PMP-701 | J460-01-2HSI-701 - Chilled water Circulation pump J460-01-1PMP-701 - Maintenance Switch | J460-01-11-07-001 | DI | KRAUS&NAIMER KG10 T203/D-Axxx | PVC | PVC | - | - | OFF | ON | - | - | KRAUS&NAIMER | KG10 T203/D-Axxx | NO |  | PVC | OFF | ON | - | - | J460-01-2HSI-701 - Chilled water Circulation pump J460-01-1PMP-701 - Maintenance Switch | J460-01-2HSI-701_ChlWtrCirPmpMS | J460-01-2HSI-701_ChlWtrCirPmpMS |  |  | 1 | 1 | 2 | 6
1.0 | 32 | J270-07-1PNL-001 | J460-01-2FT-701 | J460-01-2FT-701 - Chilled Water - Energy Meter | J460-01-11-07-001 | BACNET | Kamstrup Multical 403 - 10 (0.6 to 10m³/h) | 24VDC | - | - | - | - | - | - | - | Kamstrup | Multical 403 - 10 | NO | TF-W-013 | - | - | - | - | - | - | - | - |  |  | 1 | 2
1.0 | 33 | J270-07-1PNL-001 | J460-01-2FT-702 | J460-01-2FT-702 - Hot Water - Energy Meter | J460-01-11-07-001 | BACNET | Kamstrup Multical 403 - 10 (0.6 to 10m³/h) | 24VDC | - | - | - | - | - | - | - | Kamstrup | Multical 403 - 10 | NO | TF-W-013 | - | - | - | - | - | - | - | - |  |  | 1 | 2
2 | 34 | J270-07-1PNL-001 | J460-01-2FT-704 | J460-01-2FT-704 - 61LBK3 - Return Air Flow | J460-01-11-07-001 | AI | CMR232, P-Sensor, LCD, 24VDC, 50Pa, Modbus | 24VDC | 4-20mA | 500Ω | - | 0 | 6100 | m³/h | ±0.25% of Full Scale | CMR Controls | 232A000P0050M12 | NO | HM_CMR_232 | 2-10V | 0 | 6100 | m³/h |  | J460-01-2FT-704 - 61LBK3 - Return Air Flow | J460-01-2FT-704_RetAirFlow | J460-01-2FT-704_RetAirFlow |  |  | 1 | 1 | 4 | 3
2 | 35 | J270-07-1PNL-001 | J460-01-2TT-714 | J460-01-2TT-714 - 61LBK3 - Return Air Temperature | J460-01-11-07-001 | AI | Rotronic HF432 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C | 24VDC | 4-20mA | 500Ω | - | 0 | 50 | °C | ±0.2°C @ 23°C | Rotronic | HF432-DB1XX1XX | NO | HM_Rotronic_HF4 | 2-10V | 0 | 50 | °C |  | J460-01-2TT-714 - 61LBK3 - Return Air Temperature | J460-01-2TT-714_RetAirTemp | J460-01-2TT-714_RetAirTemp |  |  | 1 | 1 | 4 | 4
2 | 36 | J270-07-1PNL-001 | J460-01-2FT-703 | J460-01-2FT-703 - 61LBK3 - Supply Air Flow | J460-01-11-07-001 | AI | CMR232, P-Sensor, LCD, 24VDC, 50Pa, Modbus | 24VDC | 4-20mA | 500Ω | - | 0 | 6507 | m³/h | ±0.25% of Full Scale | CMR Controls | 232A000P0050M12 | NO | HM_CMR_232 | 2-10V | 0 | 6507 | m³/h |  | J460-01-2FT-703 - 61LBK3 - Supply Air Flow | J460-01-2FT-703_SupAirFlow | J460-01-2FT-703_SupAirFlow |  |  | 1 | 1 | 4 | 5
2 | 37 | J270-07-1PNL-001 | J460-01-2TT-711 | J460-01-2TT-711 - 61LBK3 - Supply Air Temperature | J460-01-11-07-001 | AI | Rotronic HF532 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C + HC2A-S | 24VDC | 4-20mA | 500Ω | - | 0 | 50 | °C | ±0.1°C @ 23°C | Rotronic | HF532-DB1XX1XX | NO | HM_Rotronic_HF5 | 2-10V | 0 | 50 | °C |  | J460-01-2TT-711 - 61LBK3 - Supply Air Temperature | J460-01-2TT-711_SupAirTemp | J460-01-2TT-711_SupAirTemp |  |  | 1 | 1 | 4 | 6
2 | 38 | J270-07-1PNL-001 | J460-01-2MT-711 | J460-01-2MT-711 - 61LBK3 - Supply Air Humidity | J460-01-11-07-001 | AI | Rotronic HF532 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C + HC2A-S | 24VDC | 4-20mA | 500Ω | - | 0 | 100 | % | ±0.8%RH @ 23°C | Rotronic | HF532-DB1XX1XX | NO | HM_Rotronic_HF5 | 2-10V | 0 | 100 | % |  | J460-01-2MT-711 - 61LBK3 - Supply Air Humidity | J460-01-2MT-711_SupAirHum | J460-01-2MT-711_SupAirHum |  |  | 1 | 1 | 4 | 7
2 | 39 | J270-07-1PNL-001 | J460-02-2FT-702 | J460-02-2FT-702 - 61LBK2 - Return Air Flow | J460-02-11-07-001 | AI | CMR232, P-Sensor, LCD, 24VDC, 100Pa, Modbus | 24VDC | 4-20mA | 500Ω | - | 0 | 21690 | m³/h | ±0.25% of Full Scale | CMR Controls | 232A000P0100M12 | NO | HM_CMR_232 | 2-10V | 0 | 21690 | m³/h |  | J460-02-2FT-702 - 61LBK2 - Return Air Flow | J460-02-2FT-702_RetAirFlow | J460-02-2FT-702_RetAirFlow |  |  | 1 | 1 | 4 | 8
2 | 40 | J270-07-1PNL-001 | J460-02-2TT-710 | J460-02-2TT-710 - 61LBK2 - Return Air Temperature | J460-02-11-07-001 | AI | Rotronic HF432 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C | 24VDC | 4-20mA | 500Ω | - | 0 | 50 | °C | ±0.2°C @ 23°C | Rotronic | HF432-DB1XX1XX | NO | HM_Rotronic_HF4 | 2-10V | 0 | 50 | °C |  | J460-02-2TT-710 - 61LBK2 - Return Air Temperature | J460-02-2TT-710_RetAirTemp | J460-02-2TT-710_RetAirTemp |  |  | 1 | 1 | 5 | 1
2 | 41 | J270-07-1PNL-001 | J460-02-2FT-701 | J460-02-2FT-701 - 61LBK2 - Supply Air Flow | J460-02-11-07-001 | AI | CMR232, P-Sensor, LCD, 24VDC, 100Pa, Modbus | 24VDC | 4-20mA | 500Ω | - | 0 | 21690 | m³/h | ±0.25% of Full Scale | CMR Controls | 232A000P0100M12 | NO | HM_CMR_232 | 2-10V | 0 | 21690 | m³/h |  | J460-02-2FT-701 - 61LBK2 - Supply Air Flow | J460-02-2FT-701_SupAirFlow | J460-02-2FT-701_SupAirFlow |  |  | 1 | 1 | 5 | 2
2 | 42 | J270-07-1PNL-001 | J460-02-2TT-709 | J460-02-2TT-709 - 61LBK2 - Supply Air Temperature | J460-02-11-07-001 | AI | Rotronic HF532 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C + HC2A-S | 24VDC | 4-20mA | 500Ω | - | 0 | 50 | °C | ±0.1°C @ 23°C | Rotronic | HF532-DB1XX1XX | NO | HM_Rotronic_HF5 | 2-10V | 0 | 50 | °C |  | J460-02-2TT-709 - 61LBK2 - Supply Air Temperature | J460-02-2TT-709_SupAirTemp | J460-02-2TT-709_SupAirTemp |  |  | 1 | 1 | 5 | 3
2 | 43 | J270-07-1PNL-001 | J460-02-2MT-709 | J460-02-2MT-709 - 61LBK2 - Supply Air Humidity | J460-02-11-07-001 | AI | Rotronic HF532 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C + HC2A-S | 24VDC | 4-20mA | 500Ω | - | 0 | 100 | % | ±0.8%RH @ 23°C | Rotronic | HF532-DB1XX1XX | NO | HM_Rotronic_HF5 | 2-10V | 0 | 100 | % |  | J460-02-2MT-709 - 61LBK2 - Supply Air Humidity | J460-02-2MT-709_SupAirHum | J460-02-2MT-709_SupAirHum |  |  | 1 | 1 | 5 | 4
2 | 44 | J270-07-1PNL-001 | J130-07-2TT-001 | J130-07-2TT-001 - Non Potable Water - Temperature | J130-07-11-01 | AI | Rotronic TF532 Temperature sensor, 4-20mA, 0°C/50°C + 111103 + 102122 | 24VDC | 4-20mA | 500Ω | - | 0 | 50 | °C | 0.2K @ 23°C ±5°C | Rotronic | TF532-WT1X1 | NO | HM_Rotronic_TF5 | 2-10V | 0 | 50 | °C |  | J130-07-2TT-001 - Non Potable Water - Temperature | J130-07-2TT-001_NPotWtrSupTemp | J130-07-2TT-001_NPotWtrSupTemp |  |  | 1 | 1 | 5 | 5
2 | 45 | J270-07-1PNL-001 | J130-07-2PT-001 | J130-07-2PT-001 - Non Potable Water - Pressure | J130-07-11-01 | AI | SHD-I 6, 0-6Bar, 4-20mA, 24VDC | 24VDC | 4-20mA | 500Ω | - | 0 | 6 | Bar | ±0.3% | Vedotec | SHD-I 6 | NO | HM_Vedotec_SHD | 2-10V | 0 | 6 | Bar |  | J130-07-2PT-001 - Non Potable Water - Pressure | J130-07-2PT-001_NPotWtrSupPress | J130-07-2PT-001_NPotWtrSupPress |  |  | 1 | 1 | 5 | 6
2 | 46 | J270-07-1PNL-001 | J130-07-2FT-001 | J100-07-2FT-001 - Potable Water - Flow Volume | J130-07-11-01 | M-BUS | Itron M-Bus Cyble V2.0 | 24VDC | M-Bus | PW03 | - | - | - | - | - | Itron | Cyble M-Bus V2.0 | NO |  | RS-232 | - | - | - |  | - | - | - |  |  | 1 | RS-232-1
2 | 47 | J270-07-1PNL-001 | J100-07-2TT-001 | J100-07-2TT-001 - Potable Water - Temperature | J100-07-11-01 | AI | Rotronic TF532 Temperature sensor, 4-20mA, 0°C/50°C + 111103 + 102122 | 24VDC | 4-20mA | 500Ω | - | 0 | 50 | °C | 0.2K @ 23°C ±5°C | Rotronic | TF532-WT1X1 | NO | HM_Rotronic_TF5 | 2-10V | 0 | 50 | °C |  | J100-07-2TT-001 - Potable Water - Temperature | J100-07-2TT-001_PotWtrSupTemp | J100-07-2TT-001_PotWtrSupTemp |  |  | 1 | 1 | 5 | 7
2 | 48 | J270-07-1PNL-001 | J100-07-2FT-001 | J100-07-2FT-001 - Potable Water - Flow Volume | J100-07-11-01 | M-BUS | Itron M-Bus Cyble V2.0 | 24VDC | M-Bus | PW03 | - | - | - | - | - | Itron | Cyble M-Bus V2.0 | NO |  | RS-232 | - | - | - |  | - | - | - |  |  | 1 | RS-232-1
1.0 | 49 | J270-07-1PNL-001 | J305-07-2FT-001 | J305-07-2FT-001 - Compressed Air - Flow Meter | J305-07-11-01 | MODBUS-IP | Rotarex EL-FLOW, F-111AC, Modbus-TCP, 4-20mA, 24VDC | 24VDC | - | - | - | 0.6 | 100 | Ln/min | ±0,5% Rd plus ±0,1%FS; | Rotarex | F-111AC | NO | TF-W-201
1.0 | 50 | J270-07-1PNL-001 | J305-07-2PT-001 | J305-07-2PT-001 - Compressed Air - Pressure | J305-07-11-01 | AI | Wika MG-1, 24VDC, 0-16Bar, 4-20mA | 24VDC | 4-20mA | 500Ω | - | 0 | 16 | Bar | ≤2% of Span | Wika | MG-1-6-BG416-HAZ2E-AA-M4Z-AA-ZZ | NO | TF-W-206 | 2-10V | 0 | 16 | Bar |  | J305-07-2PT-001 - Compressed Air - Pressure | J305-07-2PT-001_CompAirPress | J305-07-2PT-001_CompAirPress |  |  | 1 | 1 | 5 | 8
1.0 | 51 | J270-07-1PNL-001 | J305-07-2MT-001 | J305-07-2MT-001 - Compressed Air - Dewpoint | J305-07-11-01 | AI | FA515 HTR, 24VDC, 4-20mA, 2 Wire, Modbus | 24VDC | 4-20mA | 500Ω | - | -20 | 50 | °C | ±1°C@50..-20°C,±2°C@-20..-50°C,±3°C@-50..-80°C | CS Instruments | FA515 | NO | TF-W-204 | 2-10V | -20 | 50 | °C |  | J305-07-2MT-001 - Compressed Air - Dewpoint | J305-07-2MT-001_CompAirDP | J305-07-2MT-001_CompAirDP |  |  | 1 | 1 | 6 | 1
1.0 | 52 | J270-07-1PNL-001 | J320-07-2FT-001 | J320-07-2FT-001 - Carbon Dioxide Gas - Flow Meter | J320-07-11-01 | MODBUS-IP | Rotarex EL-FLOW, F-112AC, Modbus-TCP, 4-20mA, 24VDC | 24VDC | - | - | - | 1 | 130 | Ln/min | ±0,5% Rd plus ±0,1%FS; | Rotarex | F-112AC | NO | TF-W-201
1.0 | 53 | J270-07-1PNL-001 | J320-07-2PT-001 | J320-07-2PT-001 - Carbon Dioxide Gas - Pressure | J320-07-11-01 | AI | Wika MG-1, 24VDC, 0-16Bar, 4-20mA | 24VDC | 4-20mA | 500Ω | - | 0 | 16 | Bar | ≤2% of Span | Wika | MG-1-6-BG416-HAZ2E-AA-M4Z-AA-ZZ | NO | TF-W-206 | 2-10V | 0 | 16 | Bar |  | J320-07-2PT-001 - Carbon Dioxide Gas - Pressure | J320-07-2PT-001_CO2Press | J320-07-2PT-001_CO2Press |  |  | 1 | 1 | 6 | 2
1.0 | 54 | J270-07-1PNL-001 | J330-07-2FT-001 | J330-07-2FT-001 - Nitrogen Gas - Flow Meter | J330-07-11-01 | MODBUS-IP | Rotarex EL-FLOW, F-111AC, Modbus-TCP, 4-20mA, 24VDC | 24VDC | - | - | - | 1 | 130 | Ln/min | ±0,5% Rd plus ±0,1%FS; | Rotarex | F-112AC | NO | TF-W-201
1.0 | 55 | J270-07-1PNL-001 | J330-07-2PT-001 | J330-07-2PT-001 - Nitrogen Gas - Pressure | J330-07-11-01 | AI | Wika MG-1, 24VDC, 0-16Bar, 4-20mA | 24VDC | 4-20mA | 500Ω | - | 0 | 16 | Bar | ≤2% of Span | Wika | MG-1-6-BG416-HAZ2E-AA-M4Z-AA-ZZ | NO | TF-W-206 | 2-10V | 0 | 16 | Bar |  | J330-07-2PT-001 - Nitrogen Gas - Pressure | J330-07-2PT-001_NitroPress | J330-07-2PT-001_NitroPress |  |  | 1 | 1 | 6 | 3
1.0 | 56 | J270-07-1PNL-001 | J140-07-2FT-002 | J140-07-2FT-002 - Demi Water - Return Flow | J140-07-11-01 | AI | LIQUI-VIEW Base LVB-10-AD | 24VDC | 4-20mA | 500Ω | - | 2 | 40 | L/min | ≤1% @ FS | LIQUI-VIEW Base | LVB-10 | NO | TF-W-210 | 2-10V | 2 | 40 | L/min |  | J140-07-2FT-002 - Demi Water - Return Flow | J140-07-2FT-002_DmiWtrRetFlow | J140-07-2FT-002_DmiWtrRetFlow |  |  | 1 | 1 | 6 | 4
1.0 | 57 | J270-07-1PNL-001 | J140-07-2FT-001 | J140-07-2FT-001 - Demi Water - Supply Flow | J140-07-11-01 | AI | LIQUI-VIEW Base LVB-10-AD | 24VDC | 4-20mA | 500Ω | - | 2 | 40 | L/min | ≤1% @ FS | LIQUI-VIEW Base | LVB-10 | NO | TF-W-210 | 2-10V | 2 | 40 | L/min |  | J140-07-2FT-001 - Demi Water - Supply Flow | J140-07-2FT-001_DmiWtrSupFlow | J140-07-2FT-001_DmiWtrSupFlow |  |  | 1 | 1 | 6 | 5
1.0 | 58 | J270-07-1PNL-001 | J140-07-2PT-001 | J140-07-2PT-001 - Demi Water - Inlet Pressure | J140-07-11-01 | AI | Wika MG-1, 24VDC, 0-16Bar, 4-20mA | 24VDC | 4-20mA | 500Ω | - | 0 | 16 | Bar | ≤2% of Span | Wika | MG-1-6-BG416-HAZ2E-AA-M4Z-AA-ZZ | NO | TF-W-212 | 2-10V | 0 | 16 | Bar |  | J140-07-2PT-001 - Demi Water - Inlet Pressure | J140-07-2PT-001_DmiWtrInPress | J140-07-2PT-001_DmiWtrInPress |  |  | 1 | 1 | 6 | 6
1.0 | 59 | J270-07-1PNL-001 | J140-07-2PT-002 | J140-07-2PT-002 - Demi Water - Outlet Pressure | J140-07-11-01 | AI | Wika MG-1, 24VDC, 0-16Bar, 4-20mA | 24VDC | 4-20mA | 500Ω | - | 0 | 16 | Bar | ≤2% of Span | Wika | MG-1-6-BG416-HAZ2E-AA-M4Z-AA-ZZ | NO | TF-W-212 | 2-10V | 0 | 16 | Bar |  | J140-07-2PT-002 - Demi Water - Outlet Pressure | J140-07-2PT-002_DmiWtrOutPress | J140-07-2PT-002_DmiWtrOutPress |  |  | 1 | 1 | 6 | 7
1.0 | 60 | J270-07-1PNL-001 | J140-07-2PT-003 | J140-07-2PT-003 - Demi Water - Return Pressure | J140-07-11-01 | AI | Wika MG-1, 24VDC, 0-16Bar, 4-20mA | 24VDC | 4-20mA | 500Ω | - | 0 | 16 | Bar | ≤2% of Span | Wika | MG-1-6-BG416-HAZ2E-AA-M4Z-AA-ZZ | NO | TF-W-212 | 2-10V | 0 | 16 | Bar |  | J140-07-2PT-003 - Demi Water - Return Pressure | J140-07-2PT-003_DmiWtrRetPress | J140-07-2PT-003_DmiWtrRetPress |  |  | 1 | 1 | 6 | 8
1.0 | 61 | J270-07-1PNL-001 | J140-07-2XA-001 | J140-07-2XA-001 - Demi Water Control Panel - Alarm | J140-07-11-01 | DI | TBU | PVC | PVC | - | - | ALARM | NORMAL | - | - | Grundfos | Magna 3 25-100 | NO | TF-W-007 | PVC | NORMAL | ALARM | - | INVERTED | J140-07-2XA-001 - Demi Water Control Panel - Alarm | J140-07-2XA-001_ChlWtrPmpAlm | J140-07-2XA-001_ChlWtrPmpAlm |  |  | 1 | 1 | 2 | 7
1.0 | 62 | J270-07-1PNL-001 | J140-07-2HSI-001 | J140-07-2HSI-001 - Demi Water Control Panel - Maintenance Switch | J140-07-11-01 | DI | KRAUS&NAIMER KG10 T203/D-Axxx | PVC | PVC | - | - | OFF | ON | - | - | KRAUS&NAIMER | KG10 T203/D-Axxx | NO |  | PVC | OFF | ON | - | - | J140-07-2HSI-001 - Demi Water Control Panel - Maintenance Switch | J140-07-2XA-001_ChlWtrPmpMS | J140-07-2XA-001_ChlWtrPmpMS |  |  | 1 | 1 | 2 | 8
2 | 63 | J270-07-1PNL-001 | J460-02-2TT-719 | J460-02-2TT-719 - Chilled Water - Supply Temperature | J460-02-11-07-001 | AI | Rotronic TF532 Temperature sensor, 4-20mA, -40°C/60°C + 111103 + 102122 | 24VDC | 4-20mA | 500Ω | - | -40 | 60 | °C | 0.2K @ 23°C ±5°C | Rotronic | TF532-WT3X1 | NO | HM_Rotronic_TF5 | 2-10V | -40 | 60 | °C |  | J460-02-2TT-719 - Chilled Water - Supply Temperature | J460-02-2TT-719_ChlWtrSupTemp | J460-02-2TT-719_ChlWtrSupTemp |  |  | 1 | 1 | 7 | 1
2 | 64 | J270-07-1PNL-001 | J460-02-2TT-720 | J460-02-2TT-720 - Chilled Water - Return Temperature | J460-02-11-07-001 | AI | Rotronic TF532 Temperature sensor, 4-20mA, -40°C/60°C + 111103 + 102122 | 24VDC | 4-20mA | 500Ω | - | -40 | 60 | °C | 0.2K @ 23°C ±5°C | Rotronic | TF532-WT3X1 | NO | HM_Rotronic_TF5 | 2-10V | -40 | 60 | °C |  | J460-02-2TT-720 - Chilled Water - Return Temperature | J460-02-2TT-720_ChlWtrRetTemp | J460-02-2TT-720_ChlWtrRetTemp |  |  | 1 | 1 | 7 | 2
1.0 | 65 | J270-07-1PNL-001 | J460-02-2FCV-728 | J460-02-2FCV-728 - Chilled Water Valve - Control | J460-02-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  |  | 1 | 3
2.1 | 66 | J270-07-1PNL-001 | J460-02-1PMP-701 | J460-02-1PMP-701 - Chilled water Circulation pump Controller | J460-02-11-07-001 | BACNET | Grundfos Magna 3 25-80; CIM\CIU 300 BACnet MSTP | [8 empty] | - | - | - | - | - | - | - | - | - | - | - | - |  |  | 1 | 3 | bar: PVC to -
2 | 67 | J270-07-1PNL-001 | J460-02-1PMP-701 | J460-02-2XA-701 - Chilled Water Circulation Pump J460-02-1PMP-701 - Alarm | J460-02-11-07-001 | DI | Grundfos Magna 3 25-80 | PVC | PVC | - | - | ALARM | NORMAL | - | - | Grundfos | Magna 3 25-80 | NO | TF-W-007 | PVC | NORMAL | ALARM | - | INVERTED | J460-02-2XA-701 - Chilled Water Circulation Pump J460-02-1PMP-701 - Alarm | J460-02-2XA-701_ChlWtrCirPmpAlm | J460-02-2XA-701_ChlWtrCirPmpAlm |  |  | 1 | 1 | 2 | 9
2 | 68 | J270-07-1PNL-001 | J460-02-1PMP-701 | J460-02-2SS-701 - Chilled Water Circulation Pump J460-02-1PMP-701 - Status | J460-02-11-07-001 | DI | Grundfos Magna 3 25-80 | PVC | PVC | - | - | STOP | RUN | - | - | Grundfos | Magna 3 25-80 | NO | TF-W-007 | PVC | STOP | RUN | - | - | J460-02-2SS-701 - Chilled Water Circulation Pump J460-02-1PMP-701 - Status | J460-02-2SS-701_ChlWtrCirPmpSts | J460-02-2SS-701_ChlWtrCirPmpSts |  |  | 1 | 1 | 2 | 10
2 | 69 | J270-07-1PNL-001 | J460-02-1PMP-701 | J460-02-2SC-701 - Chilled Water Circulation Pump J460-02-1PMP-701 - Control Signal | J460-02-11-07-001 | AO | Grundfos Magna 3 25-80 | - | 0-10V | - | - | 0 | 100 | % | - | Grundfos | Magna 3 25-80 | NO | TF-W-007 | 0-10V | 0 | 100% | - | - | J460-02-2SC-701 - Chilled Water Circulation Pump J460-02-1PMP-701 - Control Signal | J460-02-2SC-701_ChlWtrCirPmpSpd | J460-02-2SC-701_ChlWtrCirPmpSpd |  |  | 1 | 1 | 8 | 2
2 | 70 | J270-07-1PNL-001 | J460-02-1PMP-701 | J460-02-2XS-701 - Chilled Water Circulation Pump J460-02-1PMP-701 - Enable | J460-02-11-07-001 | DO | Grundfos Magna 3 25-80 | PVC | PVC | - | - | DISABLE | ENABLE | - | - | Grundfos | Magna 3 25-80 | NO | TF-W-007 | PVC | DISABLE | ENABLE | - | - | J460-02-2XS-701 - Chilled Water Circulation Pump J460-02-1PMP-701 - Enable | J460-02-2XS-701_ChlWtrCirPmpEna | J460-02-2XS-701_ChlWtrCirPmpEna |  |  | 1 | 1 | 9 | 4
2 | 71 | J270-07-1PNL-001 | J460-02-1PMP-701 | J460-02-2HSI-701 - Chilled Water Circulation Pump J460-02-1PMP-701 - Maintenance Switch | J460-02-11-07-001 | DI | KRAUS&NAIMER KG10 T203/D-Axxx | PVC | PVC | - | - | OFF | ON | - | - | KRAUS&NAIMER | KG10 T203/D-Axxx | NO |  | PVC | OFF | ON | - | - | J460-02-2HSI-701 - Chilled Water Circulation Pump J460-02-1PMP-701 - Maintenance Switch | J460-02-2HSI-701_ChlWtrCirPmpMS | J460-02-2HSI-701_ChlWtrCirPmpMS |  |  | 1 | 1 | 2 | 11
2 | 72 | J270-07-1PNL-001 | J460-02-2PT-901 | J460-02-2PT-901 - Exhaust Duct J460-02-2B-901 - Pressure | J460-02-11-07-001 | AI | Huba 698, 24VDC, 4-20mA, 0-1000Pa | 24VDC | 4-20mA | 500Ω | - | 0 | 1000 | Pa | ±0.7% FS @25°C | Huba | 698.0081020101 | NO | HM_Huba_698 | 2-10V | 0 | 1000 | Pa | - | J460-02-2PT-901 - Exhaust Duct J460-02-2B-901 - Pressure | J460-02-2PT-901_ExhDuctPress | J460-02-2PT-901_ExhDuctPress |  |  | 1 | 1 | 7 | 3
1.0 | 73 | J270-07-1PNL-001 | J460-02-2B-901 | J460-02-2XC-901 - Exhaust Fan J460-02-2B-901 - Control Signal | J460-02-11-07-001 | AO | Rood Fan, VRE-250-731W-1900EC-DR-090R-PPs | - | 0-10V | - | - | 0 | 100 | % | - | Mietzsch GmbH | VRE-250-731W-1900EC-DR-090R-PPs | NO | TF-W-105 | 0-10V | 0 | 100% | - | - | J460-02-2XC-901 - Exhaust Fan J460-02-2B-901 - Control Signal | J460-02-2XC-901_ExhFanCntr | J460-02-2XC-901_ExhFanCntr |  |  | 1 | 1 | 8 | 3
1.0 | 74 | J270-07-1PNL-001 | J460-02-2B-901 | J460-02-2XA-901 - Exhaust Fan J460-02-2B-901 - Alarm | J460-02-11-07-001 | DI | Rood Fan, VRE-250-731W-1900EC-DR-090R-PPs | - | PVC | - | - | ALARM | NORMAL | % | - | Mietzsch GmbH | VRE-250-731W-1900EC-DR-090R-PPs | NO | TF-W-105 | PVC | NORMAL | ALARM | - | INVERTED | J460-02-2XA-901 - Exhaust Fan J460-02-2B-901 - Alarm | J460-02-2XA-901_ExhFanAlm | J460-02-2XA-901_ExhFanAlm |  |  | 1 | 1 | 2 | 12
2 | 75 | J270-07-1PNL-001 | J460-02-2B-901 | J460-02-2HSI-901 - Exhaust Fan J460-02-2B-901 - Maintenance Switch | J460-02-11-07-001 | DI | KRAUS&NAIMER KG10 T203/D-Axxx | PVC | PVC | - | - | OFF | ON | - | - | KRAUS&NAIMER | KG10 T203/D-Axxx | NO |  | PVC | OFF | ON | - | - | J460-02-2HSI-901 - Exhaust Fan J460-02-2B-901 - Maintenance Switch | J460-02-2HSI-901_ExhFanMS | J460-02-2HSI-901_ExhFanMS |  |  | 1 | 1 | 3 | 1
2 | 76 | J270-07-1PNL-001 | J460-01-2TC-701 | J460-01-2TC-701 - Room J7.02 - Room Controller | J460-01-11-07-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - | - | - | - | - | Office - Solo Room | J7.02
1.0 | 77 | J270-07-1PNL-001 | J460-01-2FCV-701 | J460-01-2FCV-701 - Room J7.02 - Reheater Valve Control | J460-01-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.02
2 | 78 | J270-07-1PNL-001 | J460-01-2TC-702 | J460-01-2TC-702 - Room J7.03 - Room Controller | J460-01-11-07-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - | - | - | - | - | Office - Solo Room | J7.03
1.0 | 79 | J270-07-1PNL-001 | J460-01-2FCV-702 | J460-01-2FCV-702 - Room J7.03 - Reheater Valve Control | J460-01-11-07-001 | BACNET | Netherlandfs2024 | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.03
2 | 80 | J270-07-1PNL-001 | J460-01-2TC-703 | J460-01-2TC-703 - Room J7.06 - Room Controller | J460-01-11-07-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - | - | - | - | - | Office - Open Workspace | J7.06
1.0 | 81 | J270-07-1PNL-001 | J460-01-2FCV-703 | J460-01-2FCV-703 - Room J7.06 - J460-01-1ACU-701 Heating Valve Control | J460-01-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.06
1.0 | 82 | J270-07-1PNL-001 | J460-01-2FCV-704 | J460-01-2FCV-704 - Room J7.06 - J460-01-1ACU-702 Heating Valve Control | J460-01-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.06
1.0 | 83 | J270-07-1PNL-001 | J460-01-2FCV-705 | J460-01-2FCV-705 - Room J7.06 - J460-01-1ACU-703 Heating Valve Control | J460-01-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.06
1.0 | 84 | J270-07-1PNL-001 | J460-01-2FCV-706 | J460-01-2FCV-706 - Room J7.06 - J460-01-1ACU-704 Heating Valve Control | J460-01-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.06
1.0 | 85 | J270-07-1PNL-001 | J460-01-2FCV-707 | J460-01-2FCV-707 - Room J7.06 - J460-01-1ACU-701 Cooling Valve Control | J460-01-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.06
1.0 | 86 | J270-07-1PNL-001 | J460-01-2FCV-708 | J460-01-2FCV-708 - Room J7.06 - J460-01-1ACU-702 Cooling Valve Control | J460-01-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.06
1.0 | 87 | J270-07-1PNL-001 | J460-01-2FCV-709 | J460-01-2FCV-709 - Room J7.06 - J460-01-1ACU-703 Cooling Valve Control | J460-01-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.06
1.0 | 88 | J270-07-1PNL-001 | J460-01-2FCV-710 | J460-01-2FCV-710 - Room J7.06 - J460-01-1ACU-704 Cooling Valve Control | J460-01-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.06
1.0 | 89 | J270-07-1PNL-001 | J460-01-1VAV-701 | J460-01-2FC-701 - Room J7.06 - Return Air Flow Control | J460-01-11-07-001 | BACNET | TROX VAV controller BM0 | 24VDC | Bacnet | - | - | 0 | 300 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET |  | 300 | m³/h |  | - | - | - |  | J7.06
1.0 | 90 | J270-07-1PNL-001 | J460-01-1VAV-702 | J460-01-2FC-702 - Room J7.06 - Return Air Flow Control | J460-01-11-07-001 | BACNET | TROX VAV controller BM0 | 24VDC | Bacnet | - | - | 0 | 300 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET |  | 300 | m³/h |  | - | - | - |  | J7.06
1.0 | 91 | J270-07-1PNL-001 | J460-01-1VAV-703 | J460-01-2FC-703 - Room J7.06 - Supply Air Fow Control | J460-01-11-07-001 | BACNET | TROX VAV controller BM0 | 24VDC | Bacnet | - | - | 0 | 450 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET |  | 450 | m³/h |  | - | - | - |  | J7.06
1.0 | 92 | J270-07-1PNL-001 | J460-01-1VAV-704 | J460-01-2FC-704 - Room J7.06 - Return Air Flow Control | J460-01-11-07-001 | BACNET | TROX VAV controller BM0 | 24VDC | Bacnet | - | - | 0 | 250 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET |  | 250 | m³/h |  | - | - | - |  | J7.06
2 | 93 | J270-07-1PNL-001 | J460-01-2TC-704 | J460-01-2TC-704 - Room J7.04 - MDF Room Controller | J460-01-11-07-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - | - | - | - | - | Office - MDF Room | J7.04
1.0 | 94 | J270-07-1PNL-001 | J460-01-1ACU-710 | J460-01-1ACU-710 - Room J7.04 - FCU Control | J460-01-11-07-001 | BACNET | Mitsubishi Electric, Bacnet-MSTP | - | Bacnet | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | J7.04
1.0 | 95 | J270-07-1PNL-001 | J460-01-1ACU-711 | J460-01-1ACU-711 - Room J7.04 - FCU Control | J460-01-11-07-001 | BACNET | Mitsubishi Electric, Bacnet-MSTP | - | Bacnet | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | J7.04
2 | 96 | J270-07-1PNL-001 | J460-01-2TC-705 | J460-01-2TC-705 - Room J7.07 - Room Controller | J460-01-11-07-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - | - | - | - | - | Office - Small Meeting Room | J7.07
1.0 | 97 | J270-07-1PNL-001 | J460-01-2FCV-711 | J460-01-2FCV-711 - Room J7.07 - Reheater Valve Control | J460-01-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.07
1.0 | 98 | J270-07-1PNL-001 | J460-01-1VAV-705 | J460-01-2FC-705 - Room J7.07 - Supply Air Fow Control | J460-01-11-07-001 | BACNET | TROX VAV controller BM0 | 24VDC | Bacnet | - | - | 0 | 350 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET |  | 350 | m³/h |  | - | - | - |  | J7.07
1.0 | 99 | J270-07-1PNL-001 | J460-01-1VAV-706 | J460-01-2FC-706 - Room J7.07 - Return Air Flow Control | J460-01-11-07-001 | BACNET | TROX VAV controller BM0 | 24VDC | Bacnet | - | - | 0 | 350 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET |  | 350 | m³/h |  | - | - | - |  | J7.07
1.0 | 100 | J270-07-1PNL-001 | J460-01-2FCV-712 | J460-01-2FCV-712 - Room J7.06 - J460-01-1ACU-705 Heating Valve Control | J460-01-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.06
1.0 | 101 | J270-07-1PNL-001 | J460-01-2FCV-713 | J460-01-2FCV-713 - Room J7.06 - J460-01-1ACU-706 Heating Valve Control | J460-01-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.06
1.0 | 102 | J270-07-1PNL-001 | J460-01-2FCV-714 | J460-01-2FCV-714 - Room J7.06 - J460-01-1ACU-707 Heating Valve Control | J460-01-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.06
1.0 | 103 | J270-07-1PNL-001 | J460-01-2FCV-715 | J460-01-2FCV-715 - Room J7.06 - J460-01-1ACU-708 Heating Valve Control | J460-01-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.06
1.0 | 104 | J270-07-1PNL-001 | J460-01-2FCV-716 | J460-01-2FCV-716 - Room J7.06 - J460-01-1ACU-705 Cooling Valve Control | J460-01-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.06
1.0 | 105 | J270-07-1PNL-001 | J460-01-2FCV-717 | J460-01-2FCV-717 - Room J7.06 - J460-01-1ACU-706 Cooling Valve Control | J460-01-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.06
1.0 | 106 | J270-07-1PNL-001 | J460-01-2FCV-718 | J460-01-2FCV-718 - Room J7.06 - J460-01-1ACU-707 Cooling Valve Control | J460-01-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.06
1.0 | 107 | J270-07-1PNL-001 | J460-01-2FCV-719 | J460-01-2FCV-719 - Room J7.06 - J460-01-1ACU-708 Cooling Valve Control | J460-01-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.06
1.0 | 108 | J270-07-1PNL-001 | J460-01-1VAV-707 | J460-01-2FC-707 - Room J7.06 - Return Air Flow Control | J460-01-11-07-001 | BACNET | TROX VAV controller BM0 | 24VDC | Bacnet | - | - | 0 | 200 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET |  | 200 | m³/h |  | - | - | - |  | J7.06
1.0 | 109 | J270-07-1PNL-001 | J460-01-1VAV-708 | J460-01-2FC-708 - Room J7.06 - Supply Air Fow Control | J460-01-11-07-001 | BACNET | TROX VAV controller BM0 | 24VDC | Bacnet | - | - | 0 | 400 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET |  | 400 | m³/h |  | - | - | - |  | J7.06
2 | 110 | J270-07-1PNL-001 | J460-01-2TC-706 | J460-01-2TC-706 - Room J7.05 - Room Controller | J460-01-11-07-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - | - | - | - | - | Office - Focus Room | J7.05
1.0 | 111 | J270-07-1PNL-001 | J460-01-2FCV-720 | J460-01-2FCV-720 - Room J7.05 - Reheater Valve Control | J460-01-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.05
1.0 | 112 | J270-07-1PNL-001 | J460-01-1VAV-709 | J460-01-2FC-709 - Room J7.05 - Supply Air Fow Control | J460-01-11-07-001 | BACNET | TROX VAV controller BM0 | 24VDC | Bacnet | - | - | 0 | 250 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET |  | 250 | m³/h |  | - | - | - |  | J7.05
1.0 | 113 | J270-07-1PNL-001 | J460-01-1VAV-710 | J460-01-2FC-710 - Room J7.05 - Return Air Flow Control | J460-01-11-07-001 | BACNET | TROX VAV controller BM0 | 24VDC | Bacnet | - | - | 0 | 250 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET |  | 250 | m³/h |  | - | - | - |  | J7.05
1.0 | 114 | J270-07-1PNL-001 | J460-01-2FCV-721 | J460-01-2FCV-721 - Room J7.06 - J460-01-1ACU-709 Heating Valve Control | J460-01-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.06
1.0 | 115 | J270-07-1PNL-001 | J460-01-2FCV-722 | J460-01-2FCV-722 - Room J7.06 - J460-01-1ACU-709 Cooling Valve Control | J460-01-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.06
1.0 | 116 | J270-07-1PNL-001 | J460-01-1VAV-711 | J460-01-2FC-711 - Room J7.06 - Supply Air Fow Control | J460-01-11-07-001 | BACNET | TROX VAV controller BM0 | 24VDC | Bacnet | - | - | 0 | 200 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET |  | 200 | m³/h |  | - | - | - |  | J7.06
2 | 117 | J270-07-1PNL-001 | J460-01-2TC-707 | J460-01-2TC-707 - Room J7.08 - Room Controller | J460-01-11-07-002 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - | - | - | - | - | Office - Conference Room | J7.08
1.0 | 118 | J270-07-1PNL-001 | J460-01-2FCV-723 | J460-01-2FCV-723 - Room J7.08 - Reheater Valve Control | J460-01-11-07-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.08
1.0 | 119 | J270-07-1PNL-001 | J460-01-1VAV-712 | J460-01-2FC-712 - Room J7.08 - Supply Air Fow Control | J460-01-11-07-002 | BACNET | TROX VAV controller BM0 | 24VDC | Bacnet | - | - | 0 | 1150 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET |  | 1150 | m³/h |  | - | - | - |  | J7.08
1.0 | 120 | J270-07-1PNL-001 | J460-01-1VAV-713 | J460-01-2FC-713 - Room J7.08 - Return Air Flow Control | J460-01-11-07-002 | BACNET | TROX VAV controller BM0 | 24VDC | Bacnet | - | - | 0 | 1150 | m³/h | - | TROX | BM0 | NO | TF-W-111 | BACNET |  | 1150 | m³/h |  | - | - | - |  | J7.08
2 | 121 | J270-07-1PNL-001 | J460-01-2TC-708 | J460-01-2TC-708 - Room J7.09 - Room Controller | J460-01-11-07-002 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - | - | - | - | - | Office - Solo Room | J7.09
1.0 | 122 | J270-07-1PNL-001 | J460-01-2FCV-724 | J460-01-2FCV-724 - Room J7.09 - Reheater Valve Control | J460-01-11-07-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.09
2 | 123 | J270-07-1PNL-001 | J460-02-2TC-701 | J460-02-2TC-701 - Room J7.16 - Lab Controller | J460-02-11-07-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RL1644MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - Master Mix | J7.16
1.0 | 124 | J270-07-1PNL-001 | J460-02-2FCV-701 | J460-02-2FCV-701 - Room J7.16 - J460-02-1ACU-701 Cooling Valve Control | J460-02-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.16
1.0 | 125 | J270-07-1PNL-001 | J460-02-2FCV-727 | J460-02-2FCV-727 - Room J7.16 - J460-02-1ACU-702 Cooling Valve Control | J460-02-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.16
2 | 126 | J270-07-1PNL-001 | J460-02-2TC-702 | J460-02-2TC-702 - Room J7.15 - Lab Controller | J460-02-11-07-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - Sample storage & critcal reagents | J7.15
1.0 | 127 | J270-07-1PNL-001 | J460-02-2FCV-702 | J460-02-2FCV-702 - Room J7.15 - J460-02-1ACU-703 Cooling Valve Control | J460-02-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.15
1.0 | 128 | J270-07-1PNL-001 | J460-02-2FCV-703 | J460-02-2FCV-703 - Room J7.15 - J460-02-1ACU-703 Heating Valve Control | J460-02-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.15
1.0 | 129 | J270-07-1PNL-001 | J460-02-1VAV-702 | J460-02-2FC-702 - Room J7.15 - Air Fow Control (Slave VAV-701) | J460-02-11-07-001 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J7.15
2 | 130 | J270-07-1PNL-001 | J460-02-2TC-703 | J460-02-2TC-703 - Room J7.17 - Lab Controller | J460-02-11-07-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - PCR | J7.17
1.0 | 131 | J270-07-1PNL-001 | J460-02-2FCV-704 | J460-02-2FCV-704 - Room J7.17 - Reheater Valve Control | J460-02-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.07
1.0 | 132 | J270-07-1PNL-001 | J460-02-1VAV-704 | J460-02-2FC-704 - Room J7.17 - Air Fow Control (Slave VAV-703) | J460-02-11-07-001 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J7.17
1.0 | 133 | J270-07-1PNL-001 | J460-02-2FCV-705 | J460-02-2FCV-705 - Room J7.17 - Reheater Valve Control | J460-02-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.17
1.0 | 134 | J270-07-1PNL-001 | J460-02-2FCV-706 | J460-02-2FCV-706 - Room J7.17 - J460-02-1ACU-704 Cooling Valve Control | J460-02-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.17
1.0 | 135 | J270-07-1PNL-001 | J460-02-1VAV-705 | J460-02-2FC-705 - Room J7.17 - Air Fow Control (Slave VAV-706, VAV-707) | J460-02-11-07-001 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J7.17 |  |  |  | (UIO) AI1
2 | 136 | J270-07-1PNL-001 | J460-02-2TC-711 | J460-02-2TC-711 - Room J7.17 - Lab Controller | J460-02-11-07-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - PCR | J7.17
1.0 | 137 | J270-07-1PNL-001 | J460-02-2FCV-707 | J460-02-2FCV-707 - Room J7.17 - Reheater Valve Control | J460-02-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.17
1.0 | 138 | J270-07-1PNL-001 | J460-02-2FCV-708 | J460-02-2FCV-708 - Room J7.17 - J460-02-1ACU-708 Cooling Valve Control | J460-02-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.17
1.0 | 139 | J270-07-1PNL-001 | J460-02-1VAV-708 | J460-02-2FC-708 - Room J7.17 - Air Fow Control (Slave VAV-709, VAV-710, VAV-711) | J460-02-11-07-001 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J7.17
2 | 140 | J270-07-1PNL-001 | J460-02-2TC-712 | J460-02-2TC-712 - Room J7.17 - Lab Controller | J460-02-11-07-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - PCR | J7.17
1.0 | 141 | J270-07-1PNL-001 | J460-02-2FCV-709 | J460-02-2FCV-709 - Room J7.17 - Reheater Valve Control | J460-02-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.17
1.0 | 142 | J270-07-1PNL-001 | J460-02-2FCV-710 | J460-02-2FCV-710 - Room J7.17 - J460-02-1ACU-710 Cooling Valve Control | J460-02-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.17
1.0 | 143 | J270-07-1PNL-001 | J460-02-1VAV-712 | J460-02-2FC-712 - Room J7.17 - Air Fow Control (Slave VAV-713, VAV-714) | J460-02-11-07-001 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J7.17
2 | 144 | J270-07-1PNL-001 | J460-02-2TC-704 | J460-02-2TC-704 - Room J7.18 - Lab Controller | J460-02-11-07-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - Pre PCR (DNA isolation) | J7.18
1.0 | 145 | J270-07-1PNL-001 | J460-02-2FCV-711 | J460-02-2FCV-711 - Room J7.18 - Reheater Valve Control | J460-02-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.18
1.0 | 146 | J270-07-1PNL-001 | J460-02-2FCV-712 | J460-02-2FCV-712 - Room J7.18 - Reheater Valve Control | J460-02-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.18
1.0 | 147 | J270-07-1PNL-001 | J460-02-1VAV-716 | J460-02-2FC-716 - Room J7.18 - Air Fow Control (Slave VAV-715, VAV-717 to VAV-721) | J460-02-11-07-001 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J7.18
2 | 148 | J270-07-1PNL-001 | J460-02-2TC-705 | J460-02-2TC-705 - Room J7.19 - Lab Controller | J460-02-11-07-001 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - Sample storage & critcal reagents | J7.19
1.0 | 149 | J270-07-1PNL-001 | J460-02-2FCV-714 | J460-02-2FCV-714 - Room J7.19 - J460-02-1ACU-708 Cooling Valve Control | J460-02-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.19
1.0 | 150 | J270-07-1PNL-001 | J460-02-2FCV-715 | J460-02-2FCV-715 - Room J7.19 - J460-02-1ACU-708 Heating Valve Control | J460-02-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.19
2 | 151 | J270-07-1PNL-001 | J460-02-2TC-713 | J460-02-2TC-713 - Room J7.15 - Lab Controller | J460-02-11-07-002 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - Sample storage & critcal reagents | J7.15
1.0 | 152 | J270-07-1PNL-001 | J460-02-2FCV-716 | J460-02-2FCV-716 - Room J7.15 - J460-02-1ACU-709 Cooling Valve Control | J460-02-11-07-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.15
1.0 | 153 | J270-07-1PNL-001 | J460-02-2FCV-717 | J460-02-2FCV-717 - Room J7.15 - J460-02-1ACU-709 Heating Valve Control | J460-02-11-07-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.15
1.0 | 154 | J270-07-1PNL-001 | J460-02-1VAV-723 | J460-02-2FC-723 - Room J7.15 - Air Fow Control (Slave VAV-722) | J460-02-11-07-002 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J7.15 |  |  |  | (UIO) DI2
2 | 155 | J270-07-1PNL-001 | J460-02-2TC-706 | J460-02-2TC-706 - Room J7.13b - Lab Controller | J460-02-11-07-002 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - Chem/phys and next product | J7.13b
1.0 | 156 | J270-07-1PNL-001 | J460-02-2FCV-718 | J460-02-2FCV-718 - Room J7.13b - Reheater Valve Control | J460-02-11-07-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.13b
1.0 | 157 | J270-07-1PNL-001 | J460-02-1VAV-724 | J460-02-XU-724 - Room J7.13b - Fume hood | J460-02-11-07-002 | BACNET | Shneider FC700 | - | Bacnet | - | - | - | - | - | - | Shneider | FC700 | NO |  | Bacnet | - | - | - | See Profile FC700 | - | - | - |  | J7.13b
1.0 | 158 | J270-07-1PNL-001 | J460-02-2FCV-719 | J460-02-2FCV-719 - Room J7.13b - Reheater Valve Control | J460-02-11-07-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.13b
1.0 | 159 | J270-07-1PNL-001 | J460-02-2FCV-720 | J460-02-2FCV-720 - Room J7.13b - J460-02-1ACU-710 Cooling Valve Control | J460-02-11-07-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.13b
1.0 | 160 | J270-07-1PNL-001 | J460-02-1VAV-729 | J460-02-2FC-729 - Room J7.13b - Air Fow Control (Slave VAV-724 to VAV-728) | J460-02-11-07-002 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J7.13b |  |  |  | (UIO) AI1
2 | 161 | J270-07-1PNL-001 | J460-02-2TC-714 | J460-02-2TC-714 - Room J7.13b - Lab Controller | J460-02-11-07-002 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - Chem/phys and next product | J7.13b
1.0 | 162 | J270-07-1PNL-001 | J460-02-2FCV-721 | J460-02-2FCV-721 - Room J7.13b - Reheater Valve Control | J460-02-11-07-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.05
1.0 | 163 | J270-07-1PNL-001 | J460-02-2FCV-722 | J460-02-2FCV-722 - Room J7.13b - J460-02-1ACU-711 Cooling Valve Control | J460-02-11-07-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.13b
1.0 | 164 | J270-07-1PNL-001 | J460-02-1VAV-730 | J460-02-2FC-730 - Room J7.13b - Air Fow Control (Slave VAV-731, VAV-732) | J460-02-11-07-002 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J7.13
2 | 165 | J270-07-1PNL-001 | J460-02-2TC-707 | J460-02-2TC-707 - Room J7.13a - Lab Controller | J460-02-11-07-002 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - Chem/phys and next product | J7.13a
1.0 | 166 | J270-07-1PNL-001 | J460-02-2FCV-723 | J460-02-2FCV-723 - Room J7.13a - Reheater Valve Control | J460-02-11-07-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.13a
1.0 | 167 | J270-07-1PNL-001 | J460-02-1VAV-735 | J460-02-2FC-735 - Room J7.13a - Air Fow Control (Slave VAV-733, VAV-734) | J460-02-11-07-002 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J7.13a
2 | 168 | J270-07-1PNL-001 | J460-02-2TC-716 | J460-02-2TC-716 - Room J7.13a - Lab Controller | J460-02-11-07-002 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - Chem/phys and next product | J7.13a
1.0 | 169 | J270-07-1PNL-001 | J460-02-2FCV-724 | J460-02-2FCV-724 - Room J7.13a - Reheater Valve Control | J460-02-11-07-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.13a
1.0 | 170 | J270-07-1PNL-001 | J460-02-1VAV-738 | J460-02-2FC-738 - Room J7.13a - Air Fow Control (Slave VAV-736, VAV-737) | J460-02-11-07-002 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J7.13a
2 | 171 | J270-07-1PNL-001 | J460-02-2TC-717 | J460-02-2TC-717 - Room J7.11 - Lab Controller | J460-02-11-07-002 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - Chem/phys and next product | J7.11
1.0 | 172 | J270-07-1PNL-001 | J460-02-2FCV-725 | J460-02-2FCV-725 - Room J7.11 - Reheater Valve Control | J460-02-11-07-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.11
1.0 | 173 | J270-07-1PNL-001 | J460-02-1VAV-741 | J460-02-2FC-741 - Room J7.11 - Air Fow Control (Slave VAV-740) | J460-02-11-07-002 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J7.11
2 | 174 | J270-07-1PNL-001 | J460-02-2TC-718 | J460-02-2TC-718 - Room J7.11 - Lab Controller | J460-02-11-07-002 | BACNET | Honeywell Beats Unitairy Controller UNI-RS0844MSB24NM | 24VDC | - | - | - | - | - | - | - | Honeywell | UNI-RS0844MSB24NM | NO | HM_HON_BeatsController | - | - | - | - |  | - | - | - | LAB - Chem/phys and next product | J7.11
1.0 | 175 | J270-07-1PNL-001 | J460-02-2FCV-726 | J460-02-2FCV-726 - Room J7.11 - Reheater Valve Control | J460-02-11-07-002 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - |  | J7.11
1.0 | 176 | J270-07-1PNL-001 | J460-02-1VAV-743 | J460-02-2FC-743 - Room J7.11 - Air Fow Control (Slave VAV-742) | J460-02-11-07-002 | BACNET | TROX VAV controller TCU3 | 24VDC | Bacnet | - | - | - | - | - | - | TROX | TCU3 | NO | TF-W-110 | Bacnet | - | - | - | See Profile TCU3 | - | - | - | - | J7.11

## RoomControllers
Version | Nr | Outstation | Device Tag | Point Descriptor | PID Nr | IO Type | Description | Power | Signal Type | Converter | Splitter | Range (Low) | Range (High) | Unit | Accuracy | Mfgr | Model | Cal Cert Req | Tech Datasheet Nr | Signal Type (CPNX/JACE) | Range (Low) (CPNX/JACE) | Range (High) (CPNX/JACE) | Unit (CPNX/JACE) | Remark (CPNX/JACE) | EBI Point Descriptor | EBI Tag | JACE Tag | Remarks | Room Number | JACE | RS485 COM | Module No | Channel No
1.0 | 1 | J460-01-1CP-701 | J460-01-2TT-701 | J460-01-2TT-701 - Room J7.02 - Temperature | J460-01-11-07-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 52 | °C | ±0.2°C @25°C | Honeywell | TR42-H | NO | HM_HON_TR4X | SYLK | 0 | 52 | °C |  | J460-01-2TT-701 - Room J7.02 - Temperature | J460-01-2TT-701_RmTemp | J460-01-2TT-701_RmTemp | - | J7.02 | - | - | -
1.0 | 2 | J460-01-1CP-701 | J460-01-2MT-701 | J460-01-2MT-701 - Room J7.02 - Humidity | J460-01-11-07-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 100 | %RH | ±3%RH from 20 to 80%RH | Honeywell | TR42-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | %RH |  | J460-01-2MT-701 - Room J7.02 - Humidity | J460-01-2MT-701_RmHum | J460-01-2MT-701_RmHum | - | J7.02 | - | - | -
1.0 | 3 | J460-01-1CP-701 | J460-01-2XT-709 | J460-01-2XT-709 - Room J7.02 - Occupied | J460-01-11-07-001 | (UIO) DI | PIR 360°, 24VDC, ON/OFF Delay | 24VDC | PVC | - | - | UNOCC | OCC | - | - | Betec | PIR-TF-25-360 | NO | HM_Betec_PIR-TF-25-360 | PVC | UNOCC | OCC | - |  | J460-01-2XT-709 - Room J7.02 - Occupied | J460-01-2XT-709_RmOCC | J460-01-2XT-709_RmOCC | - | J7.02 | - | - | - | (UIO) DI1
1.0 | 4 | J460-01-1CP-702 | J460-01-2TT-702 | J460-01-2TT-702 - Room J7.03 - Temperature | J460-01-11-07-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 52 | °C | ±0.2°C @25°C | Honeywell | TR42-H | NO | HM_HON_TR4X | SYLK | 0 | 52 | °C |  | J460-01-2TT-702 - Room J7.03 - Temperature | J460-01-2TT-702_RmTemp | J460-01-2TT-702_RmTemp | - | J7.03 | - | - | -
1.0 | 5 | J460-01-1CP-702 | J460-01-2MT-702 | J460-01-2MT-702 - Room J7.03 - Humidity | J460-01-11-07-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 100 | %RH | ±3%RH from 20 to 80%RH | Honeywell | TR42-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | %RH |  | J460-01-2MT-702 - Room J7.03 - Humidity | J460-01-2MT-702_RmHum | J460-01-2MT-702_RmHum | - | J7.03 | - | - | -
1.0 | 6 | J460-01-1CP-702 | J460-01-2XT-710 | J460-01-2XT-710 - Room J7.03 - Occupied | J460-01-11-07-001 | (UIO) DI | PIR 360°, 24VDC, ON/OFF Delay | 24VDC | PVC | - | - | UNOCC | OCC | - | - | Betec | PIR-TF-25-360 | NO | HM_Betec_PIR-TF-25-360 | PVC | UNOCC | OCC | - |  | J460-01-2XT-710 - Room J7.03 - Occupied | J460-01-2XT-710_RmOCC | J460-01-2XT-710_RmOCC | - | J7.03 | - | - | - | (UIO) DI1
1.0 | 7 | J460-01-1CP-703 | J460-01-2TT-703 | J460-01-2TT-703 - Room J7.06 - Temperature | J460-01-11-07-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 52 | °C | ±0.2°C @25°C | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 52 | °C |  | J460-01-2TT-703 - Room J7.06 - Temperature | J460-01-2TT-703_RmTemp | J460-01-2TT-703_RmTemp | - | J7.06 | - | - | -
1.0 | 8 | J460-01-1CP-703 | J460-01-2MT-703 | J460-01-2MT-703 - Room J7.06 - Humidity | J460-01-11-07-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 100 | %RH | ±3%RH from 20 to 80%RH | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 100 | %RH |  | J460-01-2MT-703 - Room J7.06 - Humidity | J460-01-2MT-703_RmHum | J460-01-2MT-703_RmHum | - | J7.06 | - | - | -
1.0 | 9 | J460-01-1CP-703 | J460-01-2XT-703 | J460-01-2XT-703 - Room J7.06 - CO2 Concentration | J460-01-11-07-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 2000 | ppm | ±30ppm + 3% Measured value | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 2000 | ppm |  | J460-01-2XT-703 - Room J7.06 - CO2 Concentration | J460-01-2XT-703_RmCO2 | J460-01-2XT-703_RmCO2 | - | J7.06 | - | - | -
1.0 | 10 | J460-01-1CP-703 | J460-01-2XT-711 | J460-01-2XT-711 - Room J7.06 - Occupied | J460-01-11-07-001 | (UIO) DI | PIR 360°, 24VDC, ON/OFF Delay | 24VDC | PVC | - | - | UNOCC | OCC | - | - | Betec | PIR-TF-25-360 | NO | HM_Betec_PIR-TF-25-360 | PVC | UNOCC | OCC | - |  | J460-01-2XT-711 - Room J7.06 - Occupied | J460-01-2XT-711_RmOCC | J460-01-2XT-711_RmOCC | - | J7.06 | - | - | - | (UIO) DI1
2 | 11 | J460-01-1CP-704 | J460-01-2TT-704 | J460-01-2TT-704 - Room J7.04 - Temperature | J460-01-11-07-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 52 | °C | ±0.2°C @25°C | Honeywell | TR42-H | NO | HM_HON_TR4X | SYLK | 0 | 52 | °C |  | J460-01-2TT-704 - Room J7.04 - Temperature | J460-01-2TT-704_RmTemp | J460-01-2TT-704_RmTemp | - | J7.04 | - | - | -
1.0 | 12 | J460-01-1CP-704 | J460-01-2MT-704 | J460-01-2MT-704 - Room J7.04 - Humidity | J460-01-11-07-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 100 | %RH | ±3%RH from 20 to 80%RH | Honeywell | TR42-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | %RH |  | J460-01-2MT-704 - Room J7.04 - Humidity | J460-01-2MT-704_RmHum | J460-01-2MT-704_RmHum | - | J7.04 | - | - | -
1.0 | 13 | J460-01-1CP-704 | J460-01-2LA-701 | J460-01-2LA-701 - Room J7.04 - Water Leakage Detection | J460-01-11-07-001 | (UIO) DI | VEDOTEC Leakage detection PEK-SPS4 | 24VDC | PVC | - | - | ALARM | NORMAL | - | - | Vedotec | PEK-LS4 | NO | HM_Vedotec_PEK-LS4 | PVC | NORMAL | ALARM | - | INVERTED | J460-01-2LA-701 - Room J7.04 - Water Leakage Detection | J460-01-2LA-001_RmWtrLeakAlm | J460-01-2LA-001_RmWtrLeakAlm | - | J7.04 | - | - | - | (UIO) DI1
1.0 | 14 | J460-01-1CP-705 | J460-01-2TT-705 | J460-01-2TT-705 - Room J7.07 - Temperature | J460-01-11-07-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 52 | °C | ±0.2°C @25°C | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 52 | °C |  | J460-01-2TT-705 - Room J7.07 - Temperature | J460-01-2TT-705_RmTemp | J460-01-2TT-705_RmTemp | - | J7.07 | - | - | -
1.0 | 15 | J460-01-1CP-705 | J460-01-2MT-705 | J460-01-2MT-705 - Room J7.07 - Humidity | J460-01-11-07-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 100 | %RH | ±3%RH from 20 to 80%RH | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 100 | %RH |  | J460-01-2MT-705 - Room J7.07 - Humidity | J460-01-2MT-705_RmHum | J460-01-2MT-705_RmHum | - | J7.07 | - | - | -
1.0 | 16 | J460-01-1CP-705 | J460-01-2XT-705 | J460-01-2XT-705 - Room J7.07 - CO2 Concentration | J460-01-11-07-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 2000 | ppm | ±30ppm + 3% Measured value | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 2000 | ppm |  | J460-01-2XT-705 - Room J7.07 - CO2 Concentration | J460-01-2XT-705_RmCO2 | J460-01-2XT-705_RmCO2 | - | J7.07 | - | - | -
1.0 | 17 | J460-01-1CP-705 | J460-01-2XT-712 | J460-01-2XT-712 - Room J7.07 - Occupied | J460-01-11-07-001 | (UIO) DI | PIR 360°, 24VDC, ON/OFF Delay | 24VDC | PVC | - | - | UNOCC | OCC | - | - | Betec | PIR-TF-25-360 | NO | HM_Betec_PIR-TF-25-360 | PVC | UNOCC | OCC | - |  | J460-01-2XT-712 - Room J7.07 - Occupied | J460-01-2XT-712_RmOCC | J460-01-2XT-712_RmOCC | - | J7.07 | - | - | - | (UIO) DI1
1.0 | 18 | J460-01-1CP-706 | J460-01-2TT-706 | J460-01-2TT-706 - Room J7.05 - Temperature | J460-01-11-07-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 52 | wil | ±0.2°C @25°C | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 52 | °C |  | J460-01-2TT-706 - Room J7.05 - Temperature | J460-01-2TT-706_RmTemp | J460-01-2TT-706_RmTemp | - | J7.05 | - | - | -
1.0 | 19 | J460-01-1CP-706 | J460-01-2MT-706 | J460-01-2MT-706 - Room J7.05 - Humidity | J460-01-11-07-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 100 | %RH | ±3%RH from 20 to 80%RH | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 100 | %RH |  | J460-01-2MT-706 - Room J7.05 - Humidity | J460-01-2MT-706_RmHum | J460-01-2MT-706_RmHum | - | J7.05 | - | - | -
1.0 | 20 | J460-01-1CP-706 | J460-01-2XT-706 | J460-01-2XT-706 - Room J7.05 - CO2 Concentration | J460-01-11-07-001 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 2000 | ppm | ±30ppm + 3% Measured value | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 2000 | ppm |  | J460-01-2XT-706 - Room J7.05 - CO2 Concentration | J460-01-2XT-706_RmCO2 | J460-01-2XT-706_RmCO2 | - | J7.05 | - | - | -
1.0 | 21 | J460-01-1CP-706 | J460-01-2XT-713 | J460-01-2XT-713 - Room J7.05 - Occupied | J460-01-11-07-001 | (UIO) DI | PIR 360°, 24VDC, ON/OFF Delay | 24VDC | PVC | - | - | UNOCC | OCC | - | - | Betec | PIR-TF-25-360 | NO | HM_Betec_PIR-TF-25-360 | PVC | UNOCC | OCC | - |  | J460-01-2XT-713 - Room J7.05 - Occupied | J460-01-2XT-713_RmOCC | J460-01-2XT-713_RmOCC | - | J7.05 | - | - | - | (UIO) DI1
1.0 | 22 | J460-01-1CP-707 | J460-01-2TT-707 | J460-01-2TT-707 - Room J7.08 - Temperature | J460-01-11-07-002 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 52 | °C | ±0.2°C @25°C | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 52 | °C |  | J460-01-2TT-707 - Room J7.08 - Temperature | J460-01-2TT-707_RmTemp | J460-01-2TT-707_RmTemp | - | J7.08 | - | - | -
1.0 | 23 | J460-01-1CP-707 | J460-01-2MT-707 | J460-01-2MT-707 - Room J7.08 - Humidity | J460-01-11-07-002 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 100 | %RH | ±3%RH from 20 to 80%RH | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 100 | %RH |  | J460-01-2MT-707 - Room J7.08 - Humidity | J460-01-2MT-707_RmHum | J460-01-2MT-707_RmHum | - | J7.08 | - | - | -
1.0 | 24 | J460-01-1CP-707 | J460-01-2XT-707 | J460-01-2XT-707 - Room J7.08 - CO2 Concentration | J460-01-11-07-002 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 2000 | ppm | ±30ppm + 3% Measured value | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 2000 | ppm |  | J460-01-2XT-707 - Room J7.08 - CO2 Concentration | J460-01-2XT-707_RmCO2 | J460-01-2XT-707_RmCO2 | - | J7.08 | - | - | -
1.0 | 25 | J460-01-1CP-707 | J460-01-2XT-714 | J460-01-2XT-714 - Room J7.08 - Occupied | J460-01-11-07-002 | (UIO) DI | PIR 360°, 24VDC, ON/OFF Delay | 24VDC | PVC | - | - | UNOCC | OCC | - | - | Betec | PIR-TF-25-360 | NO | HM_Betec_PIR-TF-25-360 | PVC | UNOCC | OCC | - |  | J460-01-2XT-714 - Room J7.08 - Occupied | J460-01-2XT-714_RmOCC | J460-01-2XT-714_RmOCC | - | J7.08 | - | - | - | (UIO) DI1
1.0 | 26 | J460-01-1CP-708 | J460-01-2TT-708 | J460-01-2TT-708 - Room J7.09 - Temperature | J460-01-11-07-002 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 52 | °C | ±0.2°C @25°C | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 52 | °C |  | J460-01-2TT-708 - Room J7.09 - Temperature | J460-01-2TT-708_RmTemp | J460-01-2TT-708_RmTemp | - | J7.09 | - | - | -
1.0 | 27 | J460-01-1CP-708 | J460-01-2MT-708 | J460-01-2MT-708 - Room J7.09 - Humidity | J460-01-11-07-002 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 100 | %RH | ±3%RH from 20 to 80%RH | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 100 | %RH |  | J460-01-2MT-708 - Room J7.09 - Humidity | J460-01-2MT-708_RmHum | J460-01-2MT-708_RmHum | - | J7.09 | - | - | -
1.0 | 28 | J460-01-1CP-708 | J460-01-2XT-708 | J460-01-2XT-708 - Room J7.09 - CO2 Concentration | J460-01-11-07-002 | SYLK | Honeywell Wallmodule TR-42 with Sylk-bus | - | SYLK | - | - | 0 | 2000 | ppm | ±30ppm + 3% Measured value | Honeywell | TR42-H-CO2 | NO | HM_HON_TR4X | SYLK | 0 | 2000 | ppm |  | J460-01-2XT-708 - Room J7.09 - CO2 Concentration | J460-01-2XT-708_RmCO2 | J460-01-2XT-708_RmCO2 | - | J7.09 | - | - | -
1.0 | 29 | J460-01-1CP-708 | J460-01-2XT-715 | J460-01-2XT-715 - Room J7.09 - Occupied | J460-01-11-07-002 | (UIO) DI | PIR 360°, 24VDC, ON/OFF Delay | 24VDC | PVC | - | - | UNOCC | OCC | - | - | Betec | PIR-TF-25-360 | NO | HM_Betec_PIR-TF-25-360 | PVC | UNOCC | OCC | - |  | J460-01-2XT-715 - Room J7.09 - Occupied | J460-01-2XT-715_RmOCC | J460-01-2XT-715_RmOCC | - | J7.09 | - | - | - | (UIO) DI1
2 | 30 | J460-02-1CP-701 | J460-02-2TT-701 | J460-02-2TT-701 - Room J7.16 - Temperature | J460-02-11-07-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 52 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 52 | °C |  | J460-02-2TT-701 - Room J7.16 - Temperature | J460-02-2TT-701_RmTemp | J460-02-2TT-701_RmTemp | - | J7.16 | - | - | -
2 | 31 | J460-02-1CP-701 | J460-02-2MT-701 | J460-02-2MT-701 - Room J7.16 - Humidity | J460-02-11-07-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-701 - Room J7.16 - Humidity | J460-02-2MT-701_RmHum | J460-02-2MT-701_RmHum | - | J7.16 | - | - | -
1.0 | 32 | J460-02-1CP-701 | J460-02-1ACU-701 | J460-02-2SC-731 - J460-02-1ACU-701 - Speed Control | J460-02-11-07-001 | (UIO) AO | CASETTE GEKO DOUBLE, GCD1.UW0.SE5 | - | 0-10V | - | - | 0 | 100 | % | - | Flaktgroup | CASETTE GEKO DOUBLE, GCD1.UW0.SE5 | NO |  | 0-10V | 0 | 100 | % |  | J460-02-2SC-731 - J460-02-1ACU-701 - Speed Control | J460-02-2SC-731_FCUSpdCntr | J460-02-2SC-731_FCUSpdCntr | - | J7.16 | - | - | - | (UIO) AO2
1.0 | 33 | J460-02-1CP-701 | J460-02-1ACU-702 | J460-02-2SC-732 - J460-02-1ACU-702 - Speed Control | J460-02-11-07-001 | (UIO) AO | CASETTE GEKO DOUBLE, GCD1.UW0.SE5 | - | 0-10V | - | - | 0 | 100 | % | - | Flaktgroup | CASETTE GEKO DOUBLE, GCD1.UW0.SE5 | NO |  | 0-10V | 0 | 100 | % |  | J460-02-2SC-732 - J460-02-1ACU-702 - Speed Control | J460-02-2SC-732_FCUSpdCntr | J460-02-2SC-732_FCUSpdCntr | - | J7.16 | - | - | - | (UIO) AO3
2 | 34 | J460-02-1CP-702 | J460-02-2TT-702 | J460-02-2TT-702 - Room J7.15 - Temperature | J460-02-11-07-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 52 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 52 | °C |  | J460-02-2TT-702 - Room J7.15 - Temperature | J460-02-2TT-702_RmTemp | J460-02-2TT-702_RmTemp | - | J7.15 | - | - | -
2 | 35 | J460-02-1CP-702 | J460-02-2MT-702 | J460-02-2MT-702 - Room J7.15 - Humidity | J460-02-11-07-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-702 - Room J7.15 - Humidity | J460-02-2MT-702_RmHum | J460-02-2MT-702_RmHum | - | J7.15 | - | - | -
1.0 | 36 | J460-02-1CP-702 | J460-02-1ACU-703 | J460-02-2SC-733 - J460-02-1ACU-703 - Speed Control | J460-02-11-07-001 | (UIO) AO | CASETTE GEKO DOUBLE, GCD1.UWW.SE5 | - | 0-10V | - | - | 0 | 100 | % | - | Flaktgroup | CASETTE GEKO DOUBLE, GCD1.UWW.SE5 | NO |  | 0-10V | 0 | 100 | % |  | J460-02-2SC-733 - J460-02-1ACU-703 - Speed Control | J460-02-2SC-733_FCUSpdCntr | J460-02-2SC-733_FCUSpdCntr | - | J7.15 | - | - | - | (UIO) AO3
2 | 37 | J460-02-1CP-703 | J460-02-2TT-703 | J460-02-2TT-703 - Room J7.17 - Temperature | J460-02-11-07-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 52 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 52 | °C |  | J460-02-2TT-703 - Room J7.17 - Temperature | J460-02-2TT-703_RmTemp | J460-02-2TT-703_RmTemp | - | J7.17 | - | - | -
2 | 38 | J460-02-1CP-703 | J460-02-2MT-703 | J460-02-2MT-703 - Room J7.17 - Humidity | J460-02-11-07-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-703 - Room J7.17 - Humidity | J460-02-2MT-703_RmHum | J460-02-2MT-703_RmHum | - | J7.17 | - | - | -
2 | 39 | J460-02-1CP-703 | J460-02-1ACU-704 | J460-02-2SC-734 - J460-02-1ACU-704 - Speed Control | J460-02-11-07-001 | (UIO) AO | HYPOPOWER GEKO, GH22.UW03.SE0C2 | - | 0-10V | - | - | 0 | 100 | % | - | Flaktgroup | HYPOPOWER GEKO, GH22.UW03.SE0C2 | NO |  | 0-10V | 0 | 100 | % |  | J460-02-2SC-734 - J460-02-1ACU-704 - Speed Control | J460-02-2SC-734_FCUSpdCntr | J460-02-2SC-734_FCUSpdCntr | - | J7.17 | - | - | - | (UIO) AO3
2 | 40 | J460-02-1CP-703 | J460-02-1ACU-704 | J460-02-2XA-734 - J460-02-1ACU-704 - Alarm | J460-02-11-07-001 | (UIO) DI | HYPOPOWER GEKO, GH22.UW03.SE0C2 | - | PVC | - | - | NORMAL | ALARM | - | - | Flaktgroup | HYPOPOWER GEKO, GH22.UW03.SE0C2 | NO |  | PVC | NORMAL | ALARM | - |  | J460-02-2XA-734 - J460-02-1ACU-704 - Alarm | J460-02-2XA-734_FCUAlm | J460-02-2XA-734_FCUAlm | - | J7.17 | - | - | - | (UIO) DI2
2 | 41 | J460-02-1CP-703 | J460-02-2TT-721 | J460-02-2TT-721 - Room J7.17 - J460-02-1ACU-704 - Supply Temperature | J460-02-11-07-001 | (UIO) AI | Rotronic HF432 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0.2°C @ 23°C | Rotronic | HF432-DB1XX1XX | NO | HM_Rotronic_HF4 | 4-20mA | 0 | 50 | °C |  | J460-02-2TT-721 - Room J7.17 - J460-02-1ACU-704 - Supply Temperature | J460-02-2TT-721_SupAirTemp | J460-02-2TT-721_SupAirTemp | - | J7.17 | - | - | - | (UIO) DI2
2 | 52 | J460-02-1CP-704 | J460-02-2TT-704 | J460-02-2TT-704 - Room J7.18 - Temperature | J460-02-11-07-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 52 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 52 | °C |  | J460-02-2TT-704 - Room J7.18 - Temperature | J460-02-2TT-704_RmTemp | J460-02-2TT-704_RmTemp | - | J7.18 | - | - | -
2 | 53 | J460-02-1CP-704 | J460-02-2MT-704 | J460-02-2MT-704 - Room J7.18 - Humidity | J460-02-11-07-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-704 - Room J7.18 - Humidity | J460-02-2MT-704_RmHum | J460-02-2MT-704_RmHum | - | J7.18 | - | - | -
1.0 | 54 | J460-02-1CP-704 | J460-02-2FCV-713 | J460-02-2FCV-713 - Room J7.18 - J460-02-1ACU-707 Cooling Valve Control | J460-02-11-07-001 | BACNET | TA-Slider 160 Bacnet-MSTP, 24VAC/DC | 24VDC | Bacnet | - | - | - | - | - | - | IMI | TA-Slider 160 Bacnet | NO | HM_IMI_Slider160Bac | - | - | - | - |  | - | - | - | - | J7.18 | - | - | -
1.0 | 55 | J460-02-1CP-704 | J460-02-1ACU-707 | J460-02-2SC-737 - J460-02-1ACU-707 - Speed Control | J460-02-11-07-001 | (UIO) AO | HYPOPOWER GEKO, GH12.UW03.SE0C2 | - | 0-10V | - | - | 0 | 100 | % | - | Flaktgroup | HYPOPOWER GEKO, GH12.UW03.SE0C2 | NO |  | 0-10V | 0 | 100 | % |  | J460-02-2SC-737 - J460-02-1ACU-707 - Speed Control | J460-02-2SC-737_FCUSpdCntr | J460-02-2SC-737_FCUSpdCntr | - | J7.18 | - | - | - | (UIO) AO3
2 | 56 | J460-02-1CP-704 | J460-02-1ACU-707 | J460-02-2XA-737 - J460-02-1ACU-707 - Alarm | J460-02-11-07-001 | (UIO) DI | HYPOPOWER GEKO, GH12.UW03.SE0C2 | - | PVC | - | - | NORMAL | ALARM | - | - | Flaktgroup | HYPOPOWER GEKO, GH12.UW03.SE0C2 | NO |  | PVC | NORMAL | ALARM | - |  | J460-02-2XA-737 - J460-02-1ACU-707 - Alarm | J460-02-2XA-737_FCUAlm | J460-02-2XA-737_FCUAlm | - | J7.18 | - | - | - | (UIO) DI2
2 | 57 | J460-02-1CP-704 | J460-02-2TT-724 | J460-02-2TT-724 - Room J7.18 - J460-02-1ACU-707 - Supply Temperature | J460-02-11-07-001 | (UIO) AI | Rotronic HF432 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0.2°C @ 23°C | Rotronic | HF432-DB1XX1XX | NO | HM_Rotronic_HF4 | 4-20mA | 0 | 50 | °C |  | J460-02-2TT-724 - Room J7.18 - J460-02-1ACU-707 - Supply Temperature | J460-02-2TT-724_SupAirTemp | J460-02-2TT-724_SupAirTemp | - | J7.18 | - | - | - | (UIO) AI1
2 | 58 | J460-02-1CP-705 | J460-02-2TT-705 | J460-02-2TT-705 - Room J7.19 - Temperature | J460-02-11-07-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 52 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 52 | °C |  | J460-02-2TT-705 - Room J7.19 - Temperature | J460-02-2TT-705_RmTemp | J460-02-2TT-705_RmTemp | - | J7.19 | - | - | -
2 | 59 | J460-02-1CP-705 | J460-02-2MT-705 | J460-02-2MT-705 - Room J7.19 - Humidity | J460-02-11-07-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-705 - Room J7.19 - Humidity | J460-02-2MT-705_RmHum | J460-02-2MT-705_RmHum | - | J7.19 | - | - | -
1.0 | 60 | J460-02-1CP-705 | J460-02-1ACU-708 | J460-02-2SC-738 - J460-02-1ACU-708 - Speed Control | J460-02-11-07-001 | (UIO) AO | CASETTE GEKO DOUBLE, GCD1.UWW.SE5 | - | 0-10V | - | - | 0 | 100 | % | - | Flaktgroup | CASETTE GEKO DOUBLE, GCD1.UWW.SE5 | NO |  | 0-10V | 0 | 100 | % |  | J460-02-2SC-738 - J460-02-1ACU-708 - Speed Control | J460-02-2SC-738_FCUSpdCntr | J460-02-2SC-738_FCUSpdCntr | - | J7.19 | - | - | - | (UIO) AO3
2 | 64 | J460-02-1CP-706 | J460-02-2TT-706 | J460-02-2TT-706 - Room J7.13b - Temperature | J460-02-11-07-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 52 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 52 | °C |  | J460-02-2TT-706 - Room J7.13b - Temperature | J460-02-2TT-706_RmTemp | J460-02-2TT-706_RmTemp | - | J7.13b | - | - | -
2 | 65 | J460-02-1CP-706 | J460-02-2MT-706 | J460-02-2MT-706 - Room J7.13b - Humidity | J460-02-11-07-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-706 - Room J7.13b - Humidity | J460-02-2MT-706_RmHum | J460-02-2MT-706_RmHum | - | J7.13b | - | - | -
2 | 66 | J460-02-1CP-706 | J460-02-1ACU-710 | J460-02-2SC-740 - J460-02-1ACU-710 - Speed Control | J460-02-11-07-002 | (UIO) AO | HYPOPOWER GEKO, GH22.UW03.SE0C2 | - | 0-10V | - | - | 0 | 100 | % | - | Flaktgroup | HYPOPOWER GEKO, GH22.UW03.SE0C2 | NO |  | 0-10V | 0 | 100 | % |  | J460-02-2SC-740 - J460-02-1ACU-710 - Speed Control | J460-02-2SC-740_FCUSpdCntr | J460-02-2SC-740_FCUSpdCntr | - | J7.13b | - | - | - | (UIO) AO3
2 | 67 | J460-02-1CP-706 | J460-02-1ACU-710 | J460-02-2XA-740 - J460-02-1ACU-710 - Alarm | J460-02-11-07-002 | (UIO) DI | HYPOPOWER GEKO, GH22.UW03.SE0C2 | - | PVC | - | - | NORMAL | ALARM | - | - | Flaktgroup | HYPOPOWER GEKO, GH22.UW03.SE0C2 | NO |  | PVC | NORMAL | ALARM | - |  | J460-02-2XA-740 - J460-02-1ACU-710 - Alarm | J460-02-2XA-740_FCUAlm | J460-02-2XA-740_FCUAlm | - | J7.13b | - | - | - | (UIO) DI2
2 | 68 | J460-02-1CP-706 | J460-02-2TT-725 | J460-02-2TT-725 - Room J7.13b - J460-02-1ACU-710 - Supply Temperature | J460-02-11-07-002 | (UIO) AI | Rotronic HF432 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0.2°C @ 23°C | Rotronic | HF432-DB1XX1XX | NO | HM_Rotronic_HF4 | 4-20mA | 0 | 50 | °C |  | J460-02-2TT-725 - Room J7.13b - J460-02-1ACU-710 - Supply Temperature | J460-02-2TT-725_SupAirTemp | J460-02-2TT-725_SupAirTemp | - | J7.13b | - | - | - | (UIO) DI2
2 | 74 | J460-02-1CP-707 | J460-02-2TT-707 | J460-02-2TT-707 - Room J7.13a - Temperature | J460-02-11-07-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 52 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 52 | °C |  | J460-02-2TT-707 - Room J7.13a - Temperature | J460-02-2TT-707_RmTemp | J460-02-2TT-707_RmTemp | - | J7.13a | - | - | -
2 | 75 | J460-02-1CP-707 | J460-02-2MT-707 | J460-02-2MT-707 - Room J7.13a - Humidity | J460-02-11-07-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-707 - Room J7.13a - Humidity | J460-02-2MT-707_RmHum | J460-02-2MT-707_RmHum | - | J7.13a | - | - | -
2 | 42 | J460-02-1CP-711 | J460-02-2TT-711 | J460-02-2TT-711 - Room J7.17 - Temperature | J460-02-11-07-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 52 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 52 | °C |  | J460-02-2TT-711 - Room J7.17 - Temperature | J460-02-2TT-711_RmTemp | J460-02-2TT-711_RmTemp | - | J7.17 | - | - | -
2 | 43 | J460-02-1CP-711 | J460-02-2MT-711 | J460-02-2MT-711 - Room J7.17 - Humidity | J460-02-11-07-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-711 - Room J7.17 - Humidity | J460-02-2MT-711_RmHum | J460-02-2MT-711_RmHum | - | J7.17 | - | - | -
1.0 | 44 | J460-02-1CP-711 | J460-02-1ACU-705 | J460-02-2SC-735 - J460-02-1ACU-705 - Speed Control | J460-02-11-07-001 | (UIO) AO | HYPOPOWER GEKO, GH12.UW04.SE0C2 | - | 0-10V | - | - | 0 | 100 | % | - | Flaktgroup | HYPOPOWER GEKO, GH12.UW04.SE0C2 | NO |  | 0-10V | 0 | 100 | % |  | J460-02-2SC-735 - J460-02-1ACU-705 - Speed Control | J460-02-2SC-735_FCUSpdCntr | J460-02-2SC-735_FCUSpdCntr | - | J7.17 | - | - | - | (UIO) AO3
2 | 45 | J460-02-1CP-711 | J460-02-1ACU-705 | J460-02-2XA-735 - J460-02-1ACU-705 - Alarm | J460-02-11-07-001 | (UIO) DI | HYPOPOWER GEKO, GH12.UW04.SE0C2 | - | PVC | - | - | NORMAL | ALARM | - | - | Flaktgroup | HYPOPOWER GEKO, GH12.UW04.SE0C2 | NO |  | PVC | NORMAL | ALARM | - |  | J460-02-2XA-735 - J460-02-1ACU-705 - Alarm | J460-02-2XA-735_FCUAlm | J460-02-2XA-735_FCUAlm | - | J7.17 | - | - | - | (UIO) DI2
2 | 46 | J460-02-1CP-711 | J460-02-2TT-722 | J460-02-2TT-722 - Room J7.17 - J460-02-1ACU-705 - Supply Temperature | J460-02-11-07-001 | (UIO) AI | Rotronic HF432 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0.2°C @ 23°C | Rotronic | HF432-DB1XX1XX | NO | HM_Rotronic_HF4 | 4-20mA | 0 | 50 | °C |  | J460-02-2TT-722 - Room J7.17 - J460-02-1ACU-705 - Supply Temperature | J460-02-2TT-722_SupAirTemp | J460-02-2TT-722_SupAirTemp | - | J7.17 | - | - | - | (UIO) AI1
2 | 47 | J460-02-1CP-712 | J460-02-2TT-712 | J460-02-2TT-712 - Room J7.17 - Temperature | J460-02-11-07-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 52 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 52 | °C |  | J460-02-2TT-712 - Room J7.17 - Temperature | J460-02-2TT-712_RmTemp | J460-02-2TT-712_RmTemp | - | J7.17 | - | - | -
2 | 48 | J460-02-1CP-712 | J460-02-2MT-712 | J460-02-2MT-712 - Room J7.17 - Humidity | J460-02-11-07-001 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-712 - Room J7.17 - Humidity | J460-02-2MT-712_RmHum | J460-02-2MT-712_RmHum | - | J7.17 | - | - | -
1.0 | 49 | J460-02-1CP-712 | J460-02-1ACU-706 | J460-02-2SC-736 - J460-02-1ACU-706 - Speed Control | J460-02-11-07-001 | (UIO) AO | HYPOPOWER GEKO, GH22.UW03.SE0C2 | - | 0-10V | - | - | 0 | 100 | % | - | Flaktgroup | HYPOPOWER GEKO, GH22.UW03.SE0C2 | NO |  | 0-10V | 0 | 100 | % |  | J460-02-2SC-736 - J460-02-1ACU-706 - Speed Control | J460-02-2SC-736_FCUSpdCntr | J460-02-2SC-736_FCUSpdCntr | - | J7.17 | - | - | - | (UIO) AO3
2 | 50 | J460-02-1CP-712 | J460-02-1ACU-706 | J460-02-2XA-736 - J460-02-1ACU-706 - Alarm | J460-02-11-07-001 | (UIO) DI | HYPOPOWER GEKO, GH22.UW03.SE0C2 | - | PVC | - | - | NORMAL | ALARM | - | - | Flaktgroup | HYPOPOWER GEKO, GH22.UW03.SE0C2 | NO |  | PVC | NORMAL | ALARM | - |  | J460-02-2XA-736 - J460-02-1ACU-706 - Alarm | J460-02-2XA-736_FCUAlm | J460-02-2XA-736_FCUAlm | - | J7.17 | - | - | - | (UIO) DI2
2 | 51 | J460-02-1CP-712 | J460-02-2TT-723 | J460-02-2TT-723 - Room J7.17 - J460-02-1ACU-706 - Supply Temperature | J460-02-11-07-001 | (UIO) AI | Rotronic HF432 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0.2°C @ 23°C | Rotronic | HF432-DB1XX1XX | NO | HM_Rotronic_HF4 | 4-20mA | 0 | 50 | °C |  | J460-02-2TT-723 - Room J7.17 - J460-02-1ACU-706 - Supply Temperature | J460-02-2TT-723_SupAirTemp | J460-02-2TT-723_SupAirTemp | - | J7.17 | - | - | - | (UIO) AI1
2 | 61 | J460-02-1CP-713 | J460-02-2TT-713 | J460-02-2TT-713 - Room J7.15 - Temperature | J460-02-11-07-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 52 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 52 | °C |  | J460-02-2TT-713 - Room J7.15 - Temperature | J460-02-2TT-713_RmTemp | J460-02-2TT-713_RmTemp | - | J7.15 | - | - | -
2 | 62 | J460-02-1CP-713 | J460-02-2MT-713 | J460-02-2MT-713 - Room J7.15 - Humidity | J460-02-11-07-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-713 - Room J7.15 - Humidity | J460-02-2MT-713_RmHum | J460-02-2MT-713_RmHum | - | J7.15 | - | - | -
1.0 | 63 | J460-02-1CP-713 | J460-02-1ACU-709 | J460-02-2SC-739 - J460-02-1ACU-709 - Speed Control | J460-02-11-07-002 | (UIO) AO | CASETTE GEKO DOUBLE, GCD1.UWW.SE5 | - | 0-10V | - | - | 0 | 100 | % | - | Flaktgroup | CASETTE GEKO DOUBLE, GCD1.UWW.SE5 | NO |  | 0-10V | 0 | 100 | % |  | J460-02-2SC-739 - J460-02-1ACU-709 - Speed Control | J460-02-2SC-739_FCUSpdCntr | J460-02-2SC-739_FCUSpdCntr | - | J7.15 | - | - | - | (UIO) AO3
2 | 69 | J460-02-1CP-714 | J460-02-2TT-714 | J460-02-2TT-714 - Room J7.13b - Temperature | J460-02-11-07-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 52 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 52 | °C |  | J460-02-2TT-714 - Room J7.13b - Temperature | J460-02-2TT-714_RmTemp | J460-02-2TT-714_RmTemp | - | J7.13b | - | - | -
2 | 70 | J460-02-1CP-714 | J460-02-2MT-714 | J460-02-2MT-714 - Room J7.13b - Humidity | J460-02-11-07-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-714 - Room J7.13b - Humidity | J460-02-2MT-714_RmHum | J460-02-2MT-714_RmHum | - | J7.13b | - | - | -
1.0 | 71 | J460-02-1CP-714 | J460-02-1ACU-711 | J460-02-2SC-741 - J460-02-1ACU-711 - Speed Control | J460-02-11-07-002 | (UIO) AO | HYPOPOWER GEKO, GH12.UW03.SE0C2 | - | 0-10V | - | - | 0 | 100 | % | - | Flaktgroup | HYPOPOWER GEKO, GH12.UW03.SE0C2 | NO |  | 0-10V | 0 | 100 | % |  | J460-02-2SC-741 - J460-02-1ACU-711 - Speed Control | J460-02-2SC-741_FCUSpdCntr | J460-02-2SC-741_FCUSpdCntr | - | J7.13b | - | - | - | (UIO) AO3
2 | 72 | J460-02-1CP-714 | J460-02-1ACU-711 | J460-02-2XA-741 - J460-02-1ACU-711 - Alarm | J460-02-11-07-002 | (UIO) DI | HYPOPOWER GEKO, GH12.UW03.SE0C2 | - | PVC | - | - | NORMAL | ALARM | - | - | Flaktgroup | HYPOPOWER GEKO, GH12.UW03.SE0C2 | NO |  | PVC | NORMAL | ALARM | - |  | J460-02-2XA-741 - J460-02-1ACU-711 - Alarm | J460-02-2XA-741_FCUAlm | J460-02-2XA-741_FCUAlm | - | J7.13b | - | - | - | (UIO) DI2
2 | 73 | J460-02-1CP-714 | J460-02-2TT-726 | J460-02-2TT-726 - Room J7.13b - J460-02-1ACU-711 - Supply Temperature | J460-02-11-07-002 | (UIO) AI | Rotronic HF432 Temperature sensor, 4-20mA, Duct Mount, 0°C/50°C | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0.2°C @ 23°C | Rotronic | HF432-DB1XX1XX | NO | HM_Rotronic_HF4 | 4-20mA | 0 | 50 | °C |  | J460-02-2TT-726 - Room J7.13b - J460-02-1ACU-711 - Supply Temperature | J460-02-2TT-726_SupAirTemp | J460-02-2TT-726_SupAirTemp | - | J7.13b | - | - | - | (UIO) AI1
2 | 76 | J460-02-1CP-716 | J460-02-2TT-716 | J460-02-2TT-716 - Room J7.13a - Temperature | J460-02-11-07-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 52 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 52 | °C |  | J460-02-2TT-716 - Room J7.13a - Temperature | J460-02-2TT-716_RmTemp | J460-02-2TT-716_RmTemp | - | J7.13a | - | - | -
2 | 77 | J460-02-1CP-716 | J460-02-2MT-716 | J460-02-2MT-716 - Room J7.13a - Humidity | J460-02-11-07-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-716 - Room J7.13a - Humidity | J460-02-2MT-716_RmHum | J460-02-2MT-716_RmHum | - | J7.13a | - | - | -
2 | 78 | J460-02-1CP-717 | J460-02-2TT-717 | J460-02-2TT-717 - Room J7.11 - Temperature | J460-02-11-07-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 52 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 52 | °C |  | J460-02-2TT-717 - Room J7.11 - Temperature | J460-02-2TT-717_RmTemp | J460-02-2TT-717_RmTemp | - | J7.11 | - | - | -
2 | 79 | J460-02-1CP-717 | J460-02-2MT-717 | J460-02-2MT-717 - Room J7.11 - Humidity | J460-02-11-07-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-717 - Room J7.11 - Humidity | J460-02-2MT-717_RmHum | J460-02-2MT-717_RmHum | - | J7.11 | - | - | -
2 | 80 | J460-02-1CP-718 | J460-02-2TT-718 | J460-02-2TT-718 - Room J7.11 - Temperature | J460-02-11-07-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 52 | °C | ±0.2°C @25°C | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 52 | °C |  | J460-02-2TT-718 - Room J7.11 - Temperature | J460-02-2TT-718_RmTemp | J460-02-2TT-718_RmTemp | - | J7.11 | - | - | -
2 | 81 | J460-02-1CP-718 | J460-02-2MT-718 | J460-02-2MT-718 - Room J7.11 - Humidity | J460-02-11-07-002 | SYLK | Honeywell Wallmodule TR-40 with Sylk-bus, Without Display | - | SYLK | - | - | 0 | 100 | % | ±3%RH from 20-80%RH | Honeywell | TR40-H | NO | HM_HON_TR4X | SYLK | 0 | 100 | % |  | J460-02-2MT-718 - Room J7.11 - Humidity | J460-02-2MT-718_RmHum | J460-02-2MT-718_RmHum | - | J7.11 | - | - | -

## RackPositioning (hidden)
7448-15-1PNL-001 |  | 7448-15-1PNL-001 Expansion
Description | Module Quantity | Description | Module Quantity
Analog Input (8 channel) | 0 | Analog Input (8 channel) | 0
Analog Input hi level (16 ch) | 5 | Analog Input hi level (16 ch) | 0
Analog Outputs 0 to 20mA (8 channel, 5 modules/rack) | 0 | Analog Outputs 0 to 20mA (8 channel, 5 modules/rack) | 0
Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 2 | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 2
Digital Input, 24VDC (32 channel) | 3 | Digital Input, 24VDC (32 channel) | 0
Digital Output, Relays ( 8 channel) | 2 | Digital Output, Relays ( 8 channel) | 1
| 12 |  | 3
Module assignement for this panel |  | Module assignement for this panel
Discription | Rack slot | Discription | Rack slot
Controller C70 CPU | 0 | I/O Scanner | 0
Power Supply 120/240VAC, 60W | 0 | Power Supply 120/240VAC, 60W | 0
Digital Input, 24VDC (32 channel) | 1 | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 1
Digital Input, 24VDC (32 channel) | 2 | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 2
Digital Input, 24VDC (32 channel) | 3 | Digital Output, Relays ( 8 channel) | 3
Analog Input hi level (16 ch) | 4 | SPARE | 4
Analog Input hi level (16 ch) | 5
Analog Input hi level (16 ch) | 6
Analog Input hi level (16 ch) | 7
Analog Input hi level (16 ch) | 8
Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 9
Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 10
Digital Output, Relays ( 8 channel) | 11
Digital Output, Relays ( 8 channel) | 12

## Doc Revision History
*** END OF DOCUMENT ***
Document Revision History
Version Number | Section | Description of Change | Justification of Change
1.0 | NA | New document | CC#2249686
2 | NA | Point tag and description correction | CC#2249686
2.1 | NA | Point description correction | CC#2249686

## Vault Data (hidden)
Vault Data |  | Vault Data
Cell Tokens | Value | (Default/Odd) Frontsheet Header | (Default/Odd) Frontsheet Header Configure Token
${vault:major} | 1 | Left Header
${vault:minor} | 1 | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
${vault:subtype__v} | Design | Right Header
${vault:document_owning_facility__vr.name__v} | Leiden JBV | (Default/Odd) Frontsheet Footer | (Default/Odd) Frontsheet Footer Configure Token
${vault:document_owning_facility__vr.id} | 00F000000003361 | Left Footer
${vault:owning_facility__v} | Leiden JBV | Central Footer
${vault:title__v} | J270-07 BMS 7th Floor Room control Instrument List J-Building | Right Footer
${vault:type__v} | Technical Document | (Even) Frontsheet Header | (Even) Frontsheet Header Configure Token
${vault:document_facility__vr.name__v} | Leiden JBV | Left Header
${vault:document_facility__vr.id} | 00F000000003361 | Central Header
${vault:version} | 2 | Right Header
${vault:document_impacted_facilities__vr.name__v} | Leiden JBV | (Even) Frontsheet Footer | (Even) Frontsheet Footer Configure Token
${vault:document_impacted_facilities__vr.id} | 00F000000003361 | Left Footer
Central Footer
Right Footer
|  | (First Page) Frontsheet Header | (First Page) Frontsheet Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) Frontsheet Footer | (First Page) Frontsheet Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) Floormanager Header | (Default/Odd) Floormanager Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) Floormanager Footer | (Default/Odd) Floormanager Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) Floormanager Header | (Even) Floormanager Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) Floormanager Footer | (Even) Floormanager Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) Floormanager Header | (First Page) Floormanager Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) Floormanager Footer | (First Page) Floormanager Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) RoomControllers Header | (Default/Odd) RoomControllers Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) RoomControllers Footer | (Default/Odd) RoomControllers Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) RoomControllers Header | (Even) RoomControllers Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) RoomControllers Footer | (Even) RoomControllers Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) RoomControllers Header | (First Page) RoomControllers Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) RoomControllers Footer | (First Page) RoomControllers Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) RackPositioning Header | (Default/Odd) RackPositioning Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) RackPositioning Footer | (Default/Odd) RackPositioning Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) RackPositioning Header | (Even) RackPositioning Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) RackPositioning Footer | (Even) RackPositioning Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) RackPositioning Header | (First Page) RackPositioning Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) RackPositioning Footer | (First Page) RackPositioning Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) Doc Revision History Header | (Default/Odd) Doc Revision History Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) Doc Revision History Footer | (Default/Odd) Doc Revision History Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) Doc Revision History Header | (Even) Doc Revision History Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) Doc Revision History Footer | (Even) Doc Revision History Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) Doc Revision History Header | (First Page) Doc Revision History Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) Doc Revision History Footer | (First Page) Doc Revision History Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) Suggestion1 Header | (Default/Odd) Suggestion1 Header Configure Token
Left Header
Central Header
Right Header
|  | (Default/Odd) Suggestion1 Footer | (Default/Odd) Suggestion1 Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) Suggestion1 Header | (Even) Suggestion1 Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) Suggestion1 Footer | (Even) Suggestion1 Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) Suggestion1 Header | (First Page) Suggestion1 Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) Suggestion1 Footer | (First Page) Suggestion1 Footer Configure Token
Left Footer
Central Footer
Right Footer

## Suggestion1 (hidden)
Field1 | Count of Field1
J460-01-11-07-001 | 60
J460-02-11-07-001 | 59
J460-02-11-07-002 | 46
J460-01-11-07-002 | 14
J460-02-11-06-001 | 1
Total Result | 180

## DPCache_Transformed Data (hidden)
Field1
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-001
J460-01-11-07-002
J460-01-11-07-002
J460-01-11-07-002
J460-01-11-07-002
J460-01-11-07-002
J460-01-11-07-002
J460-01-11-07-002
J460-01-11-07-002
J460-01-11-07-002
J460-01-11-07-002
J460-01-11-07-002
J460-01-11-07-002
J460-01-11-07-002
J460-01-11-07-002
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-001
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-06-001
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002
J460-02-11-07-002