## Frontsheet
Janssen Kappa Pollux QC
BMS 6th Floor Office And Lab Room Control Alarm & Parameter List
Document Number: J270-06-APL-001
BMS Alarm & Parameter List
Version: 2.1
BMS Panel : J270-06-1PNL-001 Controller:J270-06-3PLC-001, J270-06-3PLC-002

## Instructions
Alarm Notification Value | EBI priority | GMP Alarm Guideline
1 | Urgent (U 00) | A1 [Used for Alarm Pager]
2 | High (H 00) | A3
3 | Low (L 00) | A5
4 | Journal (J 00) | -

## RackPositioning
7448-15-1PNL-001 |  | 7448-15-1PNL-001 Expansion
Description | Module Quantity | Description | Module Quantity
Analog Input (8 channel) | 0 | Analog Input (8 channel) | 0
Analog Input hi level (16 ch) | 5 | Analog Input hi level (16 ch) | 0
Analog Outputs 0 to 20mA (8 channel, 5 modules/rack) | 0 | Analog Outputs 0 to 20mA (8 channel, 5 modules/rack) | 0
Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 2 | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 2
Digital Input, 24VDC (32 channel) | 3 | Digital Input, 24VDC (32 channel) | 0
Digital Output, Relays ( 8 channel) | 2 | Digital Output, Relays ( 8 channel) | 1
Module assignement for this panel |  | Module assignement for this panel
Discription | Rack slot | Discription | Rack slot
Controller C70 CPU | 0 | I/O Scanner | 0
Power Supply 120/240VAC, 60W | 0 | Power Supply 120/240VAC, 60W | 0
Digital Input, 24VDC (32 channel) | 1 | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 1
Digital Input, 24VDC (32 channel) | 2 | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 2
Digital Input, 24VDC (32 channel) | 3 | Digital Output, Relays ( 8 channel) | 3
Analog Input hi level (16 ch) | 4 | SPARE | 4
Analog Input hi level (16 ch) | 5
Analog Input hi level (16 ch) | 6
Analog Input hi level (16 ch) | 7
Analog Input hi level (16 ch) | 8
Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 9
Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 10
Digital Output, Relays ( 8 channel) | 11
Digital Output, Relays ( 8 channel) | 12

## Doc Revision History
*** END OF DOCUMENT ***
Document Revision History
Version Number | Section | Description of Change | Justification of Change
1.0 | All | New Document | CC#2249686
2 | All | Software changes implemented | CC#2249686
2.1 | All | Updated point description, ACU points and Ranges | CC#2249686

## Vault Data
Vault Data |  | Vault Data
Cell Tokens | Value | (Default/Odd) Frontsheet Header | (Default/Odd) Frontsheet Header Configure Token
${vault:major} | 1 | Left Header
${vault:minor} | 1 | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
${vault:subtype__v} | Design | Right Header
${vault:document_owning_facility__vr.name__v} | Leiden JBV | (Default/Odd) Frontsheet Footer | (Default/Odd) Frontsheet Footer Configure Token
${vault:document_owning_facility__vr.id} | 00F000000003361 | Left Footer
${vault:owning_facility__v} | Leiden JBV | Central Footer
${vault:title__v} | J270-06 BMS 6th Floor Alarm and Parameter list J-Building | Right Footer
${vault:type__v} | Technical Document | (Even) Frontsheet Header | (Even) Frontsheet Header Configure Token
${vault:document_facility__vr.name__v} | Leiden JBV | Left Header
${vault:document_facility__vr.id} | 00F000000003361 | Central Header
${vault:version} | 2 | Right Header
${vault:document_impacted_facilities__vr.name__v} | Leiden JBV | (Even) Frontsheet Footer | (Even) Frontsheet Footer Configure Token
${vault:document_impacted_facilities__vr.id} | 00F000000003361 | Left Footer
Central Footer
Right Footer
|  | (First Page) Frontsheet Header | (First Page) Frontsheet Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) Frontsheet Footer | (First Page) Frontsheet Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) J270-06 Header | (Default/Odd) J270-06 Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) J270-06 Footer | (Default/Odd) J270-06 Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) J270-06 Header | (Even) J270-06 Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) J270-06 Footer | (Even) J270-06 Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) J270-06 Header | (First Page) J270-06 Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) J270-06 Footer | (First Page) J270-06 Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) Instructions Header | (Default/Odd) Instructions Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) Instructions Footer | (Default/Odd) Instructions Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) Instructions Header | (Even) Instructions Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) Instructions Footer | (Even) Instructions Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) Instructions Header | (First Page) Instructions Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) Instructions Footer | (First Page) Instructions Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) RackPositioning Header | (Default/Odd) RackPositioning Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) RackPositioning Footer | (Default/Odd) RackPositioning Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) RackPositioning Header | (Even) RackPositioning Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) RackPositioning Footer | (Even) RackPositioning Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) RackPositioning Header | (First Page) RackPositioning Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) RackPositioning Footer | (First Page) RackPositioning Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) Doc Revision History Header | (Default/Odd) Doc Revision History Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) Doc Revision History Footer | (Default/Odd) Doc Revision History Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) Doc Revision History Header | (Even) Doc Revision History Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) Doc Revision History Footer | (Even) Doc Revision History Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) Doc Revision History Header | (First Page) Doc Revision History Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) Doc Revision History Footer | (First Page) Doc Revision History Footer Configure Token
Left Footer
Central Footer
Right Footer

## J270-06-demo
Rev Nr | Nr | Outstation | Device Tag | Function | Point Description | EBI Tag | JACE Tag | Range (Low) / State 0 | Range (High) / State 1 | State 2 | State 3 | State 4 | State 5 | State 6 | State 7 | State 8 | State 9 | State 16 | State 32 | State 64 | State 128 | State 8192 | State 16384 | State 32768 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
1.0 | 1 | J270-06-1PNL-001 | J270-07-2XA-001 | Measurement | J270-07-2XA-001 - J270-06-1PNL-001 - 230VAC Thermal Fault Signal | J270-07-2XA-001_230VACThemFlt |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2 | J270-06-1PNL-001 | J270-07-2XA-001 | Alarm | J270-07-2XA-001 - J270-06-1PNL-001 - 230VAC Thermal Fault Signal Alarm | J270-07-2XA-001_230VACThemFlt_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
1.0 | 1 | J270-06-1PNL-001 | J270-07-2XA-002 | Measurement | J270-07-2XA-002 - J270-06-1PNL-001 - 230VAC Thermal Fault Signal | J270-07-2XA-002_230VACThemFlt |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2 | J270-06-1PNL-001 | J270-07-2XA-002 | Alarm | J270-07-2XA-002 - J270-06-1PNL-001 - 230VAC Thermal Fault Signal Alarm | J270-07-2XA-002_230VACThemFlt_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
1.0 | 5 | J270-06-1PNL-001 | J270-07-2XA-004 | Measurement | J270-07-2XA-004 - J270-06-1PNL-001 - Surge Voltage Arrester Signal | J270-07-2XA-004_SurgeVoltArr |  | NORMAL | FAULT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 6 | J270-06-1PNL-001 | J270-07-2XA-004 | Alarm | J270-07-2XA-004 - J270-06-1PNL-001 - Surge Voltage Arrester Signal Alarm | J270-07-2XA-004_SurgeVoltArr_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
1.0 | 7 | J270-06-1PNL-001 | J270-07-2XA-005 | Measurement | J270-07-2XA-005 - J270-06-1PNL-001 - Common Fire Alarm | J270-07-2XA-005_ExtFireCom |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 8 | J270-06-1PNL-001 | J270-07-2XA-005 | Alarm | J270-07-2XA-005 - J270-06-1PNL-001 - Common Fire Alarm | J270-07-2XA-005_ExtFireCom_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | M | - | bar: State 2 to State 64
1.0 | 354 | J229-06-1PNL-001 | J229-07-2XA-101 | Measurement | J229-07-2XA-101 - SVK-6H - Voltage Surge Arrestor | J229-07-2XA-101_SurgeVoltArr |  | NORMAL | FAULT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 355 | J229-06-1PNL-001 | J229-07-2XA-101 | Alarm | J229-07-2XA-101 - SVK-6H - Voltage Surge Arrestor Alarm | J229-07-2XA-101_SurgeVoltArr_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
1.0 | 352 | J229-06-1PNL-001 | J229-07-2XA-102 | Measurement | J229-07-2XA-102 - SVK-6H - Circuit Breaker Tripped | J229-07-2XA-102_CirBrkTrip |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 353 | J229-06-1PNL-001 | J229-07-2XA-102 | Alarm | J229-07-2XA-102 - SVK-6H - Circuit Breaker Tripped Alarm | J229-07-2XA-102_CirBrkTrip_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
1.0 | 354 | J229-06-1PNL-001 | J229-07-2XA-103 | Measurement | J229-07-2XA-103 - SVK-6H - Voltage Surge Arrestor | J229-07-2XA-103_SurgeVoltArr |  | NORMAL | FAULT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 355 | J229-06-1PNL-001 | J229-07-2XA-103 | Alarm | J229-07-2XA-103 - SVK-6H - Voltage Surge Arrestor Alarm | J229-07-2XA-103_SurgeVoltArr_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
1.0 | 352 | J229-06-1PNL-001 | J229-07-2XA-104 | Measurement | J229-07-2XA-104 - SVK-6H - Circuit Breaker Tripped | J229-07-2XA-104_CirBrkTrip |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 353 | J229-06-1PNL-001 | J229-07-2XA-104 | Alarm | J229-07-2XA-104 - SVK-6H - Circuit Breaker Tripped Alarm | J229-07-2XA-104_CirBrkTrip_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
1.0 | 354 | J229-06-1PNL-001 | J229-07-2XA-105 | Measurement | J229-07-2XA-105 - SVK-6H - Voltage Surge Arrestor | J229-07-2XA-105_SurgeVoltArr |  | NORMAL | FAULT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 355 | J229-06-1PNL-001 | J229-07-2XA-105 | Alarm | J229-07-2XA-105 - SVK-6H - Voltage Surge Arrestor Alarm | J229-07-2XA-105_SurgeVoltArr_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
1.0 | 352 | J229-06-1PNL-001 | J229-07-2XA-106 | Measurement | J229-07-2XA-106 - SVK-6H - Circuit Breaker Tripped | J229-07-2XA-106_CirBrkTrip |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 353 | J229-06-1PNL-001 | J229-07-2XA-106 | Alarm | J229-07-2XA-106 - SVK-6H - Circuit Breaker Tripped Alarm | J229-07-2XA-106_CirBrkTrip_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
1.0 | 354 | J229-06-1PNL-001 | J229-07-2XA-107 | Measurement | J229-07-2XA-107 - SVK-6H - Voltage Surge Arrestor | J229-07-2XA-107_SurgeVoltArr |  | NORMAL | FAULT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 355 | J229-06-1PNL-001 | J229-07-2XA-107 | Alarm | J229-07-2XA-107 - SVK-6H - Voltage Surge Arrestor Alarm | J229-07-2XA-107_SurgeVoltArr_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
1.0 | 352 | J229-06-1PNL-001 | J229-07-2XA-108 | Measurement | J229-07-2XA-108 - SVK-6H - Circuit Breaker Tripped | J229-07-2XA-108_CirBrkTrip |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 353 | J229-06-1PNL-001 | J229-07-2XA-108 | Alarm | J229-07-2XA-108 - SVK-6H - Circuit Breaker Tripped Alarm | J229-07-2XA-108_CirBrkTrip_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
1.0 | 354 | J229-06-1PNL-001 | J229-07-2XA-109 | Measurement | J229-07-2XA-109 - SVK-6H - Voltage Surge Arrestor | J229-07-2XA-109_SurgeVoltArr |  | NORMAL | FAULT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 355 | J229-06-1PNL-001 | J229-07-2XA-109 | Alarm | J229-07-2XA-109 - SVK-6H - Voltage Surge Arrestor Alarm | J229-07-2XA-109_SurgeVoltArr_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
1.0 | 352 | J229-06-1PNL-001 | J229-07-2XA-110 | Measurement | J229-07-2XA-110 - SVK-6H - Circuit Breaker Tripped | J229-07-2XA-110_CirBrkTrip |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 353 | J229-06-1PNL-001 | J229-07-2XA-110 | Alarm | J229-07-2XA-110 - SVK-6H - Circuit Breaker Tripped Alarm | J229-07-2XA-110_CirBrkTrip_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
1.0 | 416 | J270-06-1PNL-001 | J460-02-2KS-703 | Measurement | J460-02-2KS-703 - Labs Day Extention Timer - Timer | J460-02-2KS-703_DET |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 221 | J270-06-1PNL-001 | J229-07-1QIT-001 | Measurement | J229-07-1QIT-001 - SVK-6H - Energy Meter Current Phase L1 | J229-07-1QIT-001_CurrPhase1 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 222 | J270-06-1PNL-001 | J229-07-1QIT-001 | Measurement | J229-07-1QIT-001 - SVK-6H - Energy Meter Current Phase L2 | J229-07-1QIT-001_CurrPhase2 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 223 | J270-06-1PNL-001 | J229-07-1QIT-001 | Measurement | J229-07-1QIT-001 - SVK-6H - Energy Meter Current Phase L3 | J229-07-1QIT-001_CurrPhase3 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 224 | J270-06-1PNL-001 | J229-07-1QIT-001 | Measurement | J229-07-1QIT-001 - SVK-6H - Energy Meter 3-Phase Average | J229-07-1QIT-001_3PhaseAvg |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 225 | J270-06-1PNL-001 | J229-07-1QIT-001 | Measurement | J229-07-1QIT-001 - SVK-6H - Energy Meter Voltage Phase A-B | J229-07-1QIT-001_VoltPhaseA_B |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 226 | J270-06-1PNL-001 | J229-07-1QIT-001 | Measurement | J229-07-1QIT-001 - SVK-6H - Energy Meter Voltage Phase B-C | J229-07-1QIT-001_VoltPhaseB_C |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 227 | J270-06-1PNL-001 | J229-07-1QIT-001 | Measurement | J229-07-1QIT-001 - SVK-6H - Energy Meter Voltage Phase C-A | J229-07-1QIT-001_VoltPhaseC_A |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 228 | J270-06-1PNL-001 | J229-07-1QIT-001 | Measurement | J229-07-1QIT-001 - SVK-6H - Energy Meter L-L Average | J229-07-1QIT-001_LLAverage |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 229 | J270-06-1PNL-001 | J229-07-1QIT-001 | Measurement | J229-07-1QIT-001 - SVK-6H - Energy Meter L-N Average | J229-07-1QIT-001_LNAverage |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 230 | J270-06-1PNL-001 | J229-07-1QIT-001 | Measurement | J229-07-1QIT-001 - SVK-6H - Energy Meter Real Power | J229-07-1QIT-001_RealPower |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 231 | J270-06-1PNL-001 | J229-07-1QIT-001 | Measurement | J229-07-1QIT-001 - SVK-6H - Energy Meter Reactive Power | J229-07-1QIT-001_ReactivePower |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kVAr | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 232 | J270-06-1PNL-001 | J229-07-1QIT-001 | Measurement | J229-07-1QIT-001 - SVK-6H - Energy Meter Apparent Power | J229-07-1QIT-001_ApparentPower |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kVAr | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 233 | J270-06-1PNL-001 | J229-07-1QIT-001 | Measurement | J229-07-1QIT-001 - SVK-6H - Energy Meter Frequency | J229-07-1QIT-001_Frequency |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2603 | J270-06-1PNL-001 | J229-07-1QIT-001 | Alarm | J229-07-1QIT-001 - SVK-6H - Energy Meter Communication Failure Alarm | J229-07-1QIT-001_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 221 | J270-06-1PNL-001 | J229-07-1QIT-002 | Measurement | J229-07-1QIT-002 - SVK-6H - Energy Meter Current Phase L1 | J229-07-1QIT-002_CurrPhase1 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 222 | J270-06-1PNL-001 | J229-07-1QIT-002 | Measurement | J229-07-1QIT-002 - SVK-6H - Energy Meter Current Phase L2 | J229-07-1QIT-002_CurrPhase2 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 223 | J270-06-1PNL-001 | J229-07-1QIT-002 | Measurement | J229-07-1QIT-002 - SVK-6H - Energy Meter Current Phase L3 | J229-07-1QIT-002_CurrPhase3 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 224 | J270-06-1PNL-001 | J229-07-1QIT-002 | Measurement | J229-07-1QIT-002 - SVK-6H - Energy Meter 3-Phase Average | J229-07-1QIT-002_3PhaseAvg |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 225 | J270-06-1PNL-001 | J229-07-1QIT-002 | Measurement | J229-07-1QIT-002 - SVK-6H - Energy Meter Voltage Phase A-B | J229-07-1QIT-002_VoltPhaseA_B |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 226 | J270-06-1PNL-001 | J229-07-1QIT-002 | Measurement | J229-07-1QIT-002 - SVK-6H - Energy Meter Voltage Phase B-C | J229-07-1QIT-002_VoltPhaseB_C |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 227 | J270-06-1PNL-001 | J229-07-1QIT-002 | Measurement | J229-07-1QIT-002 - SVK-6H - Energy Meter Voltage Phase C-A | J229-07-1QIT-002_VoltPhaseC_A |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 228 | J270-06-1PNL-001 | J229-07-1QIT-002 | Measurement | J229-07-1QIT-002 - SVK-6H - Energy Meter L-L Average | J229-07-1QIT-002_LLAverage |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 229 | J270-06-1PNL-001 | J229-07-1QIT-002 | Measurement | J229-07-1QIT-002 - SVK-6H - Energy Meter L-N Average | J229-07-1QIT-002_LNAverage |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 230 | J270-06-1PNL-001 | J229-07-1QIT-002 | Measurement | J229-07-1QIT-002 - SVK-6H - Energy Meter Real Power | J229-07-1QIT-002_RealPower |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 231 | J270-06-1PNL-001 | J229-07-1QIT-002 | Measurement | J229-07-1QIT-002 - SVK-6H - Energy Meter Reactive Power | J229-07-1QIT-002_ReactivePower |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kVAr | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 232 | J270-06-1PNL-001 | J229-07-1QIT-002 | Measurement | J229-07-1QIT-002 - SVK-6H - Energy Meter Apparent Power | J229-07-1QIT-002_ApparentPower |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kVAr | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 233 | J270-06-1PNL-001 | J229-07-1QIT-002 | Measurement | J229-07-1QIT-002 - SVK-6H - Energy Meter Frequency | J229-07-1QIT-002_Frequency |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2603 | J270-06-1PNL-001 | J229-07-1QIT-002 | Alarm | J229-07-1QIT-002 - SVK-6H - Energy Meter Communication Failure Alarm | J229-07-1QIT-002_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 221 | J270-06-1PNL-001 | J229-07-1QIT-003 | Measurement | J229-07-1QIT-003 - SVK-6H - Energy Meter Current Phase L1 | J229-07-1QIT-003_CurrPhase1 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 222 | J270-06-1PNL-001 | J229-07-1QIT-003 | Measurement | J229-07-1QIT-003 - SVK-6H - Energy Meter Current Phase L2 | J229-07-1QIT-003_CurrPhase2 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 223 | J270-06-1PNL-001 | J229-07-1QIT-003 | Measurement | J229-07-1QIT-003 - SVK-6H - Energy Meter Current Phase L3 | J229-07-1QIT-003_CurrPhase3 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 224 | J270-06-1PNL-001 | J229-07-1QIT-003 | Measurement | J229-07-1QIT-003 - SVK-6H - Energy Meter 3-Phase Average | J229-07-1QIT-003_3PhaseAvg |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 225 | J270-06-1PNL-001 | J229-07-1QIT-003 | Measurement | J229-07-1QIT-003 - SVK-6H - Energy Meter Voltage Phase A-B | J229-07-1QIT-003_VoltPhaseA_B |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 226 | J270-06-1PNL-001 | J229-07-1QIT-003 | Measurement | J229-07-1QIT-003 - SVK-6H - Energy Meter Voltage Phase B-C | J229-07-1QIT-003_VoltPhaseB_C |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 227 | J270-06-1PNL-001 | J229-07-1QIT-003 | Measurement | J229-07-1QIT-003 - SVK-6H - Energy Meter Voltage Phase C-A | J229-07-1QIT-003_VoltPhaseC_A |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 228 | J270-06-1PNL-001 | J229-07-1QIT-003 | Measurement | J229-07-1QIT-003 - SVK-6H - Energy Meter L-L Average | J229-07-1QIT-003_LLAverage |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 229 | J270-06-1PNL-001 | J229-07-1QIT-003 | Measurement | J229-07-1QIT-003 - SVK-6H - Energy Meter L-N Average | J229-07-1QIT-003_LNAverage |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 230 | J270-06-1PNL-001 | J229-07-1QIT-003 | Measurement | J229-07-1QIT-003 - SVK-6H - Energy Meter Real Power | J229-07-1QIT-003_RealPower |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 231 | J270-06-1PNL-001 | J229-07-1QIT-003 | Measurement | J229-07-1QIT-003 - SVK-6H - Energy Meter Reactive Power | J229-07-1QIT-003_ReactivePower |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kVAr | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 232 | J270-06-1PNL-001 | J229-07-1QIT-003 | Measurement | J229-07-1QIT-003 - SVK-6H - Energy Meter Apparent Power | J229-07-1QIT-003_ApparentPower |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kVAr | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 233 | J270-06-1PNL-001 | J229-07-1QIT-003 | Measurement | J229-07-1QIT-003 - SVK-6H - Energy Meter Frequency | J229-07-1QIT-003_Frequency |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2603 | J270-06-1PNL-001 | J229-07-1QIT-003 | Alarm | J229-07-1QIT-003 - SVK-6H - Energy Meter Communication Failure Alarm | J229-07-1QIT-003_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 221 | J270-06-1PNL-001 | J229-07-1QIT-004 | Measurement | J229-07-1QIT-004 - SVK-6H - Energy Meter Current Phase L1 | J229-07-1QIT-004_CurrPhase1 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 222 | J270-06-1PNL-001 | J229-07-1QIT-004 | Measurement | J229-07-1QIT-004 - SVK-6H - Energy Meter Current Phase L2 | J229-07-1QIT-004_CurrPhase2 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 223 | J270-06-1PNL-001 | J229-07-1QIT-004 | Measurement | J229-07-1QIT-004 - SVK-6H - Energy Meter Current Phase L3 | J229-07-1QIT-004_CurrPhase3 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 224 | J270-06-1PNL-001 | J229-07-1QIT-004 | Measurement | J229-07-1QIT-004 - SVK-6H - Energy Meter 3-Phase Average | J229-07-1QIT-004_3PhaseAvg |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 225 | J270-06-1PNL-001 | J229-07-1QIT-004 | Measurement | J229-07-1QIT-004 - SVK-6H - Energy Meter Voltage Phase A-B | J229-07-1QIT-004_VoltPhaseA_B |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 226 | J270-06-1PNL-001 | J229-07-1QIT-004 | Measurement | J229-07-1QIT-004 - SVK-6H - Energy Meter Voltage Phase B-C | J229-07-1QIT-004_VoltPhaseB_C |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 227 | J270-06-1PNL-001 | J229-07-1QIT-004 | Measurement | J229-07-1QIT-004 - SVK-6H - Energy Meter Voltage Phase C-A | J229-07-1QIT-004_VoltPhaseC_A |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 228 | J270-06-1PNL-001 | J229-07-1QIT-004 | Measurement | J229-07-1QIT-004 - SVK-6H - Energy Meter L-L Average | J229-07-1QIT-004_LLAverage |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 229 | J270-06-1PNL-001 | J229-07-1QIT-004 | Measurement | J229-07-1QIT-004 - SVK-6H - Energy Meter L-N Average | J229-07-1QIT-004_LNAverage |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 230 | J270-06-1PNL-001 | J229-07-1QIT-004 | Measurement | J229-07-1QIT-004 - SVK-6H - Energy Meter Real Power | J229-07-1QIT-004_RealPower |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 231 | J270-06-1PNL-001 | J229-07-1QIT-004 | Measurement | J229-07-1QIT-004 - SVK-6H - Energy Meter Reactive Power | J229-07-1QIT-004_ReactivePower |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kVAr | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 232 | J270-06-1PNL-001 | J229-07-1QIT-004 | Measurement | J229-07-1QIT-004 - SVK-6H - Energy Meter Apparent Power | J229-07-1QIT-004_ApparentPower |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kVAr | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 233 | J270-06-1PNL-001 | J229-07-1QIT-004 | Measurement | J229-07-1QIT-004 - SVK-6H - Energy Meter Frequency | J229-07-1QIT-004_Frequency |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2603 | J270-06-1PNL-001 | J229-07-1QIT-004 | Alarm | J229-07-1QIT-004 - SVK-6H - Energy Meter Communication Failure Alarm | J229-07-1QIT-004_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 286 | J270-06-1PNL-001 | J232-07-1UPS-001 | Measurement | J232-07-1UPS-001 - Parameters UPS MDF Room 6th Floor Outpower Phase 1 | J232-07-1UPS-001_OutPower0 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 287 | J270-06-1PNL-001 | J232-07-1UPS-001 | Measurement | J232-07-1UPS-001 - Parameters UPS MDF Room 6th Floor Outpower Phase 2 | J232-07-1UPS-001_OutPower1 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 288 | J270-06-1PNL-001 | J232-07-1UPS-001 | Measurement | J232-07-1UPS-001 - Parameters UPS MDF Room 6th Floor Outpower Phase 3 | J232-07-1UPS-001_OutPower2 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 289 | J270-06-1PNL-001 | J232-07-1UPS-001 | Measurement | J232-07-1UPS-001 - Parameters UPS MDF Room 6th Floor Battery Capacity | J232-07-1UPS-001_Battcap |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 290 | J270-06-1PNL-001 | J232-07-1UPS-001 | Measurement | J232-07-1UPS-001 - Parameters UPS MDF Room 6th Floor Temperature | J232-07-1UPS-001_Temp |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 291 | J270-06-1PNL-001 | J232-07-1UPS-001 | Measurement | J232-07-1UPS-001 - Parameters UPS MDF Room 6th Floor Autonomy Time | J232-07-1UPS-001_Autonomtime |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 292 | J270-06-1PNL-001 | J232-07-1UPS-001 | Measurement | J232-07-1UPS-001 - Parameters UPS MDF Room 6th Floor UPS MDF Room Status | J232-07-1UPS-001_Status |  | NORMAL | BYPMODE | SHUTDOWN | UPSOK | BCKMODE | BATTLOW | OVRTEMP | TSTACTV | INHIGH | OUTHIGH | INVFAIL | BATTBAD | ECOMODE | INVWARN | UPSFAIL | COMMLOST | DVGALM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 293 | J270-06-1PNL-001 | J232-07-1UPS-001 | Measurement | J232-07-1UPS-001 - Parameters UPS MDF Room 6th Floor Battery Voltage | J232-07-1UPS-001_BattVolt |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 294 | J270-06-1PNL-001 | J232-07-1UPS-001 | Measurement | J232-07-1UPS-001 - Parameters UPS MDF Room 6th Floor Powerfail Counter | J232-07-1UPS-001_CNT_PF |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 295 | J270-06-1PNL-001 | J232-07-1UPS-001 | Alarm | J232-07-1UPS-001 - Parameters UPS MDF Room 6th Floor Alarm | J232-07-1UPS-001_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
1.0 | 296 | J270-06-1PNL-001 | J232-07-1UPS-001 | Measurement | J232-07-1UPS-001 - Parameters UPS MDF Room 6th Floor Output Voltage Phase 1 | J232-07-1UPS-001_OutVolt0 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 297 | J270-06-1PNL-001 | J232-07-1UPS-001 | Measurement | J232-07-1UPS-001 - Parameters UPS MDF Room 6th Floor Output Voltage Phase 2 | J232-07-1UPS-001_OutVolt1 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 298 | J270-06-1PNL-001 | J232-07-1UPS-001 | Measurement | J232-07-1UPS-001 - Parameters UPS MDF Room 6th Floor Output Voltage Phase 3 | J232-07-1UPS-001_OutVolt2 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 299 | J270-06-1PNL-001 | J232-07-1UPS-001 | Measurement | J232-07-1UPS-001 - Parameters UPS MDF Room 6th Floor Output Current Phase 1 | J232-07-1UPS-001_OutCurrent0 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 300 | J270-06-1PNL-001 | J232-07-1UPS-001 | Measurement | J232-07-1UPS-001 - Parameters UPS MDF Room 6th Floor Output Current Phase 2 | J232-07-1UPS-001_OutCurrent1 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 301 | J270-06-1PNL-001 | J232-07-1UPS-001 | Measurement | J232-07-1UPS-001 - Parameters UPS MDF Room 6th Floor Output Current Phase 3 | J232-07-1UPS-001_OutCurrent2 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 302 | J270-06-1PNL-001 | J232-07-1UPS-001 | Measurement | J232-07-1UPS-001 - Parameters UPS MDF Room 6th Floor True Output Power Phase 1 | J232-07-1UPS-001_TrueOutPower0 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 303 | J270-06-1PNL-001 | J232-07-1UPS-001 | Measurement | J232-07-1UPS-001 - Parameters UPS MDF Room 6th Floor True Output Power Phase 2 | J232-07-1UPS-001_TrueOutPower1 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 304 | J270-06-1PNL-001 | J232-07-1UPS-001 | Measurement | J232-07-1UPS-001 - Parameters UPS MDF Room 6th Floor True Output Power Phase 3 | J232-07-1UPS-001_TrueOutPower2 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 305 | J270-06-1PNL-001 | J232-07-1UPS-001 | Measurement | J232-07-1UPS-001 - Parameters UPS MDF Room 6th Floor Battery Current | J232-07-1UPS-001_BattCurrent |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 306 | J270-06-1PNL-001 | J232-07-1UPS-001 | Measurement | J232-07-1UPS-001 - Parameters UPS MDF Room 6th Floor Output Frequency Phase 1 | J232-07-1UPS-001_OutFreq0 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 307 | J270-06-1PNL-001 | J232-07-1UPS-001 | Measurement | J232-07-1UPS-001 - Parameters UPS MDF Room 6th Floor Battery Condition | J232-07-1UPS-001_BattCond |  | GOOD | WEAK | REPLACE | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2608 | J270-06-1PNL-001 | J232-07-1UPS-001 | Alarm | J232-07-1UPS-001 - Parameters UPS MDF Room 6th Floor - Communication Failure Alarm | J232-07-1UPS-001_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 9 | J270-06-1PNL-001 | J460-01-2TT-712 | Measurement | J460-01-2TT-712 - Chilled Water - Supply Temperature | J460-01-2TT-712_ChlWtrSupTemp |  | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 10 | J270-06-1PNL-001 | J460-01-2TT-712 | Measurement | J460-01-2TT-712 - Chilled Water - Supply Temperature Field | J460-01-2TT-712_ChlWtrSupTemp_Field |  | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 11 | J270-06-1PNL-001 | J460-01-2TT-712 | Alarm | J460-01-2TT-712 - Chilled Water - Supply Temperature High Alarm | J460-01-2TT-712_ChlWtrSupTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 12 | J270-06-1PNL-001 | J460-01-2TT-712 | Setting | J460-01-2TT-712 - Chilled Water - Supply Temperature | J460-01-2TT-712_ChlWtrSupTemp_HASP |  | - | 16 | [11 empty] | - | - | - | - | - | 0.5 | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 13 | J270-06-1PNL-001 | J460-01-2TT-712 | Alarm | J460-01-2TT-712 - Chilled Water - Supply Temperature Low Alarm | J460-01-2TT-712_ChlWtrSupTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 14 | J270-06-1PNL-001 | J460-01-2TT-712 | Setting | J460-01-2TT-712 - Chilled Water - Supply Temperature | J460-01-2TT-712_ChlWtrSupTemp_LASP |  | 6 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 15 | J270-06-1PNL-001 | J460-01-2TT-712 | Setting | J460-01-2TT-712 - Chilled Water - Supply Temperature Calibration Mode Selection | J460-01-2TT-712_ChlWtrSupTempCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 16 | J270-06-1PNL-001 | J460-01-2TT-712 | Alarm | J460-01-2TT-712 - Chilled Water - Supply Temperature Calibration Still Active Alarm | J460-01-2TT-712_ChlWtrSupTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 17 | J270-06-1PNL-001 | J460-01-2TT-712 | Setting | J460-01-2TT-712 - Chilled Water - Supply Temperature Setpoint | J460-01-2TT-712_ChlWtrSupTempSetpoint |  | 16 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 20 | J270-06-1PNL-001 | J460-01-2TT-712 | Setting | J460-01-2TT-712 - Chilled Water - Supply Temperature Proportional Band | J460-01-2TT-712_ChlWtrSupTemp_Set_P |  | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 21 | J270-06-1PNL-001 | J460-01-2TT-712 | Setting | J460-01-2TT-712 - Chilled Water - Supply Temperature Integral Time | J460-01-2TT-712_ChlWtrSupTemp_Set_I |  | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 22 | J270-06-1PNL-001 | J460-01-2TT-712 | Setting | J460-01-2TT-712 - Chilled Water - Supply Temperature Derivative Time | J460-01-2TT-712_ChlWtrSupTemp_Set_D |  | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 23 | J270-06-1PNL-001 | J460-01-2TT-713 | Measurement | J460-01-2TT-713 - Chilled Water - Return Temperature | J460-01-2TT-713_ChlWtrRetTemp |  | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 24 | J270-06-1PNL-001 | J460-01-2TT-713 | Measurement | J460-01-2TT-713 - Chilled Water - Return Temperature Field | J460-01-2TT-713_ChlWtrRetTemp_Field |  | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 25 | J270-06-1PNL-001 | J460-01-2TT-713 | Alarm | J460-01-2TT-713 - Chilled Water - Return Temperature High Alarm | J460-01-2TT-713_ChlWtrRetTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 26 | J270-06-1PNL-001 | J460-01-2TT-713 | Setting | J460-01-2TT-713 - Chilled Water - Return Temperature | J460-01-2TT-713_ChlWtrRetTemp_HASP |  | - | 18.5 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 3 to State 64
1.0 | 27 | J270-06-1PNL-001 | J460-01-2TT-713 | Alarm | J460-01-2TT-713 - Chilled Water - Return Temperature Low Alarm | J460-01-2TT-713_ChlWtrRetTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 28 | J270-06-1PNL-001 | J460-01-2TT-713 | Setting | J460-01-2TT-713 - Chilled Water - Return Temperature | J460-01-2TT-713_ChlWtrRetTemp_LASP |  | 12 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 29 | J270-06-1PNL-001 | J460-01-2TT-713 | Setting | J460-01-2TT-713 - Chilled Water - Return Temperature Calibration Mode Selection | J460-01-2TT-713_ChlWtrRetTempCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 30 | J270-06-1PNL-001 | J460-01-2TT-713 | Alarm | J460-01-2TT-713 - Chilled Water - Return Temperature Calibration Still Active Alarm | J460-01-2TT-713_ChlWtrRetTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 31 | J270-06-1PNL-001 | J460-01-2FCV-743 | Alarm | J460-01-2FCV-743 - Chilled Water Valve - Controller Communication Failure Alarm | J460-01-2FCV-743_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 32 | J270-06-1PNL-001 | J460-01-2FCV-743 | Measurement | J460-01-2FCV-743 - Chilled Water Valve - Forced Position | J460-01-2FCV-743_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 33 | J270-06-1PNL-001 | J460-01-2FCV-743 | Setting | J460-01-2FCV-743 - Chilled Water Valve - Forced Calibration | J460-01-2FCV-743_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 34 | J270-06-1PNL-001 | J460-01-2FCV-743 | Measurement | J460-01-2FCV-743 - Chilled Water Valve - Status | J460-01-2FCV-743_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 35 | J270-06-1PNL-001 | J460-01-2FCV-743 | Measurement | J460-01-2FCV-743 - Chilled Water Valve - Actual SP | J460-01-2FCV-743_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 36 | J270-06-1PNL-001 | J460-01-2FCV-743 | Setting | J460-01-2FCV-743 - Chilled Water Valve - SP | J460-01-2FCV-743_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 37 | J270-06-1PNL-001 | J460-01-2FCV-743 | Alarm | J460-01-2FCV-743 - Chilled Water Valve - Controller Fail to Open Alarm | J460-01-2FCV-743_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 38 | J270-06-1PNL-001 | J460-01-2FCV-743 | Alarm | J460-01-2FCV-743 - Chilled Water Valve - Controller Fail to Close Alarm | J460-01-2FCV-743_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 39 | J270-06-1PNL-001 | J460-01-2FCV-743 | Measurement | J460-01-2FCV-743 - Chilled Water Valve - Error Code | J460-01-2FCV-743_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
| 2328 | J270-06-1PNL-001 | J460-01-2FCV-743 | Measurement | J460-01-2FCV-743 - Chilled Water Valve - Speed | J460-01-2FCV-743_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 40 | J270-06-1PNL-001 | J460-01-1PMP-701 | Alarm | J460-01-1PMP-701 - Chilled Water Circulation Pump - Controller Communication Failure Alarm | J460-01-1PMP-701_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 41 | J270-06-1PNL-001 | J460-01-1PMP-701 | Measurement | J460-01-1PMP-701 - Chilled Water Circulation Pump - Error Code | J460-01-1PMP-701_ErrCode |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 42 | J270-06-1PNL-001 | J460-01-1PMP-701 | Measurement | J460-01-1PMP-701 - Chilled Water Circulation Pump - Speed | J460-01-1PMP-701_Spd |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | rpm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 43 | J270-06-1PNL-001 | J460-01-1PMP-701 | Measurement | J460-01-1PMP-701 - Chilled Water Circulation Pump - Frequency | J460-01-1PMP-701_Frq |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 44 | J270-06-1PNL-001 | J460-01-1PMP-701 | Measurement | J460-01-1PMP-701 - Chilled Water Circulation Pump - Motor Current | J460-01-1PMP-701_MtrCur |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 45 | J270-06-1PNL-001 | J460-01-1PMP-701 | Measurement | J460-01-1PMP-701 - Chilled Water Circulation Pump - DC Link Voltage | J460-01-1PMP-701_DCVolt |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 46 | J270-06-1PNL-001 | J460-01-1PMP-701 | Measurement | J460-01-1PMP-701 - Chilled Water Circulation Pump - Power | J460-01-1PMP-701_Pwr |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | W | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 47 | J270-06-1PNL-001 | J460-01-1PMP-701 | Measurement | J460-01-1PMP-701 - Chilled Water Circulation Pump - Run Time | J460-01-1PMP-701_RunTime |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 48 | J270-06-1PNL-001 | J460-01-1PMP-701 | Measurement | J460-01-1PMP-701 - Chilled Water Circulation Pump - Load Percentage | J460-01-1PMP-701_LdPerc |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 49 | J270-06-1PNL-001 | J460-01-1PMP-701 | Measurement | J460-01-1PMP-701 - Chilled Water Circulation Pump - Control Source | J460-01-1PMP-701_CntSrc |  | LOCCNT | BUSCNT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 50 | J270-06-1PNL-001 | J460-01-1PMP-701 | Measurement | J460-01-1PMP-701 - Chilled Water Circulation Pump - Rotation Status | J460-01-1PMP-701_Rot |  | NOROT | ROT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 51 | J270-06-1PNL-001 | J460-01-1PMP-701 | Measurement | J460-01-1PMP-701 - Chilled Water Circulation Pump - Actual Operation Mode | J460-01-1PMP-701_ActOpMode |  | - | START | STOP | MINIMUM | MAXIMUM | USERDEF | LOCMODE | EMGMODE | HANDMODE | UNKNOWN | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 52 | J270-06-1PNL-001 | J460-01-1PMP-701 | Measurement | J460-01-1PMP-701 - Chilled Water Circulation Pump - Operation Mode | J460-01-1PMP-701_OpMode |  | - | START | STOP | MINIMUM | MAXIMUM | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1.0 | 53 | J270-06-1PNL-001 | J460-01-1PMP-701 | Measurement | J460-01-2XS-601 - Chilled Water Circulation Pump J460-01-1PMP-701 - Enable | J460-01-2XS-601_ChlWtrCirPmpEna |  | DISABLE | ENABLE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 54 | J270-06-1PNL-001 | J460-01-1PMP-701 | Measurement | J460-01-2SC-601 - Chilled Water Circulation Pump J460-01-1PMP-701 - Control Signal | J460-01-2SC-601_ChlWtrCirPmpCntr |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 55 | J270-06-1PNL-001 | J460-01-1PMP-701 | Measurement | J460-01-2XA-601 - Chilled Water Circulation Pump J460-01-1PMP-701 - Alarm | J460-01-2XA-601_ChlWtrCirPmpAlm | R420-01-2XA-601_ChlWtrCirPmpAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 56 | J270-06-1PNL-001 | J460-01-1PMP-701 | Alarm | J460-01-2XA-601 - Chilled Water Circulation Pump J460-01-1PMP-701 - Alarm | J460-01-2XA-601_ChlWtrCirPmpAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
1.0 | 57 | J270-06-1PNL-001 | J460-01-1PMP-701 | Measurement | J460-01-2SS-601 - Chilled Water Circulation Pump J460-01-1PMP-701 - Status | J460-01-2SS-601_ChlWtrCirPmpSts |  | STOP | RUN | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 58 | J270-06-1PNL-001 | J460-01-1PMP-701 | Alarm | J460-01-1PMP-701 - Chilled Water Circulation Pump - Fail to Start Alarm | J460-01-1PMP-701_FailToStartAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | M | - | bar: State 2 to State 64
1.0 | 59 | J270-06-1PNL-001 | J460-01-1PMP-701 | Alarm | J460-01-1PMP-701 - Chilled Water Circulation Pump - Fail to Stop Alarm | J460-01-1PMP-701_FailToStopAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 60 | J270-06-1PNL-001 | J460-01-1PMP-701 | Measurement | J460-01-2HSI-601 - Chilled Water Circulation Pump J460-01-1PMP-701 - Maintenance Switch | J460-01-2HSI-601_ChlWtrCirPmpMS |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 61 | J270-06-1PNL-001 | J460-01-2FT-701 | Alarm | J460-01-2FT-701 - Chilled Water - Energy Meter Communication Failure Alarm | J460-01-2FT-701_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 62 | J270-06-1PNL-001 | J460-01-2FT-701 | Measurement | J460-01-2FT-701 - Chilled Water - Energy Meter Flow | J460-01-2FT-701_Flow |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 63 | J270-06-1PNL-001 | J460-01-2FT-701 | Measurement | J460-01-2FT-701 - Chilled Water - Energy Meter Actual Power | J460-01-2FT-701_ActPwr |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | GJ | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 64 | J270-06-1PNL-001 | J460-01-2FT-701 | Measurement | J460-01-2FT-701 - Chilled Water - Energy Meter Inlet Temperature | J460-01-2FT-701_InlTemp |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 65 | J270-06-1PNL-001 | J460-01-2FT-701 | Measurement | J460-01-2FT-701 - Chilled Water - Energy Meter Outlet Temperature | J460-01-2FT-701_OutlTemp |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 66 | J270-06-1PNL-001 | J460-01-2FT-701 | Measurement | J460-01-2FT-701 - Chilled Water - Energy Meter Differential Temperature | J460-01-2FT-701_DiffTemp |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °K | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 67 | J270-06-1PNL-001 | J460-01-2FT-701 | Measurement | J460-01-2FT-701 - Chilled Water - Energy Meter Pressure | J460-01-2FT-701_Press |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 68 | J270-06-1PNL-001 | J460-01-2FT-701 | Measurement | J460-01-2FT-701 - Chilled Water - Energy Meter Heating Energy | J460-01-2FT-701_HtgEnergy |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kWh | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 69 | J270-06-1PNL-001 | J460-01-2FT-701 | Measurement | J460-01-2FT-701 - Chilled Water - Energy Meter Cooling Energy | J460-01-2FT-701_ClgEnergy |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kWh | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 70 | J270-06-1PNL-001 | J460-01-2FT-701 | Measurement | J460-01-2FT-701 - Chilled Water - Energy Meter Volume | J460-01-2FT-701_Volume |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³ | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 71 | J270-06-1PNL-001 | J460-01-2FT-701 | Measurement | J460-01-2FT-701 - Chilled Water - Energy Meter Runtime | J460-01-2FT-701_RunTime |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 72 | J270-06-1PNL-001 | J460-01-2FT-702 | Alarm | J460-01-2FT-702 - Hot Water - Energy Meter Communication Failure Alarm | J460-01-2FT-702_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 73 | J270-06-1PNL-001 | J460-01-2FT-702 | Measurement | J460-01-2FT-702 - Hot Water - Energy Meter Flow | J460-01-2FT-702_Flow |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 74 | J270-06-1PNL-001 | J460-01-2FT-702 | Measurement | J460-01-2FT-702 - Hot Water - Energy Meter Actual Power | J460-01-2FT-702_ActPwr |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | GJ | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 75 | J270-06-1PNL-001 | J460-01-2FT-702 | Measurement | J460-01-2FT-702 - Hot Water - Energy Meter Inlet Temperature | J460-01-2FT-702_InlTemp |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 76 | J270-06-1PNL-001 | J460-01-2FT-702 | Measurement | J460-01-2FT-702 - Hot Water - Energy Meter Outlet Temperature | J460-01-2FT-702_OutlTemp |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 77 | J270-06-1PNL-001 | J460-01-2FT-702 | Measurement | J460-01-2FT-702 - Hot Water - Energy Meter Differential Temperature | J460-01-2FT-702_DiffTemp |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | °K | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 78 | J270-06-1PNL-001 | J460-01-2FT-702 | Measurement | J460-01-2FT-702 - Hot Water - Energy Meter Pressure | J460-01-2FT-702_Press |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 79 | J270-06-1PNL-001 | J460-01-2FT-702 | Measurement | J460-01-2FT-702 - Hot Water - Energy Meter Heating Energy | J460-01-2FT-702_HtgEnergy |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kWh | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 80 | J270-06-1PNL-001 | J460-01-2FT-702 | Measurement | J460-01-2FT-702 - Hot Water - Energy Meter Cooling Energy | J460-01-2FT-702_ClgEnergy |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | kWh | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 81 | J270-06-1PNL-001 | J460-01-2FT-702 | Measurement | J460-01-2FT-702 - Hot Water - Energy Meter Volume | J460-01-2FT-702_Volume |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³ | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 82 | J270-06-1PNL-001 | J460-01-2FT-702 | Measurement | J460-01-2FT-702 - Hot Water - Energy Meter Runtime | J460-01-2FT-702_RunTime |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 91 | J270-06-1PNL-001 | J460-01-2FT-704 | Measurement | J460-01-2FT-704 - 61LBK3 - Return Air Flow | J460-01-2FT-704_RetAirFlow |  | 0 | 6507 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 92 | J270-06-1PNL-001 | J460-01-2FT-704 | Measurement | J460-01-2FT-704 - 61LBK3 - Return Air Flow Field | J460-01-2FT-704_RetAirFlow_Field |  | 0 | 6507 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 93 | J270-06-1PNL-001 | J460-01-2FT-704 | Alarm | J460-01-2FT-704 - 61LBK3 - Return Air Flow High Alarm | J460-01-2FT-704_RetAirFlowHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 94 | J270-06-1PNL-001 | J460-01-2FT-704 | Setting | J460-01-2FT-704 - 61LBK3 - Return Air Flow | J460-01-2FT-704_RetAirFlow_HASP |  | - | 4200 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 95 | J270-06-1PNL-001 | J460-01-2FT-704 | Alarm | J460-01-2FT-704 - 61LBK3 - Return Air Flow Low Alarm | J460-01-2FT-704_RetAirFlowLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 96 | J270-06-1PNL-001 | J460-01-2FT-704 | Setting | J460-01-2FT-704 - 61LBK3 - Return Air Flow | J460-01-2FT-704_RetAirFlow_LASP |  | 3800 | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 97 | J270-06-1PNL-001 | J460-01-2FT-704 | Setting | J460-01-2FT-704 - 61LBK3 - Return Air Flow Calibration Mode Selection | J460-01-2FT-704_RetAirFlowCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 98 | J270-06-1PNL-001 | J460-01-2FT-704 | Alarm | J460-01-2FT-704 - 61LBK3 - Return Air Flow Calibration Still Active Alarm | J460-01-2FT-704_RetAirFlowCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 107 | J270-06-1PNL-001 | J460-01-2TT-714 | Measurement | J460-01-2TT-714 - 61LBK3 - Return Air Temperature | J460-01-2TT-714_RetAirTemp |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 108 | J270-06-1PNL-001 | J460-01-2TT-714 | Measurement | J460-01-2TT-714 - 61LBK3 - Return Air Temperature Field | J460-01-2TT-714_RetAirTemp_Field |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 109 | J270-06-1PNL-001 | J460-01-2TT-714 | Alarm | J460-01-2TT-714 - 61LBK3 - Return Air Temperature High Alarm | J460-01-2TT-714_RetAirTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 110 | J270-06-1PNL-001 | J460-01-2TT-714 | Setting | J460-01-2TT-714 - 61LBK3 - Return Air Temperature | J460-01-2TT-714_RetAirTemp_HASP |  | - | 26 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 111 | J270-06-1PNL-001 | J460-01-2TT-714 | Alarm | J460-01-2TT-714 - 61LBK3 - Return Air Temperature Low Alarm | J460-01-2TT-714_RetAirTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 112 | J270-06-1PNL-001 | J460-01-2TT-714 | Setting | J460-01-2TT-714 - 61LBK3 - Return Air Temperature | J460-01-2TT-714_RetAirTemp_LASP |  | 16 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 113 | J270-06-1PNL-001 | J460-01-2TT-714 | Setting | J460-01-2TT-714 - 61LBK3 - Return Air Temperature Calibration Mode Selection | J460-01-2TT-714_RetAirTempCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 114 | J270-06-1PNL-001 | J460-01-2TT-714 | Alarm | J460-01-2TT-714 - 61LBK3 - Return Air Temperature Calibration Still Active Alarm | J460-01-2TT-714_RetAirTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 83 | J270-06-1PNL-001 | J460-01-2FT-703 | Measurement | J460-01-2FT-703 - 61LBK3 - Supply Air Flow | J460-01-2FT-703_SupAirFlow |  | 0 | 5258 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 84 | J270-06-1PNL-001 | J460-01-2FT-703 | Measurement | J460-01-2FT-703 - 61LBK3 - Supply Air Flow Field | J460-01-2FT-703_SupAirFlow_Field |  | 0 | 5258 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 85 | J270-06-1PNL-001 | J460-01-2FT-703 | Alarm | J460-01-2FT-703 - 61LBK3 - Supply Air Flow High Alarm | J460-01-2FT-703_SupAirFlowHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 86 | J270-06-1PNL-001 | J460-01-2FT-703 | Setting | J460-01-2FT-703 - 61LBK3 - Supply Air Flow | J460-01-2FT-703_SupAirFlow_HASP |  | - | 4200 | 3800 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | -
1.0 | 87 | J270-06-1PNL-001 | J460-01-2FT-703 | Alarm | J460-01-2FT-703 - 61LBK3 - Supply Air Flow Low Alarm | J460-01-2FT-703_SupAirFlowLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 88 | J270-06-1PNL-001 | J460-01-2FT-703 | Setting | J460-01-2FT-703 - 61LBK3 - Supply Air Flow | J460-01-2FT-703_SupAirFlow_LASP |  | 3800 | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 89 | J270-06-1PNL-001 | J460-01-2FT-703 | Setting | J460-01-2FT-703 - 61LBK3 - Supply Air Flow Calibration Mode Selection | J460-01-2FT-703_SupAirFlowCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 90 | J270-06-1PNL-001 | J460-01-2FT-703 | Alarm | J460-01-2FT-703 - 61LBK3 - Supply Air Flow Calibration Still Active Alarm | J460-01-2FT-703_SupAirFlowCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 99 | J270-06-1PNL-001 | J460-01-2TT-711 | Measurement | J460-01-2TT-711 - 61LBK3 - Supply Air Temperature | J460-01-2TT-711_SupAirTemp |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 100 | J270-06-1PNL-001 | J460-01-2TT-711 | Measurement | J460-01-2TT-711 - 61LBK3 - Supply Air Temperature Field | J460-01-2TT-711_SupAirTemp_Field |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 101 | J270-06-1PNL-001 | J460-01-2TT-711 | Alarm | J460-01-2TT-711 - 61LBK3 - Supply Air Temperature High Alarm | J460-01-2TT-711_SupAirTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 102 | J270-06-1PNL-001 | J460-01-2TT-711 | Setting | J460-01-2TT-711 - 61LBK3 - Supply Air Temperature | J460-01-2TT-711_SupAirTemp_HASP |  | - | 21 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 103 | J270-06-1PNL-001 | J460-01-2TT-711 | Alarm | J460-01-2TT-711 - 61LBK3 - Supply Air Temperature Low Alarm | J460-01-2TT-711_SupAirTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 104 | J270-06-1PNL-001 | J460-01-2TT-711 | Setting | J460-01-2TT-711 - 61LBK3 - Supply Air Temperature | J460-01-2TT-711_SupAirTemp_LASP |  | 15 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 105 | J270-06-1PNL-001 | J460-01-2TT-711 | Setting | J460-01-2TT-711 - 61LBK3 - Supply Air Temperature Calibration Mode Selection | J460-01-2TT-711_SupAirTempCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 106 | J270-06-1PNL-001 | J460-01-2TT-711 | Alarm | J460-01-2TT-711 - 61LBK3 - Supply Air Temperature Calibration Still Active Alarm | J460-01-2TT-711_SupAirTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 115 | J270-06-1PNL-001 | J460-01-2MT-711 | Measurement | J460-01-2MT-711 - 61LBK3 - Supply Air Humidity | J460-01-2MT-711_SupAirHum |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 116 | J270-06-1PNL-001 | J460-01-2MT-711 | Measurement | J460-01-2MT-711 - 61LBK3 - Supply Air Humidity Field | J460-01-2MT-711_SupAirHum_Field |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 117 | J270-06-1PNL-001 | J460-01-2MT-711 | Alarm | J460-01-2MT-711 - 61LBK3 - Supply Air Humidity High Alarm | J460-01-2MT-711_SupAirHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 118 | J270-06-1PNL-001 | J460-01-2MT-711 | Setting | J460-01-2MT-711 - 61LBK3 - Supply Air Humidity | J460-01-2MT-711_SupAirHum_HASP |  | - | 80 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 119 | J270-06-1PNL-001 | J460-01-2MT-711 | Alarm | J460-01-2MT-711 - 61LBK3 - Supply Air Humidity Low Alarm | J460-01-2MT-711_SupAirHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 120 | J270-06-1PNL-001 | J460-01-2MT-711 | Setting | J460-01-2MT-711 - 61LBK3 - Supply Air Humidity | J460-01-2MT-711_SupAirHum_LASP |  | 30 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 121 | J270-06-1PNL-001 | J460-01-2MT-711 | Setting | J460-01-2MT-711 - 61LBK3 - Supply Air Humidity Calibration Mode Selection | J460-01-2MT-711_SupAirHumCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 122 | J270-06-1PNL-001 | J460-01-2MT-711 | Alarm | J460-01-2MT-711 - 61LBK3 - Supply Air Humidity Calibration Still Active Alarm | J460-01-2MT-711_SupAirHumCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 91 | J270-06-1PNL-001 | J460-02-2FT-702 | Measurement | J460-02-2FT-702 - 61LBK3 - Return Air Flow | J460-02-2FT-702_RetAirFlow |  | 0 | 6507 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 92 | J270-06-1PNL-001 | J460-02-2FT-702 | Measurement | J460-02-2FT-702 - 61LBK3 - Return Air Flow Field | J460-02-2FT-702_RetAirFlow_Field |  | 0 | 6507 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 93 | J270-06-1PNL-001 | J460-02-2FT-702 | Alarm | J460-02-2FT-702 - 61LBK3 - Return Air Flow High Alarm | J460-02-2FT-702_RetAirFlowHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 94 | J270-06-1PNL-001 | J460-02-2FT-702 | Setting | J460-02-2FT-702 - 61LBK3 - Return Air Flow | J460-02-2FT-702_RetAirFlow_HASP |  | - | 4200 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 95 | J270-06-1PNL-001 | J460-02-2FT-702 | Alarm | J460-02-2FT-702 - 61LBK3 - Return Air Flow Low Alarm | J460-02-2FT-702_RetAirFlowLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 96 | J270-06-1PNL-001 | J460-02-2FT-702 | Setting | J460-02-2FT-702 - 61LBK3 - Return Air Flow | J460-02-2FT-702_RetAirFlow_LASP |  | 3800 | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 97 | J270-06-1PNL-001 | J460-02-2FT-702 | Setting | J460-02-2FT-702 - 61LBK3 - Return Air Flow Calibration Mode Selection | J460-02-2FT-702_RetAirFlowCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 98 | J270-06-1PNL-001 | J460-02-2FT-702 | Alarm | J460-02-2FT-702 - 61LBK3 - Return Air Flow Calibration Still Active Alarm | J460-02-2FT-702_RetAirFlowCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 107 | J270-06-1PNL-001 | J460-02-2TT-710 | Measurement | J460-02-2TT-710 - 61LBK3 - Return Air Temperature | J460-02-2TT-710_RetAirTemp |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 108 | J270-06-1PNL-001 | J460-02-2TT-710 | Measurement | J460-02-2TT-710 - 61LBK3 - Return Air Temperature Field | J460-02-2TT-710_RetAirTemp_Field |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 109 | J270-06-1PNL-001 | J460-02-2TT-710 | Alarm | J460-02-2TT-710 - 61LBK3 - Return Air Temperature High Alarm | J460-02-2TT-710_RetAirTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 110 | J270-06-1PNL-001 | J460-02-2TT-710 | Setting | J460-02-2TT-710 - 61LBK3 - Return Air Temperature | J460-02-2TT-710_RetAirTemp_HASP |  | - | 26 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 111 | J270-06-1PNL-001 | J460-02-2TT-710 | Alarm | J460-02-2TT-710 - 61LBK3 - Return Air Temperature Low Alarm | J460-02-2TT-710_RetAirTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 112 | J270-06-1PNL-001 | J460-02-2TT-710 | Setting | J460-02-2TT-710 - 61LBK3 - Return Air Temperature | J460-02-2TT-710_RetAirTemp_LASP |  | 16 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 113 | J270-06-1PNL-001 | J460-02-2TT-710 | Setting | J460-02-2TT-710 - 61LBK3 - Return Air Temperature Calibration Mode Selection | J460-02-2TT-710_RetAirTempCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 114 | J270-06-1PNL-001 | J460-02-2TT-710 | Alarm | J460-02-2TT-710 - 61LBK3 - Return Air Temperature Calibration Still Active Alarm | J460-02-2TT-710_RetAirTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 83 | J270-06-1PNL-001 | J460-02-2FT-701 | Measurement | J460-02-2FT-701 - 61LBK3 - Supply Air Flow | J460-02-2FT-701_SupAirFlow |  | 0 | 5258 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 84 | J270-06-1PNL-001 | J460-02-2FT-701 | Measurement | J460-02-2FT-701 - 61LBK3 - Supply Air Flow Field | J460-02-2FT-701_SupAirFlow_Field |  | 0 | 5258 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 85 | J270-06-1PNL-001 | J460-02-2FT-701 | Alarm | J460-02-2FT-701 - 61LBK3 - Supply Air Flow High Alarm | J460-02-2FT-701_SupAirFlowHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 86 | J270-06-1PNL-001 | J460-02-2FT-701 | Setting | J460-02-2FT-701 - 61LBK3 - Supply Air Flow | J460-02-2FT-701_SupAirFlow_HASP |  | - | 4200 | 3800 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | -
1.0 | 87 | J270-06-1PNL-001 | J460-02-2FT-701 | Alarm | J460-02-2FT-701 - 61LBK3 - Supply Air Flow Low Alarm | J460-02-2FT-701_SupAirFlowLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 88 | J270-06-1PNL-001 | J460-02-2FT-701 | Setting | J460-02-2FT-701 - 61LBK3 - Supply Air Flow | J460-02-2FT-701_SupAirFlow_LASP |  | 3800 | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 89 | J270-06-1PNL-001 | J460-02-2FT-701 | Setting | J460-02-2FT-701 - 61LBK3 - Supply Air Flow Calibration Mode Selection | J460-02-2FT-701_SupAirFlowCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 90 | J270-06-1PNL-001 | J460-02-2FT-701 | Alarm | J460-02-2FT-701 - 61LBK3 - Supply Air Flow Calibration Still Active Alarm | J460-02-2FT-701_SupAirFlowCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 99 | J270-06-1PNL-001 | J460-02-2TT-709 | Measurement | J460-02-2TT-709 - 61LBK3 - Supply Air Temperature | J460-02-2TT-709_SupAirTemp |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 100 | J270-06-1PNL-001 | J460-02-2TT-709 | Measurement | J460-02-2TT-709 - 61LBK3 - Supply Air Temperature Field | J460-02-2TT-709_SupAirTemp_Field |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 101 | J270-06-1PNL-001 | J460-02-2TT-709 | Alarm | J460-02-2TT-709 - 61LBK3 - Supply Air Temperature High Alarm | J460-02-2TT-709_SupAirTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 102 | J270-06-1PNL-001 | J460-02-2TT-709 | Setting | J460-02-2TT-709 - 61LBK3 - Supply Air Temperature | J460-02-2TT-709_SupAirTemp_HASP |  | - | 21 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 103 | J270-06-1PNL-001 | J460-02-2TT-709 | Alarm | J460-02-2TT-709 - 61LBK3 - Supply Air Temperature Low Alarm | J460-02-2TT-709_SupAirTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 104 | J270-06-1PNL-001 | J460-02-2TT-709 | Setting | J460-02-2TT-709 - 61LBK3 - Supply Air Temperature | J460-02-2TT-709_SupAirTemp_LASP |  | 15 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 105 | J270-06-1PNL-001 | J460-02-2TT-709 | Setting | J460-02-2TT-709 - 61LBK3 - Supply Air Temperature Calibration Mode Selection | J460-02-2TT-709_SupAirTempCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 106 | J270-06-1PNL-001 | J460-02-2TT-709 | Alarm | J460-02-2TT-709 - 61LBK3 - Supply Air Temperature Calibration Still Active Alarm | J460-02-2TT-709_SupAirTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 115 | J270-06-1PNL-001 | J460-02-2MT-709 | Measurement | J460-02-2MT-709 - 61LBK3 - Supply Air Humidity | J460-02-2MT-709_SupAirHum |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 116 | J270-06-1PNL-001 | J460-02-2MT-709 | Measurement | J460-02-2MT-709 - 61LBK3 - Supply Air Humidity Field | J460-02-2MT-709_SupAirHum_Field |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 117 | J270-06-1PNL-001 | J460-02-2MT-709 | Alarm | J460-02-2MT-709 - 61LBK3 - Supply Air Humidity High Alarm | J460-02-2MT-709_SupAirHumHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 118 | J270-06-1PNL-001 | J460-02-2MT-709 | Setting | J460-02-2MT-709 - 61LBK3 - Supply Air Humidity | J460-02-2MT-709_SupAirHum_HASP |  | - | 80 | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 119 | J270-06-1PNL-001 | J460-02-2MT-709 | Alarm | J460-02-2MT-709 - 61LBK3 - Supply Air Humidity Low Alarm | J460-02-2MT-709_SupAirHumLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.1 | 120 | J270-06-1PNL-001 | J460-02-2MT-709 | Setting | J460-02-2MT-709 - 61LBK3 - Supply Air Humidity | J460-02-2MT-709_SupAirHum_LASP |  | 30 | - | [11 empty] | - | - | - | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 121 | J270-06-1PNL-001 | J460-02-2MT-709 | Setting | J460-02-2MT-709 - 61LBK3 - Supply Air Humidity Calibration Mode Selection | J460-02-2MT-709_SupAirHumCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 122 | J270-06-1PNL-001 | J460-02-2MT-709 | Alarm | J460-02-2MT-709 - 61LBK3 - Supply Air Humidity Calibration Still Active Alarm | J460-02-2MT-709_SupAirHumCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 123 | J270-06-1PNL-001 | J130-07-2TT-001 | Measurement | J130-07-2TT-001 - Potable Water - Temperature | J130-07-2TT-001_PotWtrSupTemp |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 124 | J270-06-1PNL-001 | J130-07-2TT-001 | Measurement | J130-07-2TT-001 - Potable Water - Temperature Field | J130-07-2TT-001_PotWtrSupTemp_Field |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 125 | J270-06-1PNL-001 | J130-07-2TT-001 | Alarm | J130-07-2TT-001 - Potable Water - Temperature High Alarm | J130-07-2TT-001_PotWtrSupTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 126 | J270-06-1PNL-001 | J130-07-2TT-001 | Setting | J130-07-2TT-001 - Potable Water - Temperature | J130-07-2TT-001_PotWtrSupTemp_HASP |  | - | 30 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 127 | J270-06-1PNL-001 | J130-07-2TT-001 | Alarm | J130-07-2TT-001 - Potable Water - Temperature Low Alarm | J130-07-2TT-001_PotWtrSupTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 128 | J270-06-1PNL-001 | J130-07-2TT-001 | Setting | J130-07-2TT-001 - Potable Water - Temperature | J130-07-2TT-001_PotWtrSupTemp_LASP |  | 15 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 129 | J270-06-1PNL-001 | J130-07-2TT-001 | Setting | J130-07-2TT-001 - Potable Water - Temperature Calibration Mode Selection | J130-07-2TT-001_PotWtrSupTempCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 130 | J270-06-1PNL-001 | J130-07-2TT-001 | Alarm | J130-07-2TT-001 - Potable Water - Temperature Calibration Still Active Alarm | J130-07-2TT-001_PotWtrSupTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 157 | J270-06-1PNL-001 | J130-07-2PT-001 | Measurement | J130-07-2PT-001 - Non Potable Water - Pressure | J130-07-2PT-001_NPotWtrSupPress |  | 0 | 6 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 158 | J270-06-1PNL-001 | J130-07-2PT-001 | Measurement | J130-07-2PT-001 - Non Potable Water - Pressure Field | J130-07-2PT-001_NPotWtrSupPress_Field |  | 0 | 6 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 159 | J270-06-1PNL-001 | J130-07-2PT-001 | Alarm | J130-07-2PT-001 - Non Potable Water - Pressure High Alarm | J130-07-2PT-001_NPotWtrSupPressHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 160 | J270-06-1PNL-001 | J130-07-2PT-001 | Setting | J130-07-2PT-001 - Non Potable Water - Pressure | J130-07-2PT-001_NPotWtrSupPress_HASP |  | - | 10 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 161 | J270-06-1PNL-001 | J130-07-2PT-001 | Alarm | J130-07-2PT-001 - Non Potable Water - Pressure Low Alarm | J130-07-2PT-001_NPotWtrSupPressLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 162 | J270-06-1PNL-001 | J130-07-2PT-001 | Setting | J130-07-2PT-001 - Non Potable Water - Pressure | J130-07-2PT-001_NPotWtrSupPress_LASP |  | 7 | - | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 163 | J270-06-1PNL-001 | J130-07-2PT-001 | Setting | J130-07-2PT-001 - Non Potable Water - Pressure Calibration Mode Selection | J130-07-2PT-001_NPotWtrSupPresCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 164 | J270-06-1PNL-001 | J130-07-2PT-001 | Alarm | J130-07-2PT-001 - Non Potable Water - Pressure Calibration Still Active Alarm | J130-07-2PT-001_NPotWtrSupPresCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 131 | J270-06-1PNL-001 | J130-07-2FT-001 | Alarm | J130-07-2FT-001 - Potable Water - Flow Communication Failure Alarm | J130-07-2FT-001_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 132 | J270-06-1PNL-001 | J130-07-2FT-001 | Measurement | J130-07-2FT-001 - Potable Water - Flow Fabrication Number | J130-07-2FT-001_FabNo |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 133 | J270-06-1PNL-001 | J130-07-2FT-001 | Measurement | J130-07-2FT-001 - Potable Water - Flow Cust. ID | J130-07-2FT-001_CustID |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 134 | J270-06-1PNL-001 | J130-07-2FT-001 | Measurement | J130-07-2FT-001 - Potable Water - Flow Time Point | J130-07-2FT-001_TimePt |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 135 | J270-06-1PNL-001 | J130-07-2FT-001 | Measurement | J130-07-2FT-001 - Potable Water - Flow Bat. time | J130-07-2FT-001_BatTime |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 136 | J270-06-1PNL-001 | J130-07-2FT-001 | Measurement | J130-07-2FT-001 - Potable Water - Flow Volume | J130-07-2FT-001_Vol1 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 137 | J270-06-1PNL-001 | J130-07-2FT-001 | Measurement | J130-07-2FT-001 - Potable Water - Flow Volume [l]/Next VIFE Manufacturer specific | J130-07-2FT-001_NextVIFE |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 138 | J270-06-1PNL-001 | J130-07-2FT-001 | Measurement | J130-07-2FT-001 - Potable Water - Flow Volume | J130-07-2FT-001_Vol2 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 139 | J270-06-1PNL-001 | J130-07-2FT-001 | Measurement | J130-07-2FT-001 - Potable Water - Flow Manufacturer specific data structure | J130-07-2FT-001_Data |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 123 | J270-06-1PNL-001 | J100-07-2TT-001 | Measurement | J100-07-2TT-001 - Potable Water - Temperature | J100-07-2TT-001_PotWtrSupTemp |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 124 | J270-06-1PNL-001 | J100-07-2TT-001 | Measurement | J100-07-2TT-001 - Potable Water - Temperature Field | J100-07-2TT-001_PotWtrSupTemp_Field |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 125 | J270-06-1PNL-001 | J100-07-2TT-001 | Alarm | J100-07-2TT-001 - Potable Water - Temperature High Alarm | J100-07-2TT-001_PotWtrSupTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 126 | J270-06-1PNL-001 | J100-07-2TT-001 | Setting | J100-07-2TT-001 - Potable Water - Temperature | J100-07-2TT-001_PotWtrSupTemp_HASP |  | - | 30 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 127 | J270-06-1PNL-001 | J100-07-2TT-001 | Alarm | J100-07-2TT-001 - Potable Water - Temperature Low Alarm | J100-07-2TT-001_PotWtrSupTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 128 | J270-06-1PNL-001 | J100-07-2TT-001 | Setting | J100-07-2TT-001 - Potable Water - Temperature | J100-07-2TT-001_PotWtrSupTemp_LASP |  | 15 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 129 | J270-06-1PNL-001 | J100-07-2TT-001 | Setting | J100-07-2TT-001 - Potable Water - Temperature Calibration Mode Selection | J100-07-2TT-001_PotWtrSupTempCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 130 | J270-06-1PNL-001 | J100-07-2TT-001 | Alarm | J100-07-2TT-001 - Potable Water - Temperature Calibration Still Active Alarm | J100-07-2TT-001_PotWtrSupTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 131 | J270-06-1PNL-001 | J100-07-2FT-001 | Alarm | J100-07-2FT-001 - Potable Water - Flow Communication Failure Alarm | J100-07-2FT-001_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 132 | J270-06-1PNL-001 | J100-07-2FT-001 | Measurement | J100-07-2FT-001 - Potable Water - Flow Fabrication Number | J100-07-2FT-001_FabNo |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 133 | J270-06-1PNL-001 | J100-07-2FT-001 | Measurement | J100-07-2FT-001 - Potable Water - Flow Cust. ID | J100-07-2FT-001_CustID |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 134 | J270-06-1PNL-001 | J100-07-2FT-001 | Measurement | J100-07-2FT-001 - Potable Water - Flow Time Point | J100-07-2FT-001_TimePt |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 135 | J270-06-1PNL-001 | J100-07-2FT-001 | Measurement | J100-07-2FT-001 - Potable Water - Flow Bat. time | J100-07-2FT-001_BatTime |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 136 | J270-06-1PNL-001 | J100-07-2FT-001 | Measurement | J100-07-2FT-001 - Potable Water - Flow Volume | J100-07-2FT-001_Vol1 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 137 | J270-06-1PNL-001 | J100-07-2FT-001 | Measurement | J100-07-2FT-001 - Potable Water - Flow Volume [l]/Next VIFE Manufacturer specific | J100-07-2FT-001_NextVIFE |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 138 | J270-06-1PNL-001 | J100-07-2FT-001 | Measurement | J100-07-2FT-001 - Potable Water - Flow Volume | J100-07-2FT-001_Vol2 |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 139 | J270-06-1PNL-001 | J100-07-2FT-001 | Measurement | J100-07-2FT-001 - Potable Water - Flow Manufacturer specific data structure | J100-07-2FT-001_Data |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 174 | J270-06-1PNL-001 | J305-07-2FT-001 | Alarm | J305-07-2FT-001 - Compressed Air - Flow Meter Communication Failure Alarm | J305-07-2FT-001_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 175 | J270-06-1PNL-001 | J305-07-2FT-001 | Measurement | J305-07-2FT-001 - Compressed Air - Reset Alarm | J305-07-2FT-001_Reset |  | NORESET | RSTCNTR | RSTALM | RSTCNTR | RDISCNTR | RSTFWPRG | RAIERBIT | RAIWNBIT | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 176 | J270-06-1PNL-001 | J305-07-2FT-001 | Measurement | J305-07-2FT-001 - Compressed Air - Gas Flow Percentage | J305-07-2FT-001_FlowPerc |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 177 | J270-06-1PNL-001 | J305-07-2FT-001 | Measurement | J305-07-2FT-001 - Compressed Air - Gas Flow | J305-07-2FT-001_Flow |  | 4 | 750 | [11 empty] | - | - | - | - | - | - | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 178 | J270-06-1PNL-001 | J305-07-2FT-001 | Measurement | J305-07-2FT-001 - Compressed Air - Gas Flow Alarm | J305-07-2FT-001_Alm |  | - | ERROR | WARNING | - | MINALM | - | - | - | MAXALM | - | BCNTRALM | PWRUPALM | MSALARM | HWALARM | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 179 | J270-06-1PNL-001 | J305-07-2PT-001 | Measurement | J305-07-2PT-001 - Compressed Air - Pressure | J305-07-2PT-001_CompAirPress |  | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 180 | J270-06-1PNL-001 | J305-07-2PT-001 | Measurement | J305-07-2PT-001 - Compressed Air - Pressure Field | J305-07-2PT-001_CompAirPress_Field |  | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 181 | J270-06-1PNL-001 | J305-07-2PT-001 | Alarm | J305-07-2PT-001 - Compressed Air - Pressure High Alarm | J305-07-2PT-001_CompAirPressHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 182 | J270-06-1PNL-001 | J305-07-2PT-001 | Setting | J305-07-2PT-001 - Compressed Air - Pressure | J305-07-2PT-001_CompAirPress_HASP |  | - | 5 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 183 | J270-06-1PNL-001 | J305-07-2PT-001 | Alarm | J305-07-2PT-001 - Compressed Air - Pressure Low Alarm | J305-07-2PT-001_CompAirPressLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 184 | J270-06-1PNL-001 | J305-07-2PT-001 | Setting | J305-07-2PT-001 - Compressed Air - Pressure | J305-07-2PT-001_CompAirPress_LASP |  | 1 | - | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 185 | J270-06-1PNL-001 | J305-07-2PT-001 | Setting | J305-07-2PT-001 - Compressed Air - Pressure Calibration Mode Selection | J305-07-2PT-001_CompAirPressCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 186 | J270-06-1PNL-001 | J305-07-2PT-001 | Alarm | J305-07-2PT-001 - Compressed Air - Pressure Calibration Still Active Alarm | J305-07-2PT-001_CompAirPressCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 187 | J270-06-1PNL-001 | J305-07-2MT-001 | Measurement | J305-07-2MT-001 - Compressed Air - Dewpoint | J305-07-2MT-001_CompAirDP |  | -20 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 188 | J270-06-1PNL-001 | J305-07-2MT-001 | Measurement | J305-07-2MT-001 - Compressed Air - Dewpoint Field | J305-07-2MT-001_CompAirDP_Field |  | -20 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 189 | J270-06-1PNL-001 | J305-07-2MT-001 | Alarm | J305-07-2MT-001 - Compressed Air - Dewpoint High Alarm | J305-07-2MT-001_CompAirDPHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 190 | J270-06-1PNL-001 | J305-07-2MT-001 | Setting | J305-07-2MT-001 - Compressed Air - Dewpoint | J305-07-2MT-001_CompAirDP_HASP |  | - | 30 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 191 | J270-06-1PNL-001 | J305-07-2MT-001 | Alarm | J305-07-2MT-001 - Compressed Air - Dewpoint Low Alarm | J305-07-2MT-001_CompAirDPLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 192 | J270-06-1PNL-001 | J305-07-2MT-001 | Setting | J305-07-2MT-001 - Compressed Air - Dewpoint | J305-07-2MT-001_CompAirDP_LASP |  | 10 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 193 | J270-06-1PNL-001 | J305-07-2MT-001 | Setting | J305-07-2MT-001 - Compressed Air - Dewpoint Calibration Mode Selection | J305-07-2MT-001_CompAirDPCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 194 | J270-06-1PNL-001 | J305-07-2MT-001 | Alarm | J305-07-2MT-001 - Compressed Air - Dewpoint Calibration Still Active Alarm | J305-07-2MT-001_CompAirDPCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 174 | J270-06-1PNL-001 | J320-07-2FT-001 | Alarm | J320-07-2FT-001 - Compressed Air - Flow Meter Communication Failure Alarm | J320-07-2FT-001_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 175 | J270-06-1PNL-001 | J320-07-2FT-001 | Measurement | J320-07-2FT-001 - Compressed Air - Reset Alarm | J320-07-2FT-001_Reset |  | NORESET | RSTCNTR | RSTALM | RSTCNTR | RDISCNTR | RSTFWPRG | RAIERBIT | RAIWNBIT | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 176 | J270-06-1PNL-001 | J320-07-2FT-001 | Measurement | J320-07-2FT-001 - Compressed Air - Gas Flow Percentage | J320-07-2FT-001_FlowPerc |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 177 | J270-06-1PNL-001 | J320-07-2FT-001 | Measurement | J320-07-2FT-001 - Compressed Air - Gas Flow | J320-07-2FT-001_Flow |  | 4 | 750 | [11 empty] | - | - | - | - | - | - | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 178 | J270-06-1PNL-001 | J320-07-2FT-001 | Measurement | J320-07-2FT-001 - Compressed Air - Gas Flow Alarm | J320-07-2FT-001_Alm |  | - | ERROR | WARNING | - | MINALM | - | - | - | MAXALM | - | BCNTRALM | PWRUPALM | MSALARM | HWALARM | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 200 | J270-06-1PNL-001 | J320-07-2PT-001 | Measurement | J320-07-2PT-001 - Carbon Dioxide Gas - Pressure | J320-07-2PT-001_CO2Press |  | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 201 | J270-06-1PNL-001 | J320-07-2PT-001 | Measurement | J320-07-2PT-001 - Carbon Dioxide Gas - Pressure Field | J320-07-2PT-001_CO2Press_Field |  | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 202 | J270-06-1PNL-001 | J320-07-2PT-001 | Alarm | J320-07-2PT-001 - Carbon Dioxide Gas - Pressure High Alarm | J320-07-2PT-001_CO2PressHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 203 | J270-06-1PNL-001 | J320-07-2PT-001 | Setting | J320-07-2PT-001 - Carbon Dioxide Gas - Pressure | J320-07-2PT-001_CO2Press_HASP |  | - | 8 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 204 | J270-06-1PNL-001 | J320-07-2PT-001 | Alarm | J320-07-2PT-001 - Carbon Dioxide Gas - Pressure Low Alarm | J320-07-2PT-001_CO2PressLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 205 | J270-06-1PNL-001 | J320-07-2PT-001 | Setting | J320-07-2PT-001 - Carbon Dioxide Gas - Pressure | J320-07-2PT-001_CO2Press_LASP |  | 3 | - | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 206 | J270-06-1PNL-001 | J320-07-2PT-001 | Setting | J320-07-2PT-001 - Carbon Dioxide Gas - Pressure Calibration Mode Selection | J320-07-2PT-001_CO2PressCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 207 | J270-06-1PNL-001 | J320-07-2PT-001 | Alarm | J320-07-2PT-001 - Carbon Dioxide Gas - Pressure Calibration Still Active Alarm | J320-07-2PT-001_CO2PressCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 209 | J270-06-1PNL-001 | J330-07-2FT-001 | Measurement | J330-07-2FT-001 - Nitrogen Gas - Reset Alarm | J330-07-2FT-001_Reset |  | NORESET | RSTCNTR | RSTALM | RSTCNTR | RDISCNTR | RSTFWPRG | RAIERBIT | RAIWNBIT | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 210 | J270-06-1PNL-001 | J330-07-2FT-001 | Measurement | J330-07-2FT-001 - Nitrogen Gas - Gas Flow Percentage | J330-07-2FT-001_FlowPerc |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 211 | J270-06-1PNL-001 | J330-07-2FT-001 | Measurement | J330-07-2FT-001 - Nitrogen Gas - Gas Flow | J330-07-2FT-001_Flow |  | 0.6 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 212 | J270-06-1PNL-001 | J330-07-2FT-001 | Measurement | J330-07-2FT-001 - Nitrogen Gas - Gas Flow Alarm | J330-07-2FT-001_Alm |  | - | ERROR | WARNING | - | MINALM | - | - | - | MAXALM | - | BCNTRALM | PWRUPALM | MSALARM | HWALARM | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 208 | J270-06-1PNL-001 | J330-07-2PT-001 | Alarm | J330-06-2FT-001 - Nitrogen Gas - Flow Meter Communication Failure Alarm | J330-06-2FT-001_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 213 | J270-06-1PNL-001 | J330-07-2PT-001 | Measurement | J330-07-2PT-001 - Nitrogen Gas - Pressure | J330-07-2PT-001_NitroPress |  | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 214 | J270-06-1PNL-001 | J330-07-2PT-001 | Measurement | J330-07-2PT-001 - Nitrogen Gas - Pressure Field | J330-07-2PT-001_NitroPress_Field |  | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 215 | J270-06-1PNL-001 | J330-07-2PT-001 | Alarm | J330-07-2PT-001 - Nitrogen Gas - Pressure High Alarm | J330-07-2PT-001_NitroPressHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 216 | J270-06-1PNL-001 | J330-07-2PT-001 | Setting | J330-07-2PT-001 - Nitrogen Gas - Pressure | J330-07-2PT-001_NitroPress_HASP |  | - | 10 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 217 | J270-06-1PNL-001 | J330-07-2PT-001 | Alarm | J330-07-2PT-001 - Nitrogen Gas - Pressure Low Alarm | J330-07-2PT-001_NitroPressLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 218 | J270-06-1PNL-001 | J330-07-2PT-001 | Setting | J330-07-2PT-001 - Nitrogen Gas - Pressure | J330-07-2PT-001_NitroPress_LASP |  | 7 | - | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 219 | J270-06-1PNL-001 | J330-07-2PT-001 | Setting | J330-07-2PT-001 - Nitrogen Gas - Pressure Calibration Mode Selection | J330-07-2PT-001_NitroPressCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 220 | J270-06-1PNL-001 | J330-07-2PT-001 | Alarm | J330-07-2PT-001 - Nitrogen Gas - Pressure Calibration Still Active Alarm | J330-07-2PT-001_NitroPressCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 449 | J270-06-1PNL-001 | J140-07-2FT-002 | Measurement | J140-07-2FT-002 - Demi Water - Supply Flow | J140-07-2FT-002_DmiWtrSupFlow |  | 2 | 40 | [11 empty] | - | - | - | - | - | - | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 450 | J270-06-1PNL-001 | J140-07-2FT-002 | Measurement | J140-07-2FT-002 - Demi Water - Supply Flow Field | J140-07-2FT-002_DmiWtrSupFlow_Field |  | 2 | 40 | [11 empty] | - | - | - | - | - | - | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 451 | J270-06-1PNL-001 | J140-07-2FT-002 | Alarm | J140-07-2FT-002 - Demi Water - Supply Flow High Alarm | J140-07-2FT-002_DmiWtrSupFlowHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 452 | J270-06-1PNL-001 | J140-07-2FT-002 | Setting | J140-07-2FT-002 - Demi Water - Supply Flow | J140-07-2FT-002_DmiWtrSupFlow_HASP |  | - | 30 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 453 | J270-06-1PNL-001 | J140-07-2FT-002 | Alarm | J140-07-2FT-002 - Demi Water - Supply Flow Low Alarm | J140-07-2FT-002_DmiWtrSupFlowLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 454 | J270-06-1PNL-001 | J140-07-2FT-002 | Setting | J140-07-2FT-002 - Demi Water - Supply Flow | J140-07-2FT-002_DmiWtrSupFlow_LASP |  | 10 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 455 | J270-06-1PNL-001 | J140-07-2FT-002 | Setting | J140-07-2FT-002 - Demi Water - Supply Flow Calibration Mode Selection | J140-07-2FT-002_DmiWtrSupFlowCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 456 | J270-06-1PNL-001 | J140-07-2FT-002 | Alarm | J140-07-2FT-002 - Demi Water - Supply Flow Calibration Still Active Alarm | J140-07-2FT-002_DmiWtrSupFlowCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 449 | J270-06-1PNL-001 | J140-07-2FT-001 | Measurement | J140-07-2FT-001 - Demi Water - Supply Flow | J140-07-2FT-001_DmiWtrSupFlow |  | 2 | 40 | [11 empty] | - | - | - | - | - | - | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 450 | J270-06-1PNL-001 | J140-07-2FT-001 | Measurement | J140-07-2FT-001 - Demi Water - Supply Flow Field | J140-07-2FT-001_DmiWtrSupFlow_Field |  | 2 | 40 | [11 empty] | - | - | - | - | - | - | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 451 | J270-06-1PNL-001 | J140-07-2FT-001 | Alarm | J140-07-2FT-001 - Demi Water - Supply Flow High Alarm | J140-07-2FT-001_DmiWtrSupFlowHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 452 | J270-06-1PNL-001 | J140-07-2FT-001 | Setting | J140-07-2FT-001 - Demi Water - Supply Flow | J140-07-2FT-001_DmiWtrSupFlow_HASP |  | - | 30 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 453 | J270-06-1PNL-001 | J140-07-2FT-001 | Alarm | J140-07-2FT-001 - Demi Water - Supply Flow Low Alarm | J140-07-2FT-001_DmiWtrSupFlowLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 454 | J270-06-1PNL-001 | J140-07-2FT-001 | Setting | J140-07-2FT-001 - Demi Water - Supply Flow | J140-07-2FT-001_DmiWtrSupFlow_LASP |  | 10 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | L/min | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 455 | J270-06-1PNL-001 | J140-07-2FT-001 | Setting | J140-07-2FT-001 - Demi Water - Supply Flow Calibration Mode Selection | J140-07-2FT-001_DmiWtrSupFlowCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 456 | J270-06-1PNL-001 | J140-07-2FT-001 | Alarm | J140-07-2FT-001 - Demi Water - Supply Flow Calibration Still Active Alarm | J140-07-2FT-001_DmiWtrSupFlowCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 465 | J270-06-1PNL-001 | J140-07-2PT-001 | Measurement | J140-07-2PT-001 - Demi Water - Inlet Pressure | J140-07-2PT-001_DmiWtrInPress |  | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 466 | J270-06-1PNL-001 | J140-07-2PT-001 | Measurement | J140-07-2PT-001 - Demi Water - Inlet Pressure Field | J140-07-2PT-001_DmiWtrInPress_Field |  | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 467 | J270-06-1PNL-001 | J140-07-2PT-001 | Alarm | J140-07-2PT-001 - Demi Water - Inlet Pressure High Alarm | J140-07-2PT-001_DmiWtrInPressHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 468 | J270-06-1PNL-001 | J140-07-2PT-001 | Setting | J140-07-2PT-001 - Demi Water - Inlet Pressure | J140-07-2PT-001_DmiWtrInPress_HASP |  | - | 30 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 469 | J270-06-1PNL-001 | J140-07-2PT-001 | Alarm | J140-07-2PT-001 - Demi Water - Inlet Pressure Low Alarm | J140-07-2PT-001_DmiWtrInPressLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 470 | J270-06-1PNL-001 | J140-07-2PT-001 | Setting | J140-07-2PT-001 - Demi Water - Inlet Pressure | J140-07-2PT-001_DmiWtrInPress_LASP |  | 10 | - | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 471 | J270-06-1PNL-001 | J140-07-2PT-001 | Setting | J140-07-2PT-001 - Demi Water - Inlet Pressure Calibration Mode Selection | J140-07-2PT-001_DmiWtrInPressCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 472 | J270-06-1PNL-001 | J140-07-2PT-001 | Alarm | J140-07-2PT-001 - Demi Water - Inlet Pressure Calibration Still Active Alarm | J140-07-2PT-001_DmiWtrInPressCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 473 | J270-06-1PNL-001 | J140-07-2PT-002 | Measurement | J140-07-2PT-002 - Demi Water - Outlet Pressure | J140-07-2PT-002_DmiWtrOutPress |  | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 474 | J270-06-1PNL-001 | J140-07-2PT-002 | Measurement | J140-07-2PT-002 - Demi Water - Outlet Pressure Field | J140-07-2PT-002_DmiWtrOutPress_Field |  | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 475 | J270-06-1PNL-001 | J140-07-2PT-002 | Alarm | J140-07-2PT-002 - Demi Water - Outlet Pressure High Alarm | J140-07-2PT-002_DmiWtrOutPressHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 476 | J270-06-1PNL-001 | J140-07-2PT-002 | Setting | J140-07-2PT-002 - Demi Water - Outlet Pressure | J140-07-2PT-002_DmiWtrOutPress_HASP |  | - | 30 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 477 | J270-06-1PNL-001 | J140-07-2PT-002 | Alarm | J140-07-2PT-002 - Demi Water - Outlet Pressure Low Alarm | J140-07-2PT-002_DmiWtrOutPressLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 478 | J270-06-1PNL-001 | J140-07-2PT-002 | Setting | J140-07-2PT-002 - Demi Water - Outlet Pressure | J140-07-2PT-002_DmiWtrOutPress_LASP |  | 10 | - | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 479 | J270-06-1PNL-001 | J140-07-2PT-002 | Setting | J140-07-2PT-002 - Demi Water - Outlet Pressure Calibration Mode Selection | J140-07-2PT-002_DmiWtrOutPressCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 480 | J270-06-1PNL-001 | J140-07-2PT-002 | Alarm | J140-07-2PT-002 - Demi Water - Outlet Pressure Calibration Still Active Alarm | J140-07-2PT-002_DmiWtrOutPressCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 481 | J270-06-1PNL-001 | J140-07-2PT-003 | Measurement | J140-07-2PT-003 - Demi Water - Return Pressure | J140-07-2PT-003_DmiWtrRetPress |  | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 482 | J270-06-1PNL-001 | J140-07-2PT-003 | Measurement | J140-07-2PT-003 - Demi Water - Return Pressure Field | J140-07-2PT-003_DmiWtrRetPress_Field |  | 0 | 16 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 483 | J270-06-1PNL-001 | J140-07-2PT-003 | Alarm | J140-07-2PT-003 - Demi Water - Return Pressure High Alarm | J140-07-2PT-003_DmiWtrRetPressHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 484 | J270-06-1PNL-001 | J140-07-2PT-003 | Setting | J140-07-2PT-003 - Demi Water - Return Pressure | J140-07-2PT-003_DmiWtrRetPress_HASP |  | - | 30 | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 485 | J270-06-1PNL-001 | J140-07-2PT-003 | Alarm | J140-07-2PT-003 - Demi Water - Return Pressure Low Alarm | J140-07-2PT-003_DmiWtrRetPressLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 486 | J270-06-1PNL-001 | J140-07-2PT-003 | Setting | J140-07-2PT-003 - Demi Water - Return Pressure | J140-07-2PT-003_DmiWtrRetPress_LASP |  | 10 | - | [11 empty] | - | - | - | - | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 487 | J270-06-1PNL-001 | J140-07-2PT-003 | Setting | J140-07-2PT-003 - Demi Water - Return Pressure Calibration Mode Selection | J140-07-2PT-003_DmiWtrRetPressCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 488 | J270-06-1PNL-001 | J140-07-2PT-003 | Alarm | J140-07-2PT-003 - Demi Water - Return Pressure Calibration Still Active Alarm | J140-07-2PT-003_DmiWtrRetPressCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 9 | J270-06-1PNL-001 | J460-02-2TT-719 | Measurement | J460-02-2TT-719 - Chilled Water - Supply Temperature | J460-02-2TT-719_ChlWtrSupTemp |  | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 10 | J270-06-1PNL-001 | J460-02-2TT-719 | Measurement | J460-02-2TT-719 - Chilled Water - Supply Temperature Field | J460-02-2TT-719_ChlWtrSupTemp_Field |  | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 11 | J270-06-1PNL-001 | J460-02-2TT-719 | Alarm | J460-02-2TT-719 - Chilled Water - Supply Temperature High Alarm | J460-02-2TT-719_ChlWtrSupTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 12 | J270-06-1PNL-001 | J460-02-2TT-719 | Setting | J460-02-2TT-719 - Chilled Water - Supply Temperature | J460-02-2TT-719_ChlWtrSupTemp_HASP |  | - | 16 | [11 empty] | - | - | - | - | - | 0.5 | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 13 | J270-06-1PNL-001 | J460-02-2TT-719 | Alarm | J460-02-2TT-719 - Chilled Water - Supply Temperature Low Alarm | J460-02-2TT-719_ChlWtrSupTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 14 | J270-06-1PNL-001 | J460-02-2TT-719 | Setting | J460-02-2TT-719 - Chilled Water - Supply Temperature | J460-02-2TT-719_ChlWtrSupTemp_LASP |  | 6 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 15 | J270-06-1PNL-001 | J460-02-2TT-719 | Setting | J460-02-2TT-719 - Chilled Water - Supply Temperature Calibration Mode Selection | J460-02-2TT-719_ChlWtrSupTempCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 16 | J270-06-1PNL-001 | J460-02-2TT-719 | Alarm | J460-02-2TT-719 - Chilled Water - Supply Temperature Calibration Still Active Alarm | J460-02-2TT-719_ChlWtrSupTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 17 | J270-06-1PNL-001 | J460-02-2TT-719 | Setting | J460-02-2TT-719 - Chilled Water - Supply Temperature Setpoint | J460-02-2TT-719_ChlWtrSupTempSetpoint |  | 16 | - | [11 empty] | - | - | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 20 | J270-06-1PNL-001 | J460-02-2TT-719 | Setting | J460-02-2TT-719 - Chilled Water - Supply Temperature Proportional Band | J460-02-2TT-719_ChlWtrSupTemp_Set_P |  | 35 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 21 | J270-06-1PNL-001 | J460-02-2TT-719 | Setting | J460-02-2TT-719 - Chilled Water - Supply Temperature Integral Time | J460-02-2TT-719_ChlWtrSupTemp_Set_I |  | 180 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 22 | J270-06-1PNL-001 | J460-02-2TT-719 | Setting | J460-02-2TT-719 - Chilled Water - Supply Temperature Derivative Time | J460-02-2TT-719_ChlWtrSupTemp_Set_D |  | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 23 | J270-06-1PNL-001 | J460-02-2TT-720 | Measurement | J460-02-2TT-720 - Chilled Water - Return Temperature | J460-02-2TT-720_ChlWtrRetTemp |  | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 24 | J270-06-1PNL-001 | J460-02-2TT-720 | Measurement | J460-02-2TT-720 - Chilled Water - Return Temperature Field | J460-02-2TT-720_ChlWtrRetTemp_Field |  | -40 | 60 | [11 empty] | - | - | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 25 | J270-06-1PNL-001 | J460-02-2TT-720 | Alarm | J460-02-2TT-720 - Chilled Water - Return Temperature High Alarm | J460-02-2TT-720_ChlWtrRetTempHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 26 | J270-06-1PNL-001 | J460-02-2TT-720 | Setting | J460-02-2TT-720 - Chilled Water - Return Temperature | J460-02-2TT-720_ChlWtrRetTemp_HASP |  | - | 18.5 | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 3 to State 64
1.0 | 27 | J270-06-1PNL-001 | J460-02-2TT-720 | Alarm | J460-02-2TT-720 - Chilled Water - Return Temperature Low Alarm | J460-02-2TT-720_ChlWtrRetTempLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 3 | Y | - | bar: State 2 to State 64
2.1 | 28 | J270-06-1PNL-001 | J460-02-2TT-720 | Setting | J460-02-2TT-720 - Chilled Water - Return Temperature | J460-02-2TT-720_ChlWtrRetTemp_LASP |  | 12 | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 29 | J270-06-1PNL-001 | J460-02-2TT-720 | Setting | J460-02-2TT-720 - Chilled Water - Return Temperature Calibration Mode Selection | J460-02-2TT-720_ChlWtrRetTempCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 30 | J270-06-1PNL-001 | J460-02-2TT-720 | Alarm | J460-02-2TT-720 - Chilled Water - Return Temperature Calibration Still Active Alarm | J460-02-2TT-720_ChlWtrRetTempCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 31 | J270-06-1PNL-001 | J460-02-2FCV-728 | Alarm | J460-02-2FCV-728 - Chilled Water Valve - Controller Communication Failure Alarm | J460-02-2FCV-728_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 32 | J270-06-1PNL-001 | J460-02-2FCV-728 | Measurement | J460-02-2FCV-728 - Chilled Water Valve - Forced Position | J460-02-2FCV-728_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 33 | J270-06-1PNL-001 | J460-02-2FCV-728 | Setting | J460-02-2FCV-728 - Chilled Water Valve - Forced Calibration | J460-02-2FCV-728_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 34 | J270-06-1PNL-001 | J460-02-2FCV-728 | Measurement | J460-02-2FCV-728 - Chilled Water Valve - Status | J460-02-2FCV-728_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 35 | J270-06-1PNL-001 | J460-02-2FCV-728 | Measurement | J460-02-2FCV-728 - Chilled Water Valve - Actual SP | J460-02-2FCV-728_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 36 | J270-06-1PNL-001 | J460-02-2FCV-728 | Setting | J460-02-2FCV-728 - Chilled Water Valve - SP | J460-02-2FCV-728_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 37 | J270-06-1PNL-001 | J460-02-2FCV-728 | Alarm | J460-02-2FCV-728 - Chilled Water Valve - Controller Fail to Open Alarm | J460-02-2FCV-728_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 38 | J270-06-1PNL-001 | J460-02-2FCV-728 | Alarm | J460-02-2FCV-728 - Chilled Water Valve - Controller Fail to Close Alarm | J460-02-2FCV-728_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 39 | J270-06-1PNL-001 | J460-02-2FCV-728 | Measurement | J460-02-2FCV-728 - Chilled Water Valve - Error Code | J460-02-2FCV-728_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
| 2328 | J270-06-1PNL-001 | J460-02-2FCV-728 | Measurement | J460-02-2FCV-728 - Chilled Water Valve - Speed | J460-02-2FCV-728_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 40 | J270-06-1PNL-001 | J460-02-1PMP-701 | Alarm | J460-02-1PMP-701 - Chilled Water Circulation Pump - Controller Communication Failure Alarm | J460-02-1PMP-701_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 41 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Error Code | J460-02-1PMP-701_ErrCode |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 42 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Speed | J460-02-1PMP-701_Spd |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | rpm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 43 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Frequency | J460-02-1PMP-701_Frq |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 44 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Motor Current | J460-02-1PMP-701_MtrCur |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 45 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - DC Link Voltage | J460-02-1PMP-701_DCVolt |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 46 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Power | J460-02-1PMP-701_Pwr |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | W | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 47 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Run Time | J460-02-1PMP-701_RunTime |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 48 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Load Percentage | J460-02-1PMP-701_LdPerc |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 49 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Control Source | J460-02-1PMP-701_CntSrc |  | LOCCNT | BUSCNT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 50 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Rotation Status | J460-02-1PMP-701_Rot |  | NOROT | ROT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 51 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Actual Operation Mode | J460-02-1PMP-701_ActOpMode |  | - | START | STOP | MINIMUM | MAXIMUM | USERDEF | LOCMODE | EMGMODE | HANDMODE | UNKNOWN | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 52 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Operation Mode | J460-02-1PMP-701_OpMode |  | - | START | STOP | MINIMUM | MAXIMUM | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1.0 | 53 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2XS-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Enable | J460-01-2XS-601_ChlWtrCirPmpEna |  | DISABLE | ENABLE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 54 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2SC-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Control Signal | J460-01-2SC-601_ChlWtrCirPmpCntr |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 55 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2XA-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Alarm | J460-01-2XA-601_ChlWtrCirPmpAlm | R420-01-2XA-601_ChlWtrCirPmpAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 56 | J270-06-1PNL-001 | J460-02-1PMP-701 | Alarm | J460-01-2XA-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Alarm | J460-01-2XA-601_ChlWtrCirPmpAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
1.0 | 57 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2SS-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Status | J460-01-2SS-601_ChlWtrCirPmpSts |  | STOP | RUN | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 58 | J270-06-1PNL-001 | J460-02-1PMP-701 | Alarm | J460-02-1PMP-701 - Chilled Water Circulation Pump - Fail to Start Alarm | J460-02-1PMP-701_FailToStartAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | M | - | bar: State 2 to State 64
1.0 | 59 | J270-06-1PNL-001 | J460-02-1PMP-701 | Alarm | J460-02-1PMP-701 - Chilled Water Circulation Pump - Fail to Stop Alarm | J460-02-1PMP-701_FailToStopAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 60 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2HSI-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Maintenance Switch | J460-01-2HSI-601_ChlWtrCirPmpMS |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 40 | J270-06-1PNL-001 | J460-02-1PMP-701 | Alarm | J460-02-1PMP-701 - Chilled Water Circulation Pump - Controller Communication Failure Alarm | J460-02-1PMP-701_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 41 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Error Code | J460-02-1PMP-701_ErrCode |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 42 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Speed | J460-02-1PMP-701_Spd |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | rpm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 43 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Frequency | J460-02-1PMP-701_Frq |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 44 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Motor Current | J460-02-1PMP-701_MtrCur |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 45 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - DC Link Voltage | J460-02-1PMP-701_DCVolt |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 46 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Power | J460-02-1PMP-701_Pwr |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | W | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 47 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Run Time | J460-02-1PMP-701_RunTime |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 48 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Load Percentage | J460-02-1PMP-701_LdPerc |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 49 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Control Source | J460-02-1PMP-701_CntSrc |  | LOCCNT | BUSCNT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 50 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Rotation Status | J460-02-1PMP-701_Rot |  | NOROT | ROT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 51 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Actual Operation Mode | J460-02-1PMP-701_ActOpMode |  | - | START | STOP | MINIMUM | MAXIMUM | USERDEF | LOCMODE | EMGMODE | HANDMODE | UNKNOWN | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 52 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Operation Mode | J460-02-1PMP-701_OpMode |  | - | START | STOP | MINIMUM | MAXIMUM | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1.0 | 53 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2XS-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Enable | J460-01-2XS-601_ChlWtrCirPmpEna |  | DISABLE | ENABLE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 54 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2SC-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Control Signal | J460-01-2SC-601_ChlWtrCirPmpCntr |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 55 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2XA-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Alarm | J460-01-2XA-601_ChlWtrCirPmpAlm | R420-01-2XA-601_ChlWtrCirPmpAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 56 | J270-06-1PNL-001 | J460-02-1PMP-701 | Alarm | J460-01-2XA-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Alarm | J460-01-2XA-601_ChlWtrCirPmpAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
1.0 | 57 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2SS-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Status | J460-01-2SS-601_ChlWtrCirPmpSts |  | STOP | RUN | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 58 | J270-06-1PNL-001 | J460-02-1PMP-701 | Alarm | J460-02-1PMP-701 - Chilled Water Circulation Pump - Fail to Start Alarm | J460-02-1PMP-701_FailToStartAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | M | - | bar: State 2 to State 64
1.0 | 59 | J270-06-1PNL-001 | J460-02-1PMP-701 | Alarm | J460-02-1PMP-701 - Chilled Water Circulation Pump - Fail to Stop Alarm | J460-02-1PMP-701_FailToStopAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 60 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2HSI-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Maintenance Switch | J460-01-2HSI-601_ChlWtrCirPmpMS |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 40 | J270-06-1PNL-001 | J460-02-1PMP-701 | Alarm | J460-02-1PMP-701 - Chilled Water Circulation Pump - Controller Communication Failure Alarm | J460-02-1PMP-701_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 41 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Error Code | J460-02-1PMP-701_ErrCode |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 42 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Speed | J460-02-1PMP-701_Spd |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | rpm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 43 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Frequency | J460-02-1PMP-701_Frq |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 44 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Motor Current | J460-02-1PMP-701_MtrCur |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 45 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - DC Link Voltage | J460-02-1PMP-701_DCVolt |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 46 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Power | J460-02-1PMP-701_Pwr |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | W | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 47 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Run Time | J460-02-1PMP-701_RunTime |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 48 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Load Percentage | J460-02-1PMP-701_LdPerc |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 49 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Control Source | J460-02-1PMP-701_CntSrc |  | LOCCNT | BUSCNT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 50 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Rotation Status | J460-02-1PMP-701_Rot |  | NOROT | ROT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 51 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Actual Operation Mode | J460-02-1PMP-701_ActOpMode |  | - | START | STOP | MINIMUM | MAXIMUM | USERDEF | LOCMODE | EMGMODE | HANDMODE | UNKNOWN | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 52 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Operation Mode | J460-02-1PMP-701_OpMode |  | - | START | STOP | MINIMUM | MAXIMUM | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1.0 | 53 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2XS-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Enable | J460-01-2XS-601_ChlWtrCirPmpEna |  | DISABLE | ENABLE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 54 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2SC-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Control Signal | J460-01-2SC-601_ChlWtrCirPmpCntr |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 55 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2XA-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Alarm | J460-01-2XA-601_ChlWtrCirPmpAlm | R420-01-2XA-601_ChlWtrCirPmpAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 56 | J270-06-1PNL-001 | J460-02-1PMP-701 | Alarm | J460-01-2XA-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Alarm | J460-01-2XA-601_ChlWtrCirPmpAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
1.0 | 57 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2SS-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Status | J460-01-2SS-601_ChlWtrCirPmpSts |  | STOP | RUN | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 58 | J270-06-1PNL-001 | J460-02-1PMP-701 | Alarm | J460-02-1PMP-701 - Chilled Water Circulation Pump - Fail to Start Alarm | J460-02-1PMP-701_FailToStartAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | M | - | bar: State 2 to State 64
1.0 | 59 | J270-06-1PNL-001 | J460-02-1PMP-701 | Alarm | J460-02-1PMP-701 - Chilled Water Circulation Pump - Fail to Stop Alarm | J460-02-1PMP-701_FailToStopAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 60 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2HSI-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Maintenance Switch | J460-01-2HSI-601_ChlWtrCirPmpMS |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 40 | J270-06-1PNL-001 | J460-02-1PMP-701 | Alarm | J460-02-1PMP-701 - Chilled Water Circulation Pump - Controller Communication Failure Alarm | J460-02-1PMP-701_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 41 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Error Code | J460-02-1PMP-701_ErrCode |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 42 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Speed | J460-02-1PMP-701_Spd |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | rpm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 43 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Frequency | J460-02-1PMP-701_Frq |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 44 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Motor Current | J460-02-1PMP-701_MtrCur |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 45 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - DC Link Voltage | J460-02-1PMP-701_DCVolt |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 46 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Power | J460-02-1PMP-701_Pwr |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | W | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 47 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Run Time | J460-02-1PMP-701_RunTime |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 48 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Load Percentage | J460-02-1PMP-701_LdPerc |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 49 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Control Source | J460-02-1PMP-701_CntSrc |  | LOCCNT | BUSCNT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 50 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Rotation Status | J460-02-1PMP-701_Rot |  | NOROT | ROT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 51 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Actual Operation Mode | J460-02-1PMP-701_ActOpMode |  | - | START | STOP | MINIMUM | MAXIMUM | USERDEF | LOCMODE | EMGMODE | HANDMODE | UNKNOWN | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 52 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Operation Mode | J460-02-1PMP-701_OpMode |  | - | START | STOP | MINIMUM | MAXIMUM | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1.0 | 53 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2XS-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Enable | J460-01-2XS-601_ChlWtrCirPmpEna |  | DISABLE | ENABLE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 54 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2SC-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Control Signal | J460-01-2SC-601_ChlWtrCirPmpCntr |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 55 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2XA-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Alarm | J460-01-2XA-601_ChlWtrCirPmpAlm | R420-01-2XA-601_ChlWtrCirPmpAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 56 | J270-06-1PNL-001 | J460-02-1PMP-701 | Alarm | J460-01-2XA-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Alarm | J460-01-2XA-601_ChlWtrCirPmpAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
1.0 | 57 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2SS-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Status | J460-01-2SS-601_ChlWtrCirPmpSts |  | STOP | RUN | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 58 | J270-06-1PNL-001 | J460-02-1PMP-701 | Alarm | J460-02-1PMP-701 - Chilled Water Circulation Pump - Fail to Start Alarm | J460-02-1PMP-701_FailToStartAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | M | - | bar: State 2 to State 64
1.0 | 59 | J270-06-1PNL-001 | J460-02-1PMP-701 | Alarm | J460-02-1PMP-701 - Chilled Water Circulation Pump - Fail to Stop Alarm | J460-02-1PMP-701_FailToStopAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 60 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2HSI-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Maintenance Switch | J460-01-2HSI-601_ChlWtrCirPmpMS |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 40 | J270-06-1PNL-001 | J460-02-1PMP-701 | Alarm | J460-02-1PMP-701 - Chilled Water Circulation Pump - Controller Communication Failure Alarm | J460-02-1PMP-701_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 41 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Error Code | J460-02-1PMP-701_ErrCode |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 42 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Speed | J460-02-1PMP-701_Spd |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | rpm | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 43 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Frequency | J460-02-1PMP-701_Frq |  | 0 | 50 | [11 empty] | - | - | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 44 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Motor Current | J460-02-1PMP-701_MtrCur |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 45 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - DC Link Voltage | J460-02-1PMP-701_DCVolt |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 46 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Power | J460-02-1PMP-701_Pwr |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | W | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 47 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Run Time | J460-02-1PMP-701_RunTime |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 48 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Load Percentage | J460-02-1PMP-701_LdPerc |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 49 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Control Source | J460-02-1PMP-701_CntSrc |  | LOCCNT | BUSCNT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 50 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Rotation Status | J460-02-1PMP-701_Rot |  | NOROT | ROT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 51 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Actual Operation Mode | J460-02-1PMP-701_ActOpMode |  | - | START | STOP | MINIMUM | MAXIMUM | USERDEF | LOCMODE | EMGMODE | HANDMODE | UNKNOWN | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 52 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-02-1PMP-701 - Chilled Water Circulation Pump - Operation Mode | J460-02-1PMP-701_OpMode |  | - | START | STOP | MINIMUM | MAXIMUM | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1.0 | 53 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2XS-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Enable | J460-01-2XS-601_ChlWtrCirPmpEna |  | DISABLE | ENABLE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 54 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2SC-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Control Signal | J460-01-2SC-601_ChlWtrCirPmpCntr |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 55 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2XA-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Alarm | J460-01-2XA-601_ChlWtrCirPmpAlm | R420-01-2XA-601_ChlWtrCirPmpAlm | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 56 | J270-06-1PNL-001 | J460-02-1PMP-701 | Alarm | J460-01-2XA-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Alarm | J460-01-2XA-601_ChlWtrCirPmpAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
1.0 | 57 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2SS-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Status | J460-01-2SS-601_ChlWtrCirPmpSts |  | STOP | RUN | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 58 | J270-06-1PNL-001 | J460-02-1PMP-701 | Alarm | J460-02-1PMP-701 - Chilled Water Circulation Pump - Fail to Start Alarm | J460-02-1PMP-701_FailToStartAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | M | - | bar: State 2 to State 64
1.0 | 59 | J270-06-1PNL-001 | J460-02-1PMP-701 | Alarm | J460-02-1PMP-701 - Chilled Water Circulation Pump - Fail to Stop Alarm | J460-02-1PMP-701_FailToStopAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 60 | J270-06-1PNL-001 | J460-02-1PMP-701 | Measurement | J460-01-2HSI-601 - Chilled Water Circulation Pump J460-02-1PMP-701 - Maintenance Switch | J460-01-2HSI-601_ChlWtrCirPmpMS |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 519 | J270-06-1PNL-001 | J460-02-2PT-901 | Measurement | J460-02-2PT-901 - Exhaust Duct J460-02-1B-902 - Pressure | J460-02-2PT-901_ExhFanPress |  | 0 | 1000 | [11 empty] | - | - | - | - | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 520 | J270-06-1PNL-001 | J460-02-2PT-901 | Measurement | J460-02-2PT-901 - Exhaust Duct J460-02-1B-902 - Pressure Field | J460-02-2PT-901_ExhFanPress_Field |  | 0 | 1000 | [11 empty] | - | - | - | - | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 521 | J270-06-1PNL-001 | J460-02-2PT-901 | Alarm | J460-02-2PT-901 - Exhaust Duct J460-02-1B-902 - Pressure High Alarm | J460-02-2PT-901_ExhFanPressHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 522 | J270-06-1PNL-001 | J460-02-2PT-901 | Setting | J460-02-2PT-901 - Exhaust Duct J460-02-1B-902 - Pressure | J460-02-2PT-901_ExhFanPress_HASP |  | - | 350 | [11 empty] | - | - | - | - | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 523 | J270-06-1PNL-001 | J460-02-2PT-901 | Alarm | J460-02-2PT-901 - Exhaust Duct J460-02-1B-902 - Pressure Low Alarm | J460-02-2PT-901_ExhFanPressLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 524 | J270-06-1PNL-001 | J460-02-2PT-901 | Setting | J460-02-2PT-901 - Exhaust Duct J460-02-1B-902 - Pressure | J460-02-2PT-901_ExhFanPress_LASP |  | 250 | - | [11 empty] | - | - | - | - | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 525 | J270-06-1PNL-001 | J460-02-2PT-901 | Setting | J460-02-2PT-901 - Exhaust Duct J460-02-1B-902 - Pressure Calibration Mode Selection | J460-02-2PT-901_ExhFanPressCalModeSel |  | OFF | CALMDE | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 526 | J270-06-1PNL-001 | J460-02-2PT-901 | Alarm | J460-02-2PT-901 - Exhaust Duct J460-02-1B-902 - Pressure Calibration Still Active Alarm | J460-02-2PT-901_ExhFanPressCalModeAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.1 | 527 | J270-06-1PNL-001 | J460-02-2PT-901 | Setting | J460-02-2PT-901 - Exhaust Duct J460-02-1B-902 - Pressure Setpoint | J460-02-2PT-901_ExhFanPressSetpoint |  | 300 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 528 | J270-06-1PNL-001 | J460-02-2PT-901 | Setting | J460-02-2PT-901 - Exhaust Duct J460-02-1B-902 - Pressure Proportional Band | J460-02-2PT-901_ExhFanPress_Set_P |  | 1900 | - | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 529 | J270-06-1PNL-001 | J460-02-2PT-901 | Setting | J460-02-2PT-901 - Exhaust Duct J460-02-1B-902 - Pressure Integral Time | J460-02-2PT-901_ExhFanPress_Set_I |  | 200 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 530 | J270-06-1PNL-001 | J460-02-2PT-901 | Setting | J460-02-2PT-901 - Exhaust Duct J460-02-1B-902 - Pressure Derivative Time | J460-02-2PT-901_ExhFanPress_Set_D |  | 0 | - | [11 empty] | - | - | - | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 535 | J270-06-1PNL-001 | J460-01-2TC-701 | Alarm | J460-01-2TC-701 - Room J6.02 - Room Controller - Communication Failure Alarm | J460-01-2TC-701_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2139 | J270-06-1PNL-001 | J460-01-2FCV-701 | Alarm | J460-01-2FCV-701 - Room J6.14 - Reheater Valve Control - Communication Failure Alarm | J460-01-2FCV-701_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2140 | J270-06-1PNL-001 | J460-01-2FCV-701 | Measurement | J460-01-2FCV-701 - Room J6.14 - Reheater Valve Control Forced Position | J460-01-2FCV-701_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2141 | J270-06-1PNL-001 | J460-01-2FCV-701 | Setting | J460-01-2FCV-701 - Room J6.14 - Reheater Valve Control Forced Calibration | J460-01-2FCV-701_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2142 | J270-06-1PNL-001 | J460-01-2FCV-701 | Measurement | J460-01-2FCV-701 - Room J6.14 - Reheater Valve Control Status | J460-01-2FCV-701_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2143 | J270-06-1PNL-001 | J460-01-2FCV-701 | Measurement | J460-01-2FCV-701 - Room J6.14 - Reheater Valve Control Actual SP | J460-01-2FCV-701_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2144 | J270-06-1PNL-001 | J460-01-2FCV-701 | Setting | J460-01-2FCV-701 - Room J6.14 - Reheater Valve Control SP | J460-01-2FCV-701_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2145 | J270-06-1PNL-001 | J460-01-2FCV-701 | Alarm | J460-01-2FCV-701 - Room J6.14 - Reheater Valve Control Fail to Open Alarm | J460-01-2FCV-701_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2146 | J270-06-1PNL-001 | J460-01-2FCV-701 | Alarm | J460-01-2FCV-701 - Room J6.14 - Reheater Valve Control Fail to Close Alarm | J460-01-2FCV-701_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2147 | J270-06-1PNL-001 | J460-01-2FCV-701 | Measurement | J460-01-2FCV-701 - Room J6.14 - Reheater Valve Control Error Code | J460-01-2FCV-701_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2594 | J270-06-1PNL-001 | J460-01-2FCV-701 | Measurement | J460-01-2FCV-701 - Room J6.14 - Reheater Valve Control Speed | J460-01-2FCV-701_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 535 | J270-06-1PNL-001 | J460-01-2TC-702 | Alarm | J460-01-2TC-702 - Room J6.02 - Room Controller - Communication Failure Alarm | J460-01-2TC-702_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2139 | J270-06-1PNL-001 | J460-01-2FCV-702 | Alarm | J460-01-2FCV-702 - Room J6.14 - Reheater Valve Control - Communication Failure Alarm | J460-01-2FCV-702_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2140 | J270-06-1PNL-001 | J460-01-2FCV-702 | Measurement | J460-01-2FCV-702 - Room J6.14 - Reheater Valve Control Forced Position | J460-01-2FCV-702_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2141 | J270-06-1PNL-001 | J460-01-2FCV-702 | Setting | J460-01-2FCV-702 - Room J6.14 - Reheater Valve Control Forced Calibration | J460-01-2FCV-702_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2142 | J270-06-1PNL-001 | J460-01-2FCV-702 | Measurement | J460-01-2FCV-702 - Room J6.14 - Reheater Valve Control Status | J460-01-2FCV-702_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2143 | J270-06-1PNL-001 | J460-01-2FCV-702 | Measurement | J460-01-2FCV-702 - Room J6.14 - Reheater Valve Control Actual SP | J460-01-2FCV-702_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2144 | J270-06-1PNL-001 | J460-01-2FCV-702 | Setting | J460-01-2FCV-702 - Room J6.14 - Reheater Valve Control SP | J460-01-2FCV-702_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2145 | J270-06-1PNL-001 | J460-01-2FCV-702 | Alarm | J460-01-2FCV-702 - Room J6.14 - Reheater Valve Control Fail to Open Alarm | J460-01-2FCV-702_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2146 | J270-06-1PNL-001 | J460-01-2FCV-702 | Alarm | J460-01-2FCV-702 - Room J6.14 - Reheater Valve Control Fail to Close Alarm | J460-01-2FCV-702_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2147 | J270-06-1PNL-001 | J460-01-2FCV-702 | Measurement | J460-01-2FCV-702 - Room J6.14 - Reheater Valve Control Error Code | J460-01-2FCV-702_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2594 | J270-06-1PNL-001 | J460-01-2FCV-702 | Measurement | J460-01-2FCV-702 - Room J6.14 - Reheater Valve Control Speed | J460-01-2FCV-702_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 535 | J270-06-1PNL-001 | J460-01-2TC-703 | Alarm | J460-01-2TC-703 - Room J6.02 - Room Controller - Communication Failure Alarm | J460-01-2TC-703_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2184 | J270-06-1PNL-001 | J460-01-2FCV-703 | Alarm | J460-01-2FCV-703 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-703_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2185 | J270-06-1PNL-001 | J460-01-2FCV-703 | Measurement | J460-01-2FCV-703 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Position | J460-01-2FCV-703_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2186 | J270-06-1PNL-001 | J460-01-2FCV-703 | Setting | J460-01-2FCV-703 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Calibration | J460-01-2FCV-703_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2187 | J270-06-1PNL-001 | J460-01-2FCV-703 | Measurement | J460-01-2FCV-703 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Status | J460-01-2FCV-703_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2188 | J270-06-1PNL-001 | J460-01-2FCV-703 | Measurement | J460-01-2FCV-703 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Actual SP | J460-01-2FCV-703_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2189 | J270-06-1PNL-001 | J460-01-2FCV-703 | Setting | J460-01-2FCV-703 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control SP | J460-01-2FCV-703_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2190 | J270-06-1PNL-001 | J460-01-2FCV-703 | Alarm | J460-01-2FCV-703 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-703_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2191 | J270-06-1PNL-001 | J460-01-2FCV-703 | Alarm | J460-01-2FCV-703 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-703_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2192 | J270-06-1PNL-001 | J460-01-2FCV-703 | Measurement | J460-01-2FCV-703 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Error Code | J460-01-2FCV-703_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2595 | J270-06-1PNL-001 | J460-01-2FCV-703 | Measurement | J460-01-2FCV-703 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Speed | J460-01-2FCV-703_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2184 | J270-06-1PNL-001 | J460-01-2FCV-704 | Alarm | J460-01-2FCV-704 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-704_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2185 | J270-06-1PNL-001 | J460-01-2FCV-704 | Measurement | J460-01-2FCV-704 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Position | J460-01-2FCV-704_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2186 | J270-06-1PNL-001 | J460-01-2FCV-704 | Setting | J460-01-2FCV-704 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Calibration | J460-01-2FCV-704_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2187 | J270-06-1PNL-001 | J460-01-2FCV-704 | Measurement | J460-01-2FCV-704 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Status | J460-01-2FCV-704_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2188 | J270-06-1PNL-001 | J460-01-2FCV-704 | Measurement | J460-01-2FCV-704 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Actual SP | J460-01-2FCV-704_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2189 | J270-06-1PNL-001 | J460-01-2FCV-704 | Setting | J460-01-2FCV-704 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control SP | J460-01-2FCV-704_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2190 | J270-06-1PNL-001 | J460-01-2FCV-704 | Alarm | J460-01-2FCV-704 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-704_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2191 | J270-06-1PNL-001 | J460-01-2FCV-704 | Alarm | J460-01-2FCV-704 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-704_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2192 | J270-06-1PNL-001 | J460-01-2FCV-704 | Measurement | J460-01-2FCV-704 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Error Code | J460-01-2FCV-704_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2595 | J270-06-1PNL-001 | J460-01-2FCV-704 | Measurement | J460-01-2FCV-704 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Speed | J460-01-2FCV-704_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2184 | J270-06-1PNL-001 | J460-01-2FCV-705 | Alarm | J460-01-2FCV-705 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-705_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2185 | J270-06-1PNL-001 | J460-01-2FCV-705 | Measurement | J460-01-2FCV-705 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Position | J460-01-2FCV-705_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2186 | J270-06-1PNL-001 | J460-01-2FCV-705 | Setting | J460-01-2FCV-705 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Calibration | J460-01-2FCV-705_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2187 | J270-06-1PNL-001 | J460-01-2FCV-705 | Measurement | J460-01-2FCV-705 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Status | J460-01-2FCV-705_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2188 | J270-06-1PNL-001 | J460-01-2FCV-705 | Measurement | J460-01-2FCV-705 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Actual SP | J460-01-2FCV-705_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2189 | J270-06-1PNL-001 | J460-01-2FCV-705 | Setting | J460-01-2FCV-705 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control SP | J460-01-2FCV-705_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2190 | J270-06-1PNL-001 | J460-01-2FCV-705 | Alarm | J460-01-2FCV-705 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-705_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2191 | J270-06-1PNL-001 | J460-01-2FCV-705 | Alarm | J460-01-2FCV-705 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-705_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2192 | J270-06-1PNL-001 | J460-01-2FCV-705 | Measurement | J460-01-2FCV-705 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Error Code | J460-01-2FCV-705_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2595 | J270-06-1PNL-001 | J460-01-2FCV-705 | Measurement | J460-01-2FCV-705 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Speed | J460-01-2FCV-705_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2184 | J270-06-1PNL-001 | J460-01-2FCV-706 | Alarm | J460-01-2FCV-706 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-706_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2185 | J270-06-1PNL-001 | J460-01-2FCV-706 | Measurement | J460-01-2FCV-706 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Position | J460-01-2FCV-706_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2186 | J270-06-1PNL-001 | J460-01-2FCV-706 | Setting | J460-01-2FCV-706 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Calibration | J460-01-2FCV-706_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2187 | J270-06-1PNL-001 | J460-01-2FCV-706 | Measurement | J460-01-2FCV-706 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Status | J460-01-2FCV-706_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2188 | J270-06-1PNL-001 | J460-01-2FCV-706 | Measurement | J460-01-2FCV-706 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Actual SP | J460-01-2FCV-706_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2189 | J270-06-1PNL-001 | J460-01-2FCV-706 | Setting | J460-01-2FCV-706 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control SP | J460-01-2FCV-706_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2190 | J270-06-1PNL-001 | J460-01-2FCV-706 | Alarm | J460-01-2FCV-706 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-706_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2191 | J270-06-1PNL-001 | J460-01-2FCV-706 | Alarm | J460-01-2FCV-706 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-706_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2192 | J270-06-1PNL-001 | J460-01-2FCV-706 | Measurement | J460-01-2FCV-706 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Error Code | J460-01-2FCV-706_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2595 | J270-06-1PNL-001 | J460-01-2FCV-706 | Measurement | J460-01-2FCV-706 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Speed | J460-01-2FCV-706_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2220 | J270-06-1PNL-001 | J460-01-2FCV-707 | Alarm | J460-01-2FCV-707 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-707_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2221 | J270-06-1PNL-001 | J460-01-2FCV-707 | Measurement | J460-01-2FCV-707 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Position | J460-01-2FCV-707_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2222 | J270-06-1PNL-001 | J460-01-2FCV-707 | Setting | J460-01-2FCV-707 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Calibration | J460-01-2FCV-707_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2223 | J270-06-1PNL-001 | J460-01-2FCV-707 | Measurement | J460-01-2FCV-707 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Status | J460-01-2FCV-707_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2224 | J270-06-1PNL-001 | J460-01-2FCV-707 | Measurement | J460-01-2FCV-707 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Actual SP | J460-01-2FCV-707_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2225 | J270-06-1PNL-001 | J460-01-2FCV-707 | Setting | J460-01-2FCV-707 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control SP | J460-01-2FCV-707_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2226 | J270-06-1PNL-001 | J460-01-2FCV-707 | Alarm | J460-01-2FCV-707 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-707_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2227 | J270-06-1PNL-001 | J460-01-2FCV-707 | Alarm | J460-01-2FCV-707 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-707_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2228 | J270-06-1PNL-001 | J460-01-2FCV-707 | Measurement | J460-01-2FCV-707 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Error Code | J460-01-2FCV-707_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2599 | J270-06-1PNL-001 | J460-01-2FCV-707 | Measurement | J460-01-2FCV-707 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Speed | J460-01-2FCV-707_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2220 | J270-06-1PNL-001 | J460-01-2FCV-708 | Alarm | J460-01-2FCV-708 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-708_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2221 | J270-06-1PNL-001 | J460-01-2FCV-708 | Measurement | J460-01-2FCV-708 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Position | J460-01-2FCV-708_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2222 | J270-06-1PNL-001 | J460-01-2FCV-708 | Setting | J460-01-2FCV-708 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Calibration | J460-01-2FCV-708_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2223 | J270-06-1PNL-001 | J460-01-2FCV-708 | Measurement | J460-01-2FCV-708 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Status | J460-01-2FCV-708_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2224 | J270-06-1PNL-001 | J460-01-2FCV-708 | Measurement | J460-01-2FCV-708 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Actual SP | J460-01-2FCV-708_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2225 | J270-06-1PNL-001 | J460-01-2FCV-708 | Setting | J460-01-2FCV-708 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control SP | J460-01-2FCV-708_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2226 | J270-06-1PNL-001 | J460-01-2FCV-708 | Alarm | J460-01-2FCV-708 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-708_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2227 | J270-06-1PNL-001 | J460-01-2FCV-708 | Alarm | J460-01-2FCV-708 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-708_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2228 | J270-06-1PNL-001 | J460-01-2FCV-708 | Measurement | J460-01-2FCV-708 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Error Code | J460-01-2FCV-708_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2599 | J270-06-1PNL-001 | J460-01-2FCV-708 | Measurement | J460-01-2FCV-708 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Speed | J460-01-2FCV-708_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2220 | J270-06-1PNL-001 | J460-01-2FCV-709 | Alarm | J460-01-2FCV-709 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-709_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2221 | J270-06-1PNL-001 | J460-01-2FCV-709 | Measurement | J460-01-2FCV-709 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Position | J460-01-2FCV-709_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2222 | J270-06-1PNL-001 | J460-01-2FCV-709 | Setting | J460-01-2FCV-709 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Calibration | J460-01-2FCV-709_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2223 | J270-06-1PNL-001 | J460-01-2FCV-709 | Measurement | J460-01-2FCV-709 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Status | J460-01-2FCV-709_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2224 | J270-06-1PNL-001 | J460-01-2FCV-709 | Measurement | J460-01-2FCV-709 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Actual SP | J460-01-2FCV-709_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2225 | J270-06-1PNL-001 | J460-01-2FCV-709 | Setting | J460-01-2FCV-709 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control SP | J460-01-2FCV-709_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2226 | J270-06-1PNL-001 | J460-01-2FCV-709 | Alarm | J460-01-2FCV-709 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-709_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2227 | J270-06-1PNL-001 | J460-01-2FCV-709 | Alarm | J460-01-2FCV-709 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-709_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2228 | J270-06-1PNL-001 | J460-01-2FCV-709 | Measurement | J460-01-2FCV-709 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Error Code | J460-01-2FCV-709_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2599 | J270-06-1PNL-001 | J460-01-2FCV-709 | Measurement | J460-01-2FCV-709 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Speed | J460-01-2FCV-709_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2220 | J270-06-1PNL-001 | J460-01-2FCV-710 | Alarm | J460-01-2FCV-710 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-710_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2221 | J270-06-1PNL-001 | J460-01-2FCV-710 | Measurement | J460-01-2FCV-710 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Position | J460-01-2FCV-710_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2222 | J270-06-1PNL-001 | J460-01-2FCV-710 | Setting | J460-01-2FCV-710 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Calibration | J460-01-2FCV-710_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2223 | J270-06-1PNL-001 | J460-01-2FCV-710 | Measurement | J460-01-2FCV-710 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Status | J460-01-2FCV-710_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2224 | J270-06-1PNL-001 | J460-01-2FCV-710 | Measurement | J460-01-2FCV-710 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Actual SP | J460-01-2FCV-710_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2225 | J270-06-1PNL-001 | J460-01-2FCV-710 | Setting | J460-01-2FCV-710 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control SP | J460-01-2FCV-710_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2226 | J270-06-1PNL-001 | J460-01-2FCV-710 | Alarm | J460-01-2FCV-710 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-710_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2227 | J270-06-1PNL-001 | J460-01-2FCV-710 | Alarm | J460-01-2FCV-710 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-710_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2228 | J270-06-1PNL-001 | J460-01-2FCV-710 | Measurement | J460-01-2FCV-710 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Error Code | J460-01-2FCV-710_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2599 | J270-06-1PNL-001 | J460-01-2FCV-710 | Measurement | J460-01-2FCV-710 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Speed | J460-01-2FCV-710_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2256 | J270-06-1PNL-001 | J460-01-1VAV-701 | Alarm | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control - Communication Failure Alarm | J460-01-1VAV-701_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 2257 | J270-06-1PNL-001 | J460-01-1VAV-701 | Setting | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Flow Setpoint | J460-01-1VAV-701_SpRel |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2258 | J270-06-1PNL-001 | J460-01-1VAV-701 | Measurement | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Relative Position | J460-01-1VAV-701_RelPos |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2259 | J270-06-1PNL-001 | J460-01-1VAV-701 | Measurement | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-701_AbsFlw |  | 0 | 650 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2260 | J270-06-1PNL-001 | J460-01-1VAV-701 | Alarm | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-701_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 2261 | J270-06-1PNL-001 | J460-01-1VAV-701 | Setting | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-701_AbsFlw_HASP |  | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2262 | J270-06-1PNL-001 | J460-01-1VAV-701 | Alarm | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-701_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 2263 | J270-06-1PNL-001 | J460-01-1VAV-701 | Setting | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-701_AbsFlw_LASP |  | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2264 | J270-06-1PNL-001 | J460-01-1VAV-701 | Measurement | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-701_Vmin |  | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2265 | J270-06-1PNL-001 | J460-01-1VAV-701 | Measurement | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Maximum Flow | J460-01-1VAV-701_Vmax |  | 650 | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2266 | J270-06-1PNL-001 | J460-01-1VAV-701 | Measurement | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-701_Vnom |  | 0 | 650 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2267 | J270-06-1PNL-001 | J460-01-1VAV-701 | Measurement | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Summary Status | J460-01-1VAV-701_SumSts |  | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2268 | J270-06-1PNL-001 | J460-01-1VAV-701 | Alarm | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Summary Status Alarm | J460-01-1VAV-701_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 2269 | J270-06-1PNL-001 | J460-01-1VAV-701 | Measurement | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Actuator Status | J460-01-1VAV-701_ActSts |  | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2270 | J270-06-1PNL-001 | J460-01-1VAV-701 | Measurement | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Device Status | J460-01-1VAV-701_DevSts |  | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2271 | J270-06-1PNL-001 | J460-01-1VAV-701 | Setting | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Device Override | J460-01-1VAV-701_Override |  | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
A.03 | 2483 | J270-06-1PNL-001 | J460-01-1VAV-701 | Alarm | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-701_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2484 | J270-06-1PNL-001 | J460-01-1VAV-701 | Setting | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-701_Vmin_HASP |  | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2485 | J270-06-1PNL-001 | J460-01-1VAV-701 | Alarm | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-701_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2486 | J270-06-1PNL-001 | J460-01-1VAV-701 | Setting | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-701_Vmin_LASP |  | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2487 | J270-06-1PNL-001 | J460-01-1VAV-701 | Alarm | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-701_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2488 | J270-06-1PNL-001 | J460-01-1VAV-701 | Setting | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-701_Vnom_HASP |  | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2489 | J270-06-1PNL-001 | J460-01-1VAV-701 | Alarm | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-701_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2490 | J270-06-1PNL-001 | J460-01-1VAV-701 | Setting | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-701_Vnom_LASP |  | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2526 | J270-06-1PNL-001 | J460-01-1VAV-701 | Setting | J460-01-1VAV-701 - Room J0.07 - Return Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-701_MinOpnFlwSP |  | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2256 | J270-06-1PNL-001 | J460-01-1VAV-702 | Alarm | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control - Communication Failure Alarm | J460-01-1VAV-702_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 2257 | J270-06-1PNL-001 | J460-01-1VAV-702 | Setting | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Flow Setpoint | J460-01-1VAV-702_SpRel |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2258 | J270-06-1PNL-001 | J460-01-1VAV-702 | Measurement | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Relative Position | J460-01-1VAV-702_RelPos |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2259 | J270-06-1PNL-001 | J460-01-1VAV-702 | Measurement | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-702_AbsFlw |  | 0 | 650 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2260 | J270-06-1PNL-001 | J460-01-1VAV-702 | Alarm | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-702_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 2261 | J270-06-1PNL-001 | J460-01-1VAV-702 | Setting | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-702_AbsFlw_HASP |  | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2262 | J270-06-1PNL-001 | J460-01-1VAV-702 | Alarm | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-702_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 2263 | J270-06-1PNL-001 | J460-01-1VAV-702 | Setting | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-702_AbsFlw_LASP |  | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2264 | J270-06-1PNL-001 | J460-01-1VAV-702 | Measurement | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-702_Vmin |  | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2265 | J270-06-1PNL-001 | J460-01-1VAV-702 | Measurement | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Maximum Flow | J460-01-1VAV-702_Vmax |  | 650 | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2266 | J270-06-1PNL-001 | J460-01-1VAV-702 | Measurement | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-702_Vnom |  | 0 | 650 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2267 | J270-06-1PNL-001 | J460-01-1VAV-702 | Measurement | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Summary Status | J460-01-1VAV-702_SumSts |  | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2268 | J270-06-1PNL-001 | J460-01-1VAV-702 | Alarm | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Summary Status Alarm | J460-01-1VAV-702_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 2269 | J270-06-1PNL-001 | J460-01-1VAV-702 | Measurement | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Actuator Status | J460-01-1VAV-702_ActSts |  | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2270 | J270-06-1PNL-001 | J460-01-1VAV-702 | Measurement | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Device Status | J460-01-1VAV-702_DevSts |  | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2271 | J270-06-1PNL-001 | J460-01-1VAV-702 | Setting | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Device Override | J460-01-1VAV-702_Override |  | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
A.03 | 2483 | J270-06-1PNL-001 | J460-01-1VAV-702 | Alarm | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-702_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2484 | J270-06-1PNL-001 | J460-01-1VAV-702 | Setting | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-702_Vmin_HASP |  | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2485 | J270-06-1PNL-001 | J460-01-1VAV-702 | Alarm | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-702_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2486 | J270-06-1PNL-001 | J460-01-1VAV-702 | Setting | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-702_Vmin_LASP |  | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2487 | J270-06-1PNL-001 | J460-01-1VAV-702 | Alarm | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-702_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2488 | J270-06-1PNL-001 | J460-01-1VAV-702 | Setting | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-702_Vnom_HASP |  | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2489 | J270-06-1PNL-001 | J460-01-1VAV-702 | Alarm | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-702_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2490 | J270-06-1PNL-001 | J460-01-1VAV-702 | Setting | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-702_Vnom_LASP |  | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2526 | J270-06-1PNL-001 | J460-01-1VAV-702 | Setting | J460-01-1VAV-702 - Room J0.07 - Return Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-702_MinOpnFlwSP |  | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1632 | J270-06-1PNL-001 | J460-01-1VAV-703 | Alarm | J460-01-1VAV-703 - Room J6.23 - Supply Air Flow Control - Communication Failure Alarm | J460-01-1VAV-703_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1633 | J270-06-1PNL-001 | J460-01-1VAV-703 | Setting | J460-01-1VAV-703 - Room J6.23 - Supply Air Flow Control Operating Mode Entire Room | J460-01-1VAV-703_Mode |  | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1634 | J270-06-1PNL-001 | J460-01-1VAV-703 | Setting | J460-01-1VAV-703 - Room J6.23 - Supply Air Flow Control Volume Flow SP Shift | J460-01-1VAV-703_FlwSPShift |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1635 | J270-06-1PNL-001 | J460-01-1VAV-703 | Measurement | J460-01-1VAV-703 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-01-1VAV-703_LocAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1636 | J270-06-1PNL-001 | J460-01-1VAV-703 | Alarm | J460-01-1VAV-703 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-01-1VAV-703_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1637 | J270-06-1PNL-001 | J460-01-1VAV-703 | Measurement | J460-01-1VAV-703 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-01-1VAV-703_SumAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1638 | J270-06-1PNL-001 | J460-01-1VAV-703 | Alarm | J460-01-1VAV-703 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-01-1VAV-703_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 1639 | J270-06-1PNL-001 | J460-01-1VAV-703 | Measurement | J460-02-1VAV-608 - Room J6.23 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-608_RmEaFlwTot |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1640 | J270-06-1PNL-001 | J460-01-1VAV-703 | Measurement | J460-01-1VAV-703 - Room J6.23 - Supply Air Flow Control Supply Air Volume | J460-01-1VAV-703_RmSaFlw |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2256 | J270-06-1PNL-001 | J460-01-1VAV-704 | Alarm | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control - Communication Failure Alarm | J460-01-1VAV-704_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 2257 | J270-06-1PNL-001 | J460-01-1VAV-704 | Setting | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Flow Setpoint | J460-01-1VAV-704_SpRel |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2258 | J270-06-1PNL-001 | J460-01-1VAV-704 | Measurement | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Relative Position | J460-01-1VAV-704_RelPos |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2259 | J270-06-1PNL-001 | J460-01-1VAV-704 | Measurement | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-704_AbsFlw |  | 0 | 650 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2260 | J270-06-1PNL-001 | J460-01-1VAV-704 | Alarm | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-704_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 2261 | J270-06-1PNL-001 | J460-01-1VAV-704 | Setting | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-704_AbsFlw_HASP |  | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2262 | J270-06-1PNL-001 | J460-01-1VAV-704 | Alarm | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-704_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 2263 | J270-06-1PNL-001 | J460-01-1VAV-704 | Setting | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-704_AbsFlw_LASP |  | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2264 | J270-06-1PNL-001 | J460-01-1VAV-704 | Measurement | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-704_Vmin |  | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2265 | J270-06-1PNL-001 | J460-01-1VAV-704 | Measurement | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Maximum Flow | J460-01-1VAV-704_Vmax |  | 650 | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2266 | J270-06-1PNL-001 | J460-01-1VAV-704 | Measurement | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-704_Vnom |  | 0 | 650 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2267 | J270-06-1PNL-001 | J460-01-1VAV-704 | Measurement | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Summary Status | J460-01-1VAV-704_SumSts |  | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2268 | J270-06-1PNL-001 | J460-01-1VAV-704 | Alarm | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Summary Status Alarm | J460-01-1VAV-704_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 2269 | J270-06-1PNL-001 | J460-01-1VAV-704 | Measurement | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Actuator Status | J460-01-1VAV-704_ActSts |  | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2270 | J270-06-1PNL-001 | J460-01-1VAV-704 | Measurement | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Device Status | J460-01-1VAV-704_DevSts |  | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2271 | J270-06-1PNL-001 | J460-01-1VAV-704 | Setting | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Device Override | J460-01-1VAV-704_Override |  | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
A.03 | 2483 | J270-06-1PNL-001 | J460-01-1VAV-704 | Alarm | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-704_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2484 | J270-06-1PNL-001 | J460-01-1VAV-704 | Setting | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-704_Vmin_HASP |  | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2485 | J270-06-1PNL-001 | J460-01-1VAV-704 | Alarm | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-704_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2486 | J270-06-1PNL-001 | J460-01-1VAV-704 | Setting | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-704_Vmin_LASP |  | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2487 | J270-06-1PNL-001 | J460-01-1VAV-704 | Alarm | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-704_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2488 | J270-06-1PNL-001 | J460-01-1VAV-704 | Setting | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-704_Vnom_HASP |  | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2489 | J270-06-1PNL-001 | J460-01-1VAV-704 | Alarm | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-704_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2490 | J270-06-1PNL-001 | J460-01-1VAV-704 | Setting | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-704_Vnom_LASP |  | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2526 | J270-06-1PNL-001 | J460-01-1VAV-704 | Setting | J460-01-1VAV-704 - Room J0.07 - Return Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-704_MinOpnFlwSP |  | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 535 | J270-06-1PNL-001 | J460-01-2TC-704 | Alarm | J460-01-2TC-704 - Room J6.02 - Room Controller - Communication Failure Alarm | J460-01-2TC-704_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 535 | J270-06-1PNL-001 | J460-01-2TC-705 | Alarm | J460-01-2TC-705 - Room J6.02 - Room Controller - Communication Failure Alarm | J460-01-2TC-705_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2139 | J270-06-1PNL-001 | J460-01-2FCV-711 | Alarm | J460-01-2FCV-711 - Room J6.14 - Reheater Valve Control - Communication Failure Alarm | J460-01-2FCV-711_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2140 | J270-06-1PNL-001 | J460-01-2FCV-711 | Measurement | J460-01-2FCV-711 - Room J6.14 - Reheater Valve Control Forced Position | J460-01-2FCV-711_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2141 | J270-06-1PNL-001 | J460-01-2FCV-711 | Setting | J460-01-2FCV-711 - Room J6.14 - Reheater Valve Control Forced Calibration | J460-01-2FCV-711_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2142 | J270-06-1PNL-001 | J460-01-2FCV-711 | Measurement | J460-01-2FCV-711 - Room J6.14 - Reheater Valve Control Status | J460-01-2FCV-711_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2143 | J270-06-1PNL-001 | J460-01-2FCV-711 | Measurement | J460-01-2FCV-711 - Room J6.14 - Reheater Valve Control Actual SP | J460-01-2FCV-711_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2144 | J270-06-1PNL-001 | J460-01-2FCV-711 | Setting | J460-01-2FCV-711 - Room J6.14 - Reheater Valve Control SP | J460-01-2FCV-711_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2145 | J270-06-1PNL-001 | J460-01-2FCV-711 | Alarm | J460-01-2FCV-711 - Room J6.14 - Reheater Valve Control Fail to Open Alarm | J460-01-2FCV-711_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2146 | J270-06-1PNL-001 | J460-01-2FCV-711 | Alarm | J460-01-2FCV-711 - Room J6.14 - Reheater Valve Control Fail to Close Alarm | J460-01-2FCV-711_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2147 | J270-06-1PNL-001 | J460-01-2FCV-711 | Measurement | J460-01-2FCV-711 - Room J6.14 - Reheater Valve Control Error Code | J460-01-2FCV-711_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2594 | J270-06-1PNL-001 | J460-01-2FCV-711 | Measurement | J460-01-2FCV-711 - Room J6.14 - Reheater Valve Control Speed | J460-01-2FCV-711_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1632 | J270-06-1PNL-001 | J460-01-1VAV-705 | Alarm | J460-01-1VAV-705 - Room J6.23 - Supply Air Flow Control - Communication Failure Alarm | J460-01-1VAV-705_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1633 | J270-06-1PNL-001 | J460-01-1VAV-705 | Setting | J460-01-1VAV-705 - Room J6.23 - Supply Air Flow Control Operating Mode Entire Room | J460-01-1VAV-705_Mode |  | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1634 | J270-06-1PNL-001 | J460-01-1VAV-705 | Setting | J460-01-1VAV-705 - Room J6.23 - Supply Air Flow Control Volume Flow SP Shift | J460-01-1VAV-705_FlwSPShift |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1635 | J270-06-1PNL-001 | J460-01-1VAV-705 | Measurement | J460-01-1VAV-705 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-01-1VAV-705_LocAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1636 | J270-06-1PNL-001 | J460-01-1VAV-705 | Alarm | J460-01-1VAV-705 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-01-1VAV-705_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1637 | J270-06-1PNL-001 | J460-01-1VAV-705 | Measurement | J460-01-1VAV-705 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-01-1VAV-705_SumAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1638 | J270-06-1PNL-001 | J460-01-1VAV-705 | Alarm | J460-01-1VAV-705 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-01-1VAV-705_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 1639 | J270-06-1PNL-001 | J460-01-1VAV-705 | Measurement | J460-02-1VAV-608 - Room J6.23 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-608_RmEaFlwTot |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1640 | J270-06-1PNL-001 | J460-01-1VAV-705 | Measurement | J460-01-1VAV-705 - Room J6.23 - Supply Air Flow Control Supply Air Volume | J460-01-1VAV-705_RmSaFlw |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2256 | J270-06-1PNL-001 | J460-01-1VAV-706 | Alarm | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control - Communication Failure Alarm | J460-01-1VAV-706_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 2257 | J270-06-1PNL-001 | J460-01-1VAV-706 | Setting | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Flow Setpoint | J460-01-1VAV-706_SpRel |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2258 | J270-06-1PNL-001 | J460-01-1VAV-706 | Measurement | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Relative Position | J460-01-1VAV-706_RelPos |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2259 | J270-06-1PNL-001 | J460-01-1VAV-706 | Measurement | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-706_AbsFlw |  | 0 | 650 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2260 | J270-06-1PNL-001 | J460-01-1VAV-706 | Alarm | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-706_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 2261 | J270-06-1PNL-001 | J460-01-1VAV-706 | Setting | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-706_AbsFlw_HASP |  | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2262 | J270-06-1PNL-001 | J460-01-1VAV-706 | Alarm | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-706_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 2263 | J270-06-1PNL-001 | J460-01-1VAV-706 | Setting | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-706_AbsFlw_LASP |  | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2264 | J270-06-1PNL-001 | J460-01-1VAV-706 | Measurement | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-706_Vmin |  | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2265 | J270-06-1PNL-001 | J460-01-1VAV-706 | Measurement | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Maximum Flow | J460-01-1VAV-706_Vmax |  | 650 | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2266 | J270-06-1PNL-001 | J460-01-1VAV-706 | Measurement | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-706_Vnom |  | 0 | 650 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2267 | J270-06-1PNL-001 | J460-01-1VAV-706 | Measurement | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Summary Status | J460-01-1VAV-706_SumSts |  | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2268 | J270-06-1PNL-001 | J460-01-1VAV-706 | Alarm | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Summary Status Alarm | J460-01-1VAV-706_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 2269 | J270-06-1PNL-001 | J460-01-1VAV-706 | Measurement | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Actuator Status | J460-01-1VAV-706_ActSts |  | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2270 | J270-06-1PNL-001 | J460-01-1VAV-706 | Measurement | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Device Status | J460-01-1VAV-706_DevSts |  | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2271 | J270-06-1PNL-001 | J460-01-1VAV-706 | Setting | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Device Override | J460-01-1VAV-706_Override |  | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
A.03 | 2483 | J270-06-1PNL-001 | J460-01-1VAV-706 | Alarm | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-706_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2484 | J270-06-1PNL-001 | J460-01-1VAV-706 | Setting | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-706_Vmin_HASP |  | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2485 | J270-06-1PNL-001 | J460-01-1VAV-706 | Alarm | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-706_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2486 | J270-06-1PNL-001 | J460-01-1VAV-706 | Setting | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-706_Vmin_LASP |  | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2487 | J270-06-1PNL-001 | J460-01-1VAV-706 | Alarm | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-706_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2488 | J270-06-1PNL-001 | J460-01-1VAV-706 | Setting | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-706_Vnom_HASP |  | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2489 | J270-06-1PNL-001 | J460-01-1VAV-706 | Alarm | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-706_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2490 | J270-06-1PNL-001 | J460-01-1VAV-706 | Setting | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-706_Vnom_LASP |  | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2526 | J270-06-1PNL-001 | J460-01-1VAV-706 | Setting | J460-01-1VAV-706 - Room J0.07 - Return Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-706_MinOpnFlwSP |  | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2184 | J270-06-1PNL-001 | J460-01-2FCV-712 | Alarm | J460-01-2FCV-712 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-712_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2185 | J270-06-1PNL-001 | J460-01-2FCV-712 | Measurement | J460-01-2FCV-712 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Position | J460-01-2FCV-712_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2186 | J270-06-1PNL-001 | J460-01-2FCV-712 | Setting | J460-01-2FCV-712 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Calibration | J460-01-2FCV-712_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2187 | J270-06-1PNL-001 | J460-01-2FCV-712 | Measurement | J460-01-2FCV-712 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Status | J460-01-2FCV-712_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2188 | J270-06-1PNL-001 | J460-01-2FCV-712 | Measurement | J460-01-2FCV-712 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Actual SP | J460-01-2FCV-712_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2189 | J270-06-1PNL-001 | J460-01-2FCV-712 | Setting | J460-01-2FCV-712 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control SP | J460-01-2FCV-712_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2190 | J270-06-1PNL-001 | J460-01-2FCV-712 | Alarm | J460-01-2FCV-712 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-712_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2191 | J270-06-1PNL-001 | J460-01-2FCV-712 | Alarm | J460-01-2FCV-712 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-712_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2192 | J270-06-1PNL-001 | J460-01-2FCV-712 | Measurement | J460-01-2FCV-712 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Error Code | J460-01-2FCV-712_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2595 | J270-06-1PNL-001 | J460-01-2FCV-712 | Measurement | J460-01-2FCV-712 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Speed | J460-01-2FCV-712_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2184 | J270-06-1PNL-001 | J460-01-2FCV-713 | Alarm | J460-01-2FCV-713 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-713_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2185 | J270-06-1PNL-001 | J460-01-2FCV-713 | Measurement | J460-01-2FCV-713 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Position | J460-01-2FCV-713_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2186 | J270-06-1PNL-001 | J460-01-2FCV-713 | Setting | J460-01-2FCV-713 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Calibration | J460-01-2FCV-713_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2187 | J270-06-1PNL-001 | J460-01-2FCV-713 | Measurement | J460-01-2FCV-713 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Status | J460-01-2FCV-713_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2188 | J270-06-1PNL-001 | J460-01-2FCV-713 | Measurement | J460-01-2FCV-713 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Actual SP | J460-01-2FCV-713_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2189 | J270-06-1PNL-001 | J460-01-2FCV-713 | Setting | J460-01-2FCV-713 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control SP | J460-01-2FCV-713_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2190 | J270-06-1PNL-001 | J460-01-2FCV-713 | Alarm | J460-01-2FCV-713 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-713_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2191 | J270-06-1PNL-001 | J460-01-2FCV-713 | Alarm | J460-01-2FCV-713 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-713_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2192 | J270-06-1PNL-001 | J460-01-2FCV-713 | Measurement | J460-01-2FCV-713 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Error Code | J460-01-2FCV-713_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2595 | J270-06-1PNL-001 | J460-01-2FCV-713 | Measurement | J460-01-2FCV-713 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Speed | J460-01-2FCV-713_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2184 | J270-06-1PNL-001 | J460-01-2FCV-714 | Alarm | J460-01-2FCV-714 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-714_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2185 | J270-06-1PNL-001 | J460-01-2FCV-714 | Measurement | J460-01-2FCV-714 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Position | J460-01-2FCV-714_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2186 | J270-06-1PNL-001 | J460-01-2FCV-714 | Setting | J460-01-2FCV-714 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Calibration | J460-01-2FCV-714_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2187 | J270-06-1PNL-001 | J460-01-2FCV-714 | Measurement | J460-01-2FCV-714 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Status | J460-01-2FCV-714_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2188 | J270-06-1PNL-001 | J460-01-2FCV-714 | Measurement | J460-01-2FCV-714 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Actual SP | J460-01-2FCV-714_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2189 | J270-06-1PNL-001 | J460-01-2FCV-714 | Setting | J460-01-2FCV-714 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control SP | J460-01-2FCV-714_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2190 | J270-06-1PNL-001 | J460-01-2FCV-714 | Alarm | J460-01-2FCV-714 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-714_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2191 | J270-06-1PNL-001 | J460-01-2FCV-714 | Alarm | J460-01-2FCV-714 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-714_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2192 | J270-06-1PNL-001 | J460-01-2FCV-714 | Measurement | J460-01-2FCV-714 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Error Code | J460-01-2FCV-714_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2595 | J270-06-1PNL-001 | J460-01-2FCV-714 | Measurement | J460-01-2FCV-714 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Speed | J460-01-2FCV-714_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2184 | J270-06-1PNL-001 | J460-01-2FCV-715 | Alarm | J460-01-2FCV-715 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-715_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2185 | J270-06-1PNL-001 | J460-01-2FCV-715 | Measurement | J460-01-2FCV-715 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Position | J460-01-2FCV-715_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2186 | J270-06-1PNL-001 | J460-01-2FCV-715 | Setting | J460-01-2FCV-715 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Calibration | J460-01-2FCV-715_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2187 | J270-06-1PNL-001 | J460-01-2FCV-715 | Measurement | J460-01-2FCV-715 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Status | J460-01-2FCV-715_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2188 | J270-06-1PNL-001 | J460-01-2FCV-715 | Measurement | J460-01-2FCV-715 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Actual SP | J460-01-2FCV-715_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2189 | J270-06-1PNL-001 | J460-01-2FCV-715 | Setting | J460-01-2FCV-715 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control SP | J460-01-2FCV-715_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2190 | J270-06-1PNL-001 | J460-01-2FCV-715 | Alarm | J460-01-2FCV-715 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-715_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2191 | J270-06-1PNL-001 | J460-01-2FCV-715 | Alarm | J460-01-2FCV-715 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-715_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2192 | J270-06-1PNL-001 | J460-01-2FCV-715 | Measurement | J460-01-2FCV-715 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Error Code | J460-01-2FCV-715_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2595 | J270-06-1PNL-001 | J460-01-2FCV-715 | Measurement | J460-01-2FCV-715 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Speed | J460-01-2FCV-715_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2220 | J270-06-1PNL-001 | J460-01-2FCV-716 | Alarm | J460-01-2FCV-716 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-716_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2221 | J270-06-1PNL-001 | J460-01-2FCV-716 | Measurement | J460-01-2FCV-716 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Position | J460-01-2FCV-716_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2222 | J270-06-1PNL-001 | J460-01-2FCV-716 | Setting | J460-01-2FCV-716 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Calibration | J460-01-2FCV-716_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2223 | J270-06-1PNL-001 | J460-01-2FCV-716 | Measurement | J460-01-2FCV-716 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Status | J460-01-2FCV-716_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2224 | J270-06-1PNL-001 | J460-01-2FCV-716 | Measurement | J460-01-2FCV-716 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Actual SP | J460-01-2FCV-716_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2225 | J270-06-1PNL-001 | J460-01-2FCV-716 | Setting | J460-01-2FCV-716 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control SP | J460-01-2FCV-716_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2226 | J270-06-1PNL-001 | J460-01-2FCV-716 | Alarm | J460-01-2FCV-716 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-716_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2227 | J270-06-1PNL-001 | J460-01-2FCV-716 | Alarm | J460-01-2FCV-716 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-716_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2228 | J270-06-1PNL-001 | J460-01-2FCV-716 | Measurement | J460-01-2FCV-716 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Error Code | J460-01-2FCV-716_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2599 | J270-06-1PNL-001 | J460-01-2FCV-716 | Measurement | J460-01-2FCV-716 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Speed | J460-01-2FCV-716_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2220 | J270-06-1PNL-001 | J460-01-2FCV-717 | Alarm | J460-01-2FCV-717 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-717_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2221 | J270-06-1PNL-001 | J460-01-2FCV-717 | Measurement | J460-01-2FCV-717 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Position | J460-01-2FCV-717_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2222 | J270-06-1PNL-001 | J460-01-2FCV-717 | Setting | J460-01-2FCV-717 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Calibration | J460-01-2FCV-717_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2223 | J270-06-1PNL-001 | J460-01-2FCV-717 | Measurement | J460-01-2FCV-717 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Status | J460-01-2FCV-717_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2224 | J270-06-1PNL-001 | J460-01-2FCV-717 | Measurement | J460-01-2FCV-717 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Actual SP | J460-01-2FCV-717_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2225 | J270-06-1PNL-001 | J460-01-2FCV-717 | Setting | J460-01-2FCV-717 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control SP | J460-01-2FCV-717_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2226 | J270-06-1PNL-001 | J460-01-2FCV-717 | Alarm | J460-01-2FCV-717 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-717_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2227 | J270-06-1PNL-001 | J460-01-2FCV-717 | Alarm | J460-01-2FCV-717 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-717_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2228 | J270-06-1PNL-001 | J460-01-2FCV-717 | Measurement | J460-01-2FCV-717 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Error Code | J460-01-2FCV-717_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2599 | J270-06-1PNL-001 | J460-01-2FCV-717 | Measurement | J460-01-2FCV-717 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Speed | J460-01-2FCV-717_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2220 | J270-06-1PNL-001 | J460-01-2FCV-718 | Alarm | J460-01-2FCV-718 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-718_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2221 | J270-06-1PNL-001 | J460-01-2FCV-718 | Measurement | J460-01-2FCV-718 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Position | J460-01-2FCV-718_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2222 | J270-06-1PNL-001 | J460-01-2FCV-718 | Setting | J460-01-2FCV-718 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Calibration | J460-01-2FCV-718_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2223 | J270-06-1PNL-001 | J460-01-2FCV-718 | Measurement | J460-01-2FCV-718 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Status | J460-01-2FCV-718_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2224 | J270-06-1PNL-001 | J460-01-2FCV-718 | Measurement | J460-01-2FCV-718 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Actual SP | J460-01-2FCV-718_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2225 | J270-06-1PNL-001 | J460-01-2FCV-718 | Setting | J460-01-2FCV-718 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control SP | J460-01-2FCV-718_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2226 | J270-06-1PNL-001 | J460-01-2FCV-718 | Alarm | J460-01-2FCV-718 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-718_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2227 | J270-06-1PNL-001 | J460-01-2FCV-718 | Alarm | J460-01-2FCV-718 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-718_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2228 | J270-06-1PNL-001 | J460-01-2FCV-718 | Measurement | J460-01-2FCV-718 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Error Code | J460-01-2FCV-718_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2599 | J270-06-1PNL-001 | J460-01-2FCV-718 | Measurement | J460-01-2FCV-718 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Speed | J460-01-2FCV-718_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2220 | J270-06-1PNL-001 | J460-01-2FCV-719 | Alarm | J460-01-2FCV-719 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-719_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2221 | J270-06-1PNL-001 | J460-01-2FCV-719 | Measurement | J460-01-2FCV-719 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Position | J460-01-2FCV-719_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2222 | J270-06-1PNL-001 | J460-01-2FCV-719 | Setting | J460-01-2FCV-719 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Calibration | J460-01-2FCV-719_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2223 | J270-06-1PNL-001 | J460-01-2FCV-719 | Measurement | J460-01-2FCV-719 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Status | J460-01-2FCV-719_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2224 | J270-06-1PNL-001 | J460-01-2FCV-719 | Measurement | J460-01-2FCV-719 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Actual SP | J460-01-2FCV-719_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2225 | J270-06-1PNL-001 | J460-01-2FCV-719 | Setting | J460-01-2FCV-719 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control SP | J460-01-2FCV-719_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2226 | J270-06-1PNL-001 | J460-01-2FCV-719 | Alarm | J460-01-2FCV-719 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-719_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2227 | J270-06-1PNL-001 | J460-01-2FCV-719 | Alarm | J460-01-2FCV-719 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-719_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2228 | J270-06-1PNL-001 | J460-01-2FCV-719 | Measurement | J460-01-2FCV-719 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Error Code | J460-01-2FCV-719_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2599 | J270-06-1PNL-001 | J460-01-2FCV-719 | Measurement | J460-01-2FCV-719 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Speed | J460-01-2FCV-719_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2256 | J270-06-1PNL-001 | J460-01-1VAV-707 | Alarm | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control - Communication Failure Alarm | J460-01-1VAV-707_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 2257 | J270-06-1PNL-001 | J460-01-1VAV-707 | Setting | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Flow Setpoint | J460-01-1VAV-707_SpRel |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2258 | J270-06-1PNL-001 | J460-01-1VAV-707 | Measurement | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Relative Position | J460-01-1VAV-707_RelPos |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2259 | J270-06-1PNL-001 | J460-01-1VAV-707 | Measurement | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-707_AbsFlw |  | 0 | 650 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2260 | J270-06-1PNL-001 | J460-01-1VAV-707 | Alarm | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-707_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 2261 | J270-06-1PNL-001 | J460-01-1VAV-707 | Setting | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-707_AbsFlw_HASP |  | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2262 | J270-06-1PNL-001 | J460-01-1VAV-707 | Alarm | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-707_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 2263 | J270-06-1PNL-001 | J460-01-1VAV-707 | Setting | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-707_AbsFlw_LASP |  | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2264 | J270-06-1PNL-001 | J460-01-1VAV-707 | Measurement | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-707_Vmin |  | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2265 | J270-06-1PNL-001 | J460-01-1VAV-707 | Measurement | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Maximum Flow | J460-01-1VAV-707_Vmax |  | 650 | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2266 | J270-06-1PNL-001 | J460-01-1VAV-707 | Measurement | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-707_Vnom |  | 0 | 650 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2267 | J270-06-1PNL-001 | J460-01-1VAV-707 | Measurement | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Summary Status | J460-01-1VAV-707_SumSts |  | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2268 | J270-06-1PNL-001 | J460-01-1VAV-707 | Alarm | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Summary Status Alarm | J460-01-1VAV-707_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 2269 | J270-06-1PNL-001 | J460-01-1VAV-707 | Measurement | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Actuator Status | J460-01-1VAV-707_ActSts |  | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2270 | J270-06-1PNL-001 | J460-01-1VAV-707 | Measurement | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Device Status | J460-01-1VAV-707_DevSts |  | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2271 | J270-06-1PNL-001 | J460-01-1VAV-707 | Setting | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Device Override | J460-01-1VAV-707_Override |  | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
A.03 | 2483 | J270-06-1PNL-001 | J460-01-1VAV-707 | Alarm | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-707_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2484 | J270-06-1PNL-001 | J460-01-1VAV-707 | Setting | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-707_Vmin_HASP |  | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2485 | J270-06-1PNL-001 | J460-01-1VAV-707 | Alarm | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-707_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2486 | J270-06-1PNL-001 | J460-01-1VAV-707 | Setting | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-707_Vmin_LASP |  | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2487 | J270-06-1PNL-001 | J460-01-1VAV-707 | Alarm | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-707_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2488 | J270-06-1PNL-001 | J460-01-1VAV-707 | Setting | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-707_Vnom_HASP |  | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2489 | J270-06-1PNL-001 | J460-01-1VAV-707 | Alarm | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-707_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2490 | J270-06-1PNL-001 | J460-01-1VAV-707 | Setting | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-707_Vnom_LASP |  | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2526 | J270-06-1PNL-001 | J460-01-1VAV-707 | Setting | J460-01-1VAV-707 - Room J0.07 - Return Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-707_MinOpnFlwSP |  | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1632 | J270-06-1PNL-001 | J460-01-1VAV-708 | Alarm | J460-01-1VAV-708 - Room J6.23 - Supply Air Flow Control - Communication Failure Alarm | J460-01-1VAV-708_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1633 | J270-06-1PNL-001 | J460-01-1VAV-708 | Setting | J460-01-1VAV-708 - Room J6.23 - Supply Air Flow Control Operating Mode Entire Room | J460-01-1VAV-708_Mode |  | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1634 | J270-06-1PNL-001 | J460-01-1VAV-708 | Setting | J460-01-1VAV-708 - Room J6.23 - Supply Air Flow Control Volume Flow SP Shift | J460-01-1VAV-708_FlwSPShift |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1635 | J270-06-1PNL-001 | J460-01-1VAV-708 | Measurement | J460-01-1VAV-708 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-01-1VAV-708_LocAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1636 | J270-06-1PNL-001 | J460-01-1VAV-708 | Alarm | J460-01-1VAV-708 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-01-1VAV-708_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1637 | J270-06-1PNL-001 | J460-01-1VAV-708 | Measurement | J460-01-1VAV-708 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-01-1VAV-708_SumAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1638 | J270-06-1PNL-001 | J460-01-1VAV-708 | Alarm | J460-01-1VAV-708 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-01-1VAV-708_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 1639 | J270-06-1PNL-001 | J460-01-1VAV-708 | Measurement | J460-02-1VAV-608 - Room J6.23 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-608_RmEaFlwTot |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1640 | J270-06-1PNL-001 | J460-01-1VAV-708 | Measurement | J460-01-1VAV-708 - Room J6.23 - Supply Air Flow Control Supply Air Volume | J460-01-1VAV-708_RmSaFlw |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 535 | J270-06-1PNL-001 | J460-01-2TC-706 | Alarm | J460-01-2TC-706 - Room J6.02 - Room Controller - Communication Failure Alarm | J460-01-2TC-706_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2139 | J270-06-1PNL-001 | J460-01-2FCV-720 | Alarm | J460-01-2FCV-720 - Room J6.14 - Reheater Valve Control - Communication Failure Alarm | J460-01-2FCV-720_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2140 | J270-06-1PNL-001 | J460-01-2FCV-720 | Measurement | J460-01-2FCV-720 - Room J6.14 - Reheater Valve Control Forced Position | J460-01-2FCV-720_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2141 | J270-06-1PNL-001 | J460-01-2FCV-720 | Setting | J460-01-2FCV-720 - Room J6.14 - Reheater Valve Control Forced Calibration | J460-01-2FCV-720_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2142 | J270-06-1PNL-001 | J460-01-2FCV-720 | Measurement | J460-01-2FCV-720 - Room J6.14 - Reheater Valve Control Status | J460-01-2FCV-720_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2143 | J270-06-1PNL-001 | J460-01-2FCV-720 | Measurement | J460-01-2FCV-720 - Room J6.14 - Reheater Valve Control Actual SP | J460-01-2FCV-720_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2144 | J270-06-1PNL-001 | J460-01-2FCV-720 | Setting | J460-01-2FCV-720 - Room J6.14 - Reheater Valve Control SP | J460-01-2FCV-720_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2145 | J270-06-1PNL-001 | J460-01-2FCV-720 | Alarm | J460-01-2FCV-720 - Room J6.14 - Reheater Valve Control Fail to Open Alarm | J460-01-2FCV-720_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2146 | J270-06-1PNL-001 | J460-01-2FCV-720 | Alarm | J460-01-2FCV-720 - Room J6.14 - Reheater Valve Control Fail to Close Alarm | J460-01-2FCV-720_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2147 | J270-06-1PNL-001 | J460-01-2FCV-720 | Measurement | J460-01-2FCV-720 - Room J6.14 - Reheater Valve Control Error Code | J460-01-2FCV-720_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2594 | J270-06-1PNL-001 | J460-01-2FCV-720 | Measurement | J460-01-2FCV-720 - Room J6.14 - Reheater Valve Control Speed | J460-01-2FCV-720_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1632 | J270-06-1PNL-001 | J460-01-1VAV-709 | Alarm | J460-01-1VAV-709 - Room J6.23 - Supply Air Flow Control - Communication Failure Alarm | J460-01-1VAV-709_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1633 | J270-06-1PNL-001 | J460-01-1VAV-709 | Setting | J460-01-1VAV-709 - Room J6.23 - Supply Air Flow Control Operating Mode Entire Room | J460-01-1VAV-709_Mode |  | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1634 | J270-06-1PNL-001 | J460-01-1VAV-709 | Setting | J460-01-1VAV-709 - Room J6.23 - Supply Air Flow Control Volume Flow SP Shift | J460-01-1VAV-709_FlwSPShift |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1635 | J270-06-1PNL-001 | J460-01-1VAV-709 | Measurement | J460-01-1VAV-709 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-01-1VAV-709_LocAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1636 | J270-06-1PNL-001 | J460-01-1VAV-709 | Alarm | J460-01-1VAV-709 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-01-1VAV-709_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1637 | J270-06-1PNL-001 | J460-01-1VAV-709 | Measurement | J460-01-1VAV-709 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-01-1VAV-709_SumAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1638 | J270-06-1PNL-001 | J460-01-1VAV-709 | Alarm | J460-01-1VAV-709 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-01-1VAV-709_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 1639 | J270-06-1PNL-001 | J460-01-1VAV-709 | Measurement | J460-02-1VAV-608 - Room J6.23 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-608_RmEaFlwTot |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1640 | J270-06-1PNL-001 | J460-01-1VAV-709 | Measurement | J460-01-1VAV-709 - Room J6.23 - Supply Air Flow Control Supply Air Volume | J460-01-1VAV-709_RmSaFlw |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2256 | J270-06-1PNL-001 | J460-01-1VAV-710 | Alarm | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control - Communication Failure Alarm | J460-01-1VAV-710_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 2257 | J270-06-1PNL-001 | J460-01-1VAV-710 | Setting | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Flow Setpoint | J460-01-1VAV-710_SpRel |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2258 | J270-06-1PNL-001 | J460-01-1VAV-710 | Measurement | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Relative Position | J460-01-1VAV-710_RelPos |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2259 | J270-06-1PNL-001 | J460-01-1VAV-710 | Measurement | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-710_AbsFlw |  | 0 | 650 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2260 | J270-06-1PNL-001 | J460-01-1VAV-710 | Alarm | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-710_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 2261 | J270-06-1PNL-001 | J460-01-1VAV-710 | Setting | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-710_AbsFlw_HASP |  | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2262 | J270-06-1PNL-001 | J460-01-1VAV-710 | Alarm | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-710_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 2263 | J270-06-1PNL-001 | J460-01-1VAV-710 | Setting | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-710_AbsFlw_LASP |  | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2264 | J270-06-1PNL-001 | J460-01-1VAV-710 | Measurement | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-710_Vmin |  | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2265 | J270-06-1PNL-001 | J460-01-1VAV-710 | Measurement | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Maximum Flow | J460-01-1VAV-710_Vmax |  | 650 | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2266 | J270-06-1PNL-001 | J460-01-1VAV-710 | Measurement | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-710_Vnom |  | 0 | 650 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2267 | J270-06-1PNL-001 | J460-01-1VAV-710 | Measurement | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Summary Status | J460-01-1VAV-710_SumSts |  | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2268 | J270-06-1PNL-001 | J460-01-1VAV-710 | Alarm | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Summary Status Alarm | J460-01-1VAV-710_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 2269 | J270-06-1PNL-001 | J460-01-1VAV-710 | Measurement | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Actuator Status | J460-01-1VAV-710_ActSts |  | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2270 | J270-06-1PNL-001 | J460-01-1VAV-710 | Measurement | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Device Status | J460-01-1VAV-710_DevSts |  | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2271 | J270-06-1PNL-001 | J460-01-1VAV-710 | Setting | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Device Override | J460-01-1VAV-710_Override |  | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
A.03 | 2483 | J270-06-1PNL-001 | J460-01-1VAV-710 | Alarm | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-710_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2484 | J270-06-1PNL-001 | J460-01-1VAV-710 | Setting | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-710_Vmin_HASP |  | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2485 | J270-06-1PNL-001 | J460-01-1VAV-710 | Alarm | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-710_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2486 | J270-06-1PNL-001 | J460-01-1VAV-710 | Setting | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-710_Vmin_LASP |  | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2487 | J270-06-1PNL-001 | J460-01-1VAV-710 | Alarm | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-710_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2488 | J270-06-1PNL-001 | J460-01-1VAV-710 | Setting | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-710_Vnom_HASP |  | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2489 | J270-06-1PNL-001 | J460-01-1VAV-710 | Alarm | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-710_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2490 | J270-06-1PNL-001 | J460-01-1VAV-710 | Setting | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-710_Vnom_LASP |  | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2526 | J270-06-1PNL-001 | J460-01-1VAV-710 | Setting | J460-01-1VAV-710 - Room J0.07 - Return Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-710_MinOpnFlwSP |  | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2184 | J270-06-1PNL-001 | J460-01-2FCV-721 | Alarm | J460-01-2FCV-721 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control - Communication Failure Alarm | J460-01-2FCV-721_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2185 | J270-06-1PNL-001 | J460-01-2FCV-721 | Measurement | J460-01-2FCV-721 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Position | J460-01-2FCV-721_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2186 | J270-06-1PNL-001 | J460-01-2FCV-721 | Setting | J460-01-2FCV-721 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Calibration | J460-01-2FCV-721_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2187 | J270-06-1PNL-001 | J460-01-2FCV-721 | Measurement | J460-01-2FCV-721 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Status | J460-01-2FCV-721_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2188 | J270-06-1PNL-001 | J460-01-2FCV-721 | Measurement | J460-01-2FCV-721 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Actual SP | J460-01-2FCV-721_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2189 | J270-06-1PNL-001 | J460-01-2FCV-721 | Setting | J460-01-2FCV-721 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control SP | J460-01-2FCV-721_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2190 | J270-06-1PNL-001 | J460-01-2FCV-721 | Alarm | J460-01-2FCV-721 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Open Alarm | J460-01-2FCV-721_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2191 | J270-06-1PNL-001 | J460-01-2FCV-721 | Alarm | J460-01-2FCV-721 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Close Alarm | J460-01-2FCV-721_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2192 | J270-06-1PNL-001 | J460-01-2FCV-721 | Measurement | J460-01-2FCV-721 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Error Code | J460-01-2FCV-721_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2595 | J270-06-1PNL-001 | J460-01-2FCV-721 | Measurement | J460-01-2FCV-721 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Speed | J460-01-2FCV-721_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2220 | J270-06-1PNL-001 | J460-01-2FCV-722 | Alarm | J460-01-2FCV-722 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control - Communication Failure Alarm | J460-01-2FCV-722_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2221 | J270-06-1PNL-001 | J460-01-2FCV-722 | Measurement | J460-01-2FCV-722 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Position | J460-01-2FCV-722_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2222 | J270-06-1PNL-001 | J460-01-2FCV-722 | Setting | J460-01-2FCV-722 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Calibration | J460-01-2FCV-722_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2223 | J270-06-1PNL-001 | J460-01-2FCV-722 | Measurement | J460-01-2FCV-722 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Status | J460-01-2FCV-722_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2224 | J270-06-1PNL-001 | J460-01-2FCV-722 | Measurement | J460-01-2FCV-722 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Actual SP | J460-01-2FCV-722_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2225 | J270-06-1PNL-001 | J460-01-2FCV-722 | Setting | J460-01-2FCV-722 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control SP | J460-01-2FCV-722_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2226 | J270-06-1PNL-001 | J460-01-2FCV-722 | Alarm | J460-01-2FCV-722 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Open Alarm | J460-01-2FCV-722_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2227 | J270-06-1PNL-001 | J460-01-2FCV-722 | Alarm | J460-01-2FCV-722 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Close Alarm | J460-01-2FCV-722_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2228 | J270-06-1PNL-001 | J460-01-2FCV-722 | Measurement | J460-01-2FCV-722 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Error Code | J460-01-2FCV-722_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2599 | J270-06-1PNL-001 | J460-01-2FCV-722 | Measurement | J460-01-2FCV-722 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Speed | J460-01-2FCV-722_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1632 | J270-06-1PNL-001 | J460-01-1VAV-711 | Alarm | J460-01-1VAV-711 - Room J6.23 - Supply Air Flow Control - Communication Failure Alarm | J460-01-1VAV-711_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1633 | J270-06-1PNL-001 | J460-01-1VAV-711 | Setting | J460-01-1VAV-711 - Room J6.23 - Supply Air Flow Control Operating Mode Entire Room | J460-01-1VAV-711_Mode |  | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1634 | J270-06-1PNL-001 | J460-01-1VAV-711 | Setting | J460-01-1VAV-711 - Room J6.23 - Supply Air Flow Control Volume Flow SP Shift | J460-01-1VAV-711_FlwSPShift |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1635 | J270-06-1PNL-001 | J460-01-1VAV-711 | Measurement | J460-01-1VAV-711 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-01-1VAV-711_LocAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1636 | J270-06-1PNL-001 | J460-01-1VAV-711 | Alarm | J460-01-1VAV-711 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-01-1VAV-711_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1637 | J270-06-1PNL-001 | J460-01-1VAV-711 | Measurement | J460-01-1VAV-711 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-01-1VAV-711_SumAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1638 | J270-06-1PNL-001 | J460-01-1VAV-711 | Alarm | J460-01-1VAV-711 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-01-1VAV-711_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 1639 | J270-06-1PNL-001 | J460-01-1VAV-711 | Measurement | J460-02-1VAV-608 - Room J6.23 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-608_RmEaFlwTot |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1640 | J270-06-1PNL-001 | J460-01-1VAV-711 | Measurement | J460-01-1VAV-711 - Room J6.23 - Supply Air Flow Control Supply Air Volume | J460-01-1VAV-711_RmSaFlw |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 535 | J270-06-1PNL-001 | J460-01-2TC-707 | Alarm | J460-01-2TC-707 - Room J6.02 - Room Controller - Communication Failure Alarm | J460-01-2TC-707_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2139 | J270-06-1PNL-001 | J460-01-2FCV-723 | Alarm | J460-01-2FCV-723 - Room J6.14 - Reheater Valve Control - Communication Failure Alarm | J460-01-2FCV-723_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2140 | J270-06-1PNL-001 | J460-01-2FCV-723 | Measurement | J460-01-2FCV-723 - Room J6.14 - Reheater Valve Control Forced Position | J460-01-2FCV-723_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2141 | J270-06-1PNL-001 | J460-01-2FCV-723 | Setting | J460-01-2FCV-723 - Room J6.14 - Reheater Valve Control Forced Calibration | J460-01-2FCV-723_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2142 | J270-06-1PNL-001 | J460-01-2FCV-723 | Measurement | J460-01-2FCV-723 - Room J6.14 - Reheater Valve Control Status | J460-01-2FCV-723_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2143 | J270-06-1PNL-001 | J460-01-2FCV-723 | Measurement | J460-01-2FCV-723 - Room J6.14 - Reheater Valve Control Actual SP | J460-01-2FCV-723_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2144 | J270-06-1PNL-001 | J460-01-2FCV-723 | Setting | J460-01-2FCV-723 - Room J6.14 - Reheater Valve Control SP | J460-01-2FCV-723_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2145 | J270-06-1PNL-001 | J460-01-2FCV-723 | Alarm | J460-01-2FCV-723 - Room J6.14 - Reheater Valve Control Fail to Open Alarm | J460-01-2FCV-723_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2146 | J270-06-1PNL-001 | J460-01-2FCV-723 | Alarm | J460-01-2FCV-723 - Room J6.14 - Reheater Valve Control Fail to Close Alarm | J460-01-2FCV-723_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2147 | J270-06-1PNL-001 | J460-01-2FCV-723 | Measurement | J460-01-2FCV-723 - Room J6.14 - Reheater Valve Control Error Code | J460-01-2FCV-723_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2594 | J270-06-1PNL-001 | J460-01-2FCV-723 | Measurement | J460-01-2FCV-723 - Room J6.14 - Reheater Valve Control Speed | J460-01-2FCV-723_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1632 | J270-06-1PNL-001 | J460-01-1VAV-712 | Alarm | J460-01-1VAV-712 - Room J6.23 - Supply Air Flow Control - Communication Failure Alarm | J460-01-1VAV-712_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1633 | J270-06-1PNL-001 | J460-01-1VAV-712 | Setting | J460-01-1VAV-712 - Room J6.23 - Supply Air Flow Control Operating Mode Entire Room | J460-01-1VAV-712_Mode |  | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1634 | J270-06-1PNL-001 | J460-01-1VAV-712 | Setting | J460-01-1VAV-712 - Room J6.23 - Supply Air Flow Control Volume Flow SP Shift | J460-01-1VAV-712_FlwSPShift |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1635 | J270-06-1PNL-001 | J460-01-1VAV-712 | Measurement | J460-01-1VAV-712 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-01-1VAV-712_LocAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1636 | J270-06-1PNL-001 | J460-01-1VAV-712 | Alarm | J460-01-1VAV-712 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-01-1VAV-712_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1637 | J270-06-1PNL-001 | J460-01-1VAV-712 | Measurement | J460-01-1VAV-712 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-01-1VAV-712_SumAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1638 | J270-06-1PNL-001 | J460-01-1VAV-712 | Alarm | J460-01-1VAV-712 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-01-1VAV-712_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 1639 | J270-06-1PNL-001 | J460-01-1VAV-712 | Measurement | J460-02-1VAV-608 - Room J6.23 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-608_RmEaFlwTot |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1640 | J270-06-1PNL-001 | J460-01-1VAV-712 | Measurement | J460-01-1VAV-712 - Room J6.23 - Supply Air Flow Control Supply Air Volume | J460-01-1VAV-712_RmSaFlw |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2256 | J270-06-1PNL-001 | J460-01-1VAV-713 | Alarm | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control - Communication Failure Alarm | J460-01-1VAV-713_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 2257 | J270-06-1PNL-001 | J460-01-1VAV-713 | Setting | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Flow Setpoint | J460-01-1VAV-713_SpRel |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2258 | J270-06-1PNL-001 | J460-01-1VAV-713 | Measurement | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Relative Position | J460-01-1VAV-713_RelPos |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2259 | J270-06-1PNL-001 | J460-01-1VAV-713 | Measurement | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-713_AbsFlw |  | 0 | 650 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2260 | J270-06-1PNL-001 | J460-01-1VAV-713 | Alarm | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-713_AbsFlwHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 2261 | J270-06-1PNL-001 | J460-01-1VAV-713 | Setting | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-713_AbsFlw_HASP |  | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2262 | J270-06-1PNL-001 | J460-01-1VAV-713 | Alarm | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-713_AbsFlwLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 2263 | J270-06-1PNL-001 | J460-01-1VAV-713 | Setting | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Absolute Flow | J460-01-1VAV-713_AbsFlw_LASP |  | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2264 | J270-06-1PNL-001 | J460-01-1VAV-713 | Measurement | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-713_Vmin |  | Calculated | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 2265 | J270-06-1PNL-001 | J460-01-1VAV-713 | Measurement | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Maximum Flow | J460-01-1VAV-713_Vmax |  | 650 | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2266 | J270-06-1PNL-001 | J460-01-1VAV-713 | Measurement | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-713_Vnom |  | 0 | 650 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2267 | J270-06-1PNL-001 | J460-01-1VAV-713 | Measurement | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Summary Status | J460-01-1VAV-713_SumSts |  | NOERROR | ERROR | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2268 | J270-06-1PNL-001 | J460-01-1VAV-713 | Alarm | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Summary Status Alarm | J460-01-1VAV-713_SumSts_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 2269 | J270-06-1PNL-001 | J460-01-1VAV-713 | Measurement | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Actuator Status | J460-01-1VAV-713_ActSts |  | - | OK | ACTCOMOV | GRELACTV | MECTRVXD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2270 | J270-06-1PNL-001 | J460-01-1VAV-713 | Measurement | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Device Status | J460-01-1VAV-713_DevSts |  | - | OK | BTOMACTV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 2271 | J270-06-1PNL-001 | J460-01-1VAV-713 | Setting | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Device Override | J460-01-1VAV-713_Override |  | - | NONE | OPEN | CLOSED | QVMIN | QVMID | QVMAX | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
A.03 | 2483 | J270-06-1PNL-001 | J460-01-1VAV-713 | Alarm | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Minimum Flow High Alarm | J460-01-1VAV-713_VminHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2484 | J270-06-1PNL-001 | J460-01-1VAV-713 | Setting | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-713_Vmin_HASP |  | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2485 | J270-06-1PNL-001 | J460-01-1VAV-713 | Alarm | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Minimum Flow Low Alarm | J460-01-1VAV-713_VminLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2486 | J270-06-1PNL-001 | J460-01-1VAV-713 | Setting | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Minimum Flow | J460-01-1VAV-713_Vmin_LASP |  | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2487 | J270-06-1PNL-001 | J460-01-1VAV-713 | Alarm | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Nominal Flow High Alarm | J460-01-1VAV-713_VnomHiAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2488 | J270-06-1PNL-001 | J460-01-1VAV-713 | Setting | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-713_Vnom_HASP |  | - | Calculated | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
A.03 | 2489 | J270-06-1PNL-001 | J460-01-1VAV-713 | Alarm | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Nominal Flow Low Alarm | J460-01-1VAV-713_VnomLoAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
A.03 | 2490 | J270-06-1PNL-001 | J460-01-1VAV-713 | Setting | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Nominal Flow | J460-01-1VAV-713_Vnom_LASP |  | Calculated | - | [11 empty] | - | - | - | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 2526 | J270-06-1PNL-001 | J460-01-1VAV-713 | Setting | J460-01-1VAV-713 - Room J0.07 - Return Air Flow Control Minimum Open Flow Setpoint | J460-01-1VAV-713_MinOpnFlwSP |  | 30 | - | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 535 | J270-06-1PNL-001 | J460-01-2TC-708 | Alarm | J460-01-2TC-708 - Room J6.02 - Room Controller - Communication Failure Alarm | J460-01-2TC-708_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2139 | J270-06-1PNL-001 | J460-01-2FCV-724 | Alarm | J460-01-2FCV-724 - Room J6.14 - Reheater Valve Control - Communication Failure Alarm | J460-01-2FCV-724_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2140 | J270-06-1PNL-001 | J460-01-2FCV-724 | Measurement | J460-01-2FCV-724 - Room J6.14 - Reheater Valve Control Forced Position | J460-01-2FCV-724_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2141 | J270-06-1PNL-001 | J460-01-2FCV-724 | Setting | J460-01-2FCV-724 - Room J6.14 - Reheater Valve Control Forced Calibration | J460-01-2FCV-724_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2142 | J270-06-1PNL-001 | J460-01-2FCV-724 | Measurement | J460-01-2FCV-724 - Room J6.14 - Reheater Valve Control Status | J460-01-2FCV-724_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2143 | J270-06-1PNL-001 | J460-01-2FCV-724 | Measurement | J460-01-2FCV-724 - Room J6.14 - Reheater Valve Control Actual SP | J460-01-2FCV-724_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2144 | J270-06-1PNL-001 | J460-01-2FCV-724 | Setting | J460-01-2FCV-724 - Room J6.14 - Reheater Valve Control SP | J460-01-2FCV-724_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2145 | J270-06-1PNL-001 | J460-01-2FCV-724 | Alarm | J460-01-2FCV-724 - Room J6.14 - Reheater Valve Control Fail to Open Alarm | J460-01-2FCV-724_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2146 | J270-06-1PNL-001 | J460-01-2FCV-724 | Alarm | J460-01-2FCV-724 - Room J6.14 - Reheater Valve Control Fail to Close Alarm | J460-01-2FCV-724_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2147 | J270-06-1PNL-001 | J460-01-2FCV-724 | Measurement | J460-01-2FCV-724 - Room J6.14 - Reheater Valve Control Error Code | J460-01-2FCV-724_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2594 | J270-06-1PNL-001 | J460-01-2FCV-724 | Measurement | J460-01-2FCV-724 - Room J6.14 - Reheater Valve Control Speed | J460-01-2FCV-724_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2220 | J270-06-1PNL-001 | J460-02-2FCV-701 | Alarm | J460-02-2FCV-701 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control - Communication Failure Alarm | J460-02-2FCV-701_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2221 | J270-06-1PNL-001 | J460-02-2FCV-701 | Measurement | J460-02-2FCV-701 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Position | J460-02-2FCV-701_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2222 | J270-06-1PNL-001 | J460-02-2FCV-701 | Setting | J460-02-2FCV-701 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Calibration | J460-02-2FCV-701_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2223 | J270-06-1PNL-001 | J460-02-2FCV-701 | Measurement | J460-02-2FCV-701 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Status | J460-02-2FCV-701_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2224 | J270-06-1PNL-001 | J460-02-2FCV-701 | Measurement | J460-02-2FCV-701 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Actual SP | J460-02-2FCV-701_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2225 | J270-06-1PNL-001 | J460-02-2FCV-701 | Setting | J460-02-2FCV-701 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control SP | J460-02-2FCV-701_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2226 | J270-06-1PNL-001 | J460-02-2FCV-701 | Alarm | J460-02-2FCV-701 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Open Alarm | J460-02-2FCV-701_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2227 | J270-06-1PNL-001 | J460-02-2FCV-701 | Alarm | J460-02-2FCV-701 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Close Alarm | J460-02-2FCV-701_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2228 | J270-06-1PNL-001 | J460-02-2FCV-701 | Measurement | J460-02-2FCV-701 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Error Code | J460-02-2FCV-701_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2599 | J270-06-1PNL-001 | J460-02-2FCV-701 | Measurement | J460-02-2FCV-701 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Speed | J460-02-2FCV-701_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2220 | J270-06-1PNL-001 | J460-02-2FCV-727 | Alarm | J460-02-2FCV-727 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control - Communication Failure Alarm | J460-02-2FCV-727_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2221 | J270-06-1PNL-001 | J460-02-2FCV-727 | Measurement | J460-02-2FCV-727 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Position | J460-02-2FCV-727_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2222 | J270-06-1PNL-001 | J460-02-2FCV-727 | Setting | J460-02-2FCV-727 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Calibration | J460-02-2FCV-727_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2223 | J270-06-1PNL-001 | J460-02-2FCV-727 | Measurement | J460-02-2FCV-727 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Status | J460-02-2FCV-727_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2224 | J270-06-1PNL-001 | J460-02-2FCV-727 | Measurement | J460-02-2FCV-727 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Actual SP | J460-02-2FCV-727_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2225 | J270-06-1PNL-001 | J460-02-2FCV-727 | Setting | J460-02-2FCV-727 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control SP | J460-02-2FCV-727_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2226 | J270-06-1PNL-001 | J460-02-2FCV-727 | Alarm | J460-02-2FCV-727 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Open Alarm | J460-02-2FCV-727_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2227 | J270-06-1PNL-001 | J460-02-2FCV-727 | Alarm | J460-02-2FCV-727 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Close Alarm | J460-02-2FCV-727_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2228 | J270-06-1PNL-001 | J460-02-2FCV-727 | Measurement | J460-02-2FCV-727 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Error Code | J460-02-2FCV-727_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2599 | J270-06-1PNL-001 | J460-02-2FCV-727 | Measurement | J460-02-2FCV-727 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Speed | J460-02-2FCV-727_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2220 | J270-06-1PNL-001 | J460-02-2FCV-702 | Alarm | J460-02-2FCV-702 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control - Communication Failure Alarm | J460-02-2FCV-702_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2221 | J270-06-1PNL-001 | J460-02-2FCV-702 | Measurement | J460-02-2FCV-702 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Position | J460-02-2FCV-702_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2222 | J270-06-1PNL-001 | J460-02-2FCV-702 | Setting | J460-02-2FCV-702 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Calibration | J460-02-2FCV-702_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2223 | J270-06-1PNL-001 | J460-02-2FCV-702 | Measurement | J460-02-2FCV-702 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Status | J460-02-2FCV-702_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2224 | J270-06-1PNL-001 | J460-02-2FCV-702 | Measurement | J460-02-2FCV-702 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Actual SP | J460-02-2FCV-702_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2225 | J270-06-1PNL-001 | J460-02-2FCV-702 | Setting | J460-02-2FCV-702 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control SP | J460-02-2FCV-702_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2226 | J270-06-1PNL-001 | J460-02-2FCV-702 | Alarm | J460-02-2FCV-702 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Open Alarm | J460-02-2FCV-702_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2227 | J270-06-1PNL-001 | J460-02-2FCV-702 | Alarm | J460-02-2FCV-702 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Close Alarm | J460-02-2FCV-702_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2228 | J270-06-1PNL-001 | J460-02-2FCV-702 | Measurement | J460-02-2FCV-702 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Error Code | J460-02-2FCV-702_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2599 | J270-06-1PNL-001 | J460-02-2FCV-702 | Measurement | J460-02-2FCV-702 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Speed | J460-02-2FCV-702_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2184 | J270-06-1PNL-001 | J460-02-2FCV-703 | Alarm | J460-02-2FCV-703 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control - Communication Failure Alarm | J460-02-2FCV-703_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2185 | J270-06-1PNL-001 | J460-02-2FCV-703 | Measurement | J460-02-2FCV-703 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Position | J460-02-2FCV-703_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2186 | J270-06-1PNL-001 | J460-02-2FCV-703 | Setting | J460-02-2FCV-703 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Calibration | J460-02-2FCV-703_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2187 | J270-06-1PNL-001 | J460-02-2FCV-703 | Measurement | J460-02-2FCV-703 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Status | J460-02-2FCV-703_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2188 | J270-06-1PNL-001 | J460-02-2FCV-703 | Measurement | J460-02-2FCV-703 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Actual SP | J460-02-2FCV-703_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2189 | J270-06-1PNL-001 | J460-02-2FCV-703 | Setting | J460-02-2FCV-703 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control SP | J460-02-2FCV-703_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2190 | J270-06-1PNL-001 | J460-02-2FCV-703 | Alarm | J460-02-2FCV-703 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Open Alarm | J460-02-2FCV-703_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2191 | J270-06-1PNL-001 | J460-02-2FCV-703 | Alarm | J460-02-2FCV-703 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Close Alarm | J460-02-2FCV-703_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2192 | J270-06-1PNL-001 | J460-02-2FCV-703 | Measurement | J460-02-2FCV-703 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Error Code | J460-02-2FCV-703_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2595 | J270-06-1PNL-001 | J460-02-2FCV-703 | Measurement | J460-02-2FCV-703 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Speed | J460-02-2FCV-703_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1632 | J270-06-1PNL-001 | J460-02-1VAV-702 | Alarm | J460-02-1VAV-702 - Room J6.23 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-702_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1633 | J270-06-1PNL-001 | J460-02-1VAV-702 | Setting | J460-02-1VAV-702 - Room J6.23 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-702_Mode |  | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1634 | J270-06-1PNL-001 | J460-02-1VAV-702 | Setting | J460-02-1VAV-702 - Room J6.23 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-702_FlwSPShift |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1635 | J270-06-1PNL-001 | J460-02-1VAV-702 | Measurement | J460-02-1VAV-702 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-702_LocAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1636 | J270-06-1PNL-001 | J460-02-1VAV-702 | Alarm | J460-02-1VAV-702 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-702_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1637 | J270-06-1PNL-001 | J460-02-1VAV-702 | Measurement | J460-02-1VAV-702 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-702_SumAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1638 | J270-06-1PNL-001 | J460-02-1VAV-702 | Alarm | J460-02-1VAV-702 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-702_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 1639 | J270-06-1PNL-001 | J460-02-1VAV-702 | Measurement | J460-02-1VAV-608 - Room J6.23 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-608_RmEaFlwTot |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1640 | J270-06-1PNL-001 | J460-02-1VAV-702 | Measurement | J460-02-1VAV-702 - Room J6.23 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-702_RmSaFlw |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2139 | J270-06-1PNL-001 | J460-02-2FCV-704 | Alarm | J460-02-2FCV-704 - Room J6.14 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-704_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2140 | J270-06-1PNL-001 | J460-02-2FCV-704 | Measurement | J460-02-2FCV-704 - Room J6.14 - Reheater Valve Control Forced Position | J460-02-2FCV-704_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2141 | J270-06-1PNL-001 | J460-02-2FCV-704 | Setting | J460-02-2FCV-704 - Room J6.14 - Reheater Valve Control Forced Calibration | J460-02-2FCV-704_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2142 | J270-06-1PNL-001 | J460-02-2FCV-704 | Measurement | J460-02-2FCV-704 - Room J6.14 - Reheater Valve Control Status | J460-02-2FCV-704_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2143 | J270-06-1PNL-001 | J460-02-2FCV-704 | Measurement | J460-02-2FCV-704 - Room J6.14 - Reheater Valve Control Actual SP | J460-02-2FCV-704_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2144 | J270-06-1PNL-001 | J460-02-2FCV-704 | Setting | J460-02-2FCV-704 - Room J6.14 - Reheater Valve Control SP | J460-02-2FCV-704_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2145 | J270-06-1PNL-001 | J460-02-2FCV-704 | Alarm | J460-02-2FCV-704 - Room J6.14 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-704_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2146 | J270-06-1PNL-001 | J460-02-2FCV-704 | Alarm | J460-02-2FCV-704 - Room J6.14 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-704_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2147 | J270-06-1PNL-001 | J460-02-2FCV-704 | Measurement | J460-02-2FCV-704 - Room J6.14 - Reheater Valve Control Error Code | J460-02-2FCV-704_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2594 | J270-06-1PNL-001 | J460-02-2FCV-704 | Measurement | J460-02-2FCV-704 - Room J6.14 - Reheater Valve Control Speed | J460-02-2FCV-704_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1632 | J270-06-1PNL-001 | J460-02-1VAV-704 | Alarm | J460-02-1VAV-704 - Room J6.23 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-704_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1633 | J270-06-1PNL-001 | J460-02-1VAV-704 | Setting | J460-02-1VAV-704 - Room J6.23 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-704_Mode |  | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1634 | J270-06-1PNL-001 | J460-02-1VAV-704 | Setting | J460-02-1VAV-704 - Room J6.23 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-704_FlwSPShift |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1635 | J270-06-1PNL-001 | J460-02-1VAV-704 | Measurement | J460-02-1VAV-704 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-704_LocAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1636 | J270-06-1PNL-001 | J460-02-1VAV-704 | Alarm | J460-02-1VAV-704 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-704_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1637 | J270-06-1PNL-001 | J460-02-1VAV-704 | Measurement | J460-02-1VAV-704 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-704_SumAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1638 | J270-06-1PNL-001 | J460-02-1VAV-704 | Alarm | J460-02-1VAV-704 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-704_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 1639 | J270-06-1PNL-001 | J460-02-1VAV-704 | Measurement | J460-02-1VAV-608 - Room J6.23 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-608_RmEaFlwTot |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1640 | J270-06-1PNL-001 | J460-02-1VAV-704 | Measurement | J460-02-1VAV-704 - Room J6.23 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-704_RmSaFlw |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2139 | J270-06-1PNL-001 | J460-02-2FCV-705 | Alarm | J460-02-2FCV-705 - Room J6.14 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-705_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2140 | J270-06-1PNL-001 | J460-02-2FCV-705 | Measurement | J460-02-2FCV-705 - Room J6.14 - Reheater Valve Control Forced Position | J460-02-2FCV-705_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2141 | J270-06-1PNL-001 | J460-02-2FCV-705 | Setting | J460-02-2FCV-705 - Room J6.14 - Reheater Valve Control Forced Calibration | J460-02-2FCV-705_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2142 | J270-06-1PNL-001 | J460-02-2FCV-705 | Measurement | J460-02-2FCV-705 - Room J6.14 - Reheater Valve Control Status | J460-02-2FCV-705_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2143 | J270-06-1PNL-001 | J460-02-2FCV-705 | Measurement | J460-02-2FCV-705 - Room J6.14 - Reheater Valve Control Actual SP | J460-02-2FCV-705_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2144 | J270-06-1PNL-001 | J460-02-2FCV-705 | Setting | J460-02-2FCV-705 - Room J6.14 - Reheater Valve Control SP | J460-02-2FCV-705_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2145 | J270-06-1PNL-001 | J460-02-2FCV-705 | Alarm | J460-02-2FCV-705 - Room J6.14 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-705_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2146 | J270-06-1PNL-001 | J460-02-2FCV-705 | Alarm | J460-02-2FCV-705 - Room J6.14 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-705_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2147 | J270-06-1PNL-001 | J460-02-2FCV-705 | Measurement | J460-02-2FCV-705 - Room J6.14 - Reheater Valve Control Error Code | J460-02-2FCV-705_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2594 | J270-06-1PNL-001 | J460-02-2FCV-705 | Measurement | J460-02-2FCV-705 - Room J6.14 - Reheater Valve Control Speed | J460-02-2FCV-705_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2220 | J270-06-1PNL-001 | J460-02-2FCV-706 | Alarm | J460-02-2FCV-706 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control - Communication Failure Alarm | J460-02-2FCV-706_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2221 | J270-06-1PNL-001 | J460-02-2FCV-706 | Measurement | J460-02-2FCV-706 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Position | J460-02-2FCV-706_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2222 | J270-06-1PNL-001 | J460-02-2FCV-706 | Setting | J460-02-2FCV-706 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Calibration | J460-02-2FCV-706_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2223 | J270-06-1PNL-001 | J460-02-2FCV-706 | Measurement | J460-02-2FCV-706 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Status | J460-02-2FCV-706_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2224 | J270-06-1PNL-001 | J460-02-2FCV-706 | Measurement | J460-02-2FCV-706 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Actual SP | J460-02-2FCV-706_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2225 | J270-06-1PNL-001 | J460-02-2FCV-706 | Setting | J460-02-2FCV-706 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control SP | J460-02-2FCV-706_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2226 | J270-06-1PNL-001 | J460-02-2FCV-706 | Alarm | J460-02-2FCV-706 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Open Alarm | J460-02-2FCV-706_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2227 | J270-06-1PNL-001 | J460-02-2FCV-706 | Alarm | J460-02-2FCV-706 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Close Alarm | J460-02-2FCV-706_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2228 | J270-06-1PNL-001 | J460-02-2FCV-706 | Measurement | J460-02-2FCV-706 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Error Code | J460-02-2FCV-706_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2599 | J270-06-1PNL-001 | J460-02-2FCV-706 | Measurement | J460-02-2FCV-706 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Speed | J460-02-2FCV-706_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1632 | J270-06-1PNL-001 | J460-02-1VAV-705 | Alarm | J460-02-1VAV-705 - Room J6.23 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-705_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1633 | J270-06-1PNL-001 | J460-02-1VAV-705 | Setting | J460-02-1VAV-705 - Room J6.23 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-705_Mode |  | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1634 | J270-06-1PNL-001 | J460-02-1VAV-705 | Setting | J460-02-1VAV-705 - Room J6.23 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-705_FlwSPShift |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1635 | J270-06-1PNL-001 | J460-02-1VAV-705 | Measurement | J460-02-1VAV-705 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-705_LocAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1636 | J270-06-1PNL-001 | J460-02-1VAV-705 | Alarm | J460-02-1VAV-705 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-705_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1637 | J270-06-1PNL-001 | J460-02-1VAV-705 | Measurement | J460-02-1VAV-705 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-705_SumAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1638 | J270-06-1PNL-001 | J460-02-1VAV-705 | Alarm | J460-02-1VAV-705 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-705_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 1639 | J270-06-1PNL-001 | J460-02-1VAV-705 | Measurement | J460-02-1VAV-608 - Room J6.23 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-608_RmEaFlwTot |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1640 | J270-06-1PNL-001 | J460-02-1VAV-705 | Measurement | J460-02-1VAV-705 - Room J6.23 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-705_RmSaFlw |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2139 | J270-06-1PNL-001 | J460-02-2FCV-707 | Alarm | J460-02-2FCV-707 - Room J6.14 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-707_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2140 | J270-06-1PNL-001 | J460-02-2FCV-707 | Measurement | J460-02-2FCV-707 - Room J6.14 - Reheater Valve Control Forced Position | J460-02-2FCV-707_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2141 | J270-06-1PNL-001 | J460-02-2FCV-707 | Setting | J460-02-2FCV-707 - Room J6.14 - Reheater Valve Control Forced Calibration | J460-02-2FCV-707_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2142 | J270-06-1PNL-001 | J460-02-2FCV-707 | Measurement | J460-02-2FCV-707 - Room J6.14 - Reheater Valve Control Status | J460-02-2FCV-707_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2143 | J270-06-1PNL-001 | J460-02-2FCV-707 | Measurement | J460-02-2FCV-707 - Room J6.14 - Reheater Valve Control Actual SP | J460-02-2FCV-707_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2144 | J270-06-1PNL-001 | J460-02-2FCV-707 | Setting | J460-02-2FCV-707 - Room J6.14 - Reheater Valve Control SP | J460-02-2FCV-707_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2145 | J270-06-1PNL-001 | J460-02-2FCV-707 | Alarm | J460-02-2FCV-707 - Room J6.14 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-707_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2146 | J270-06-1PNL-001 | J460-02-2FCV-707 | Alarm | J460-02-2FCV-707 - Room J6.14 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-707_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2147 | J270-06-1PNL-001 | J460-02-2FCV-707 | Measurement | J460-02-2FCV-707 - Room J6.14 - Reheater Valve Control Error Code | J460-02-2FCV-707_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2594 | J270-06-1PNL-001 | J460-02-2FCV-707 | Measurement | J460-02-2FCV-707 - Room J6.14 - Reheater Valve Control Speed | J460-02-2FCV-707_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2220 | J270-06-1PNL-001 | J460-02-2FCV-708 | Alarm | J460-02-2FCV-708 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control - Communication Failure Alarm | J460-02-2FCV-708_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2221 | J270-06-1PNL-001 | J460-02-2FCV-708 | Measurement | J460-02-2FCV-708 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Position | J460-02-2FCV-708_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2222 | J270-06-1PNL-001 | J460-02-2FCV-708 | Setting | J460-02-2FCV-708 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Calibration | J460-02-2FCV-708_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2223 | J270-06-1PNL-001 | J460-02-2FCV-708 | Measurement | J460-02-2FCV-708 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Status | J460-02-2FCV-708_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2224 | J270-06-1PNL-001 | J460-02-2FCV-708 | Measurement | J460-02-2FCV-708 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Actual SP | J460-02-2FCV-708_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2225 | J270-06-1PNL-001 | J460-02-2FCV-708 | Setting | J460-02-2FCV-708 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control SP | J460-02-2FCV-708_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2226 | J270-06-1PNL-001 | J460-02-2FCV-708 | Alarm | J460-02-2FCV-708 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Open Alarm | J460-02-2FCV-708_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2227 | J270-06-1PNL-001 | J460-02-2FCV-708 | Alarm | J460-02-2FCV-708 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Close Alarm | J460-02-2FCV-708_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2228 | J270-06-1PNL-001 | J460-02-2FCV-708 | Measurement | J460-02-2FCV-708 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Error Code | J460-02-2FCV-708_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2599 | J270-06-1PNL-001 | J460-02-2FCV-708 | Measurement | J460-02-2FCV-708 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Speed | J460-02-2FCV-708_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1632 | J270-06-1PNL-001 | J460-02-1VAV-708 | Alarm | J460-02-1VAV-708 - Room J6.23 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-708_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1633 | J270-06-1PNL-001 | J460-02-1VAV-708 | Setting | J460-02-1VAV-708 - Room J6.23 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-708_Mode |  | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1634 | J270-06-1PNL-001 | J460-02-1VAV-708 | Setting | J460-02-1VAV-708 - Room J6.23 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-708_FlwSPShift |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1635 | J270-06-1PNL-001 | J460-02-1VAV-708 | Measurement | J460-02-1VAV-708 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-708_LocAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1636 | J270-06-1PNL-001 | J460-02-1VAV-708 | Alarm | J460-02-1VAV-708 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-708_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1637 | J270-06-1PNL-001 | J460-02-1VAV-708 | Measurement | J460-02-1VAV-708 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-708_SumAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1638 | J270-06-1PNL-001 | J460-02-1VAV-708 | Alarm | J460-02-1VAV-708 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-708_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 1639 | J270-06-1PNL-001 | J460-02-1VAV-708 | Measurement | J460-02-1VAV-608 - Room J6.23 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-608_RmEaFlwTot |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1640 | J270-06-1PNL-001 | J460-02-1VAV-708 | Measurement | J460-02-1VAV-708 - Room J6.23 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-708_RmSaFlw |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2139 | J270-06-1PNL-001 | J460-02-2FCV-709 | Alarm | J460-02-2FCV-709 - Room J6.14 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-709_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2140 | J270-06-1PNL-001 | J460-02-2FCV-709 | Measurement | J460-02-2FCV-709 - Room J6.14 - Reheater Valve Control Forced Position | J460-02-2FCV-709_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2141 | J270-06-1PNL-001 | J460-02-2FCV-709 | Setting | J460-02-2FCV-709 - Room J6.14 - Reheater Valve Control Forced Calibration | J460-02-2FCV-709_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2142 | J270-06-1PNL-001 | J460-02-2FCV-709 | Measurement | J460-02-2FCV-709 - Room J6.14 - Reheater Valve Control Status | J460-02-2FCV-709_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2143 | J270-06-1PNL-001 | J460-02-2FCV-709 | Measurement | J460-02-2FCV-709 - Room J6.14 - Reheater Valve Control Actual SP | J460-02-2FCV-709_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2144 | J270-06-1PNL-001 | J460-02-2FCV-709 | Setting | J460-02-2FCV-709 - Room J6.14 - Reheater Valve Control SP | J460-02-2FCV-709_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2145 | J270-06-1PNL-001 | J460-02-2FCV-709 | Alarm | J460-02-2FCV-709 - Room J6.14 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-709_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2146 | J270-06-1PNL-001 | J460-02-2FCV-709 | Alarm | J460-02-2FCV-709 - Room J6.14 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-709_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2147 | J270-06-1PNL-001 | J460-02-2FCV-709 | Measurement | J460-02-2FCV-709 - Room J6.14 - Reheater Valve Control Error Code | J460-02-2FCV-709_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2594 | J270-06-1PNL-001 | J460-02-2FCV-709 | Measurement | J460-02-2FCV-709 - Room J6.14 - Reheater Valve Control Speed | J460-02-2FCV-709_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2220 | J270-06-1PNL-001 | J460-02-2FCV-710 | Alarm | J460-02-2FCV-710 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control - Communication Failure Alarm | J460-02-2FCV-710_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2221 | J270-06-1PNL-001 | J460-02-2FCV-710 | Measurement | J460-02-2FCV-710 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Position | J460-02-2FCV-710_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2222 | J270-06-1PNL-001 | J460-02-2FCV-710 | Setting | J460-02-2FCV-710 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Calibration | J460-02-2FCV-710_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2223 | J270-06-1PNL-001 | J460-02-2FCV-710 | Measurement | J460-02-2FCV-710 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Status | J460-02-2FCV-710_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2224 | J270-06-1PNL-001 | J460-02-2FCV-710 | Measurement | J460-02-2FCV-710 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Actual SP | J460-02-2FCV-710_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2225 | J270-06-1PNL-001 | J460-02-2FCV-710 | Setting | J460-02-2FCV-710 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control SP | J460-02-2FCV-710_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2226 | J270-06-1PNL-001 | J460-02-2FCV-710 | Alarm | J460-02-2FCV-710 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Open Alarm | J460-02-2FCV-710_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2227 | J270-06-1PNL-001 | J460-02-2FCV-710 | Alarm | J460-02-2FCV-710 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Close Alarm | J460-02-2FCV-710_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2228 | J270-06-1PNL-001 | J460-02-2FCV-710 | Measurement | J460-02-2FCV-710 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Error Code | J460-02-2FCV-710_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2599 | J270-06-1PNL-001 | J460-02-2FCV-710 | Measurement | J460-02-2FCV-710 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Speed | J460-02-2FCV-710_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1632 | J270-06-1PNL-001 | J460-02-1VAV-712 | Alarm | J460-02-1VAV-712 - Room J6.23 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-712_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1633 | J270-06-1PNL-001 | J460-02-1VAV-712 | Setting | J460-02-1VAV-712 - Room J6.23 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-712_Mode |  | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1634 | J270-06-1PNL-001 | J460-02-1VAV-712 | Setting | J460-02-1VAV-712 - Room J6.23 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-712_FlwSPShift |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1635 | J270-06-1PNL-001 | J460-02-1VAV-712 | Measurement | J460-02-1VAV-712 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-712_LocAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1636 | J270-06-1PNL-001 | J460-02-1VAV-712 | Alarm | J460-02-1VAV-712 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-712_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1637 | J270-06-1PNL-001 | J460-02-1VAV-712 | Measurement | J460-02-1VAV-712 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-712_SumAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1638 | J270-06-1PNL-001 | J460-02-1VAV-712 | Alarm | J460-02-1VAV-712 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-712_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 1639 | J270-06-1PNL-001 | J460-02-1VAV-712 | Measurement | J460-02-1VAV-608 - Room J6.23 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-608_RmEaFlwTot |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1640 | J270-06-1PNL-001 | J460-02-1VAV-712 | Measurement | J460-02-1VAV-712 - Room J6.23 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-712_RmSaFlw |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2139 | J270-06-1PNL-001 | J460-02-2FCV-711 | Alarm | J460-02-2FCV-711 - Room J6.14 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-711_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2140 | J270-06-1PNL-001 | J460-02-2FCV-711 | Measurement | J460-02-2FCV-711 - Room J6.14 - Reheater Valve Control Forced Position | J460-02-2FCV-711_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2141 | J270-06-1PNL-001 | J460-02-2FCV-711 | Setting | J460-02-2FCV-711 - Room J6.14 - Reheater Valve Control Forced Calibration | J460-02-2FCV-711_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2142 | J270-06-1PNL-001 | J460-02-2FCV-711 | Measurement | J460-02-2FCV-711 - Room J6.14 - Reheater Valve Control Status | J460-02-2FCV-711_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2143 | J270-06-1PNL-001 | J460-02-2FCV-711 | Measurement | J460-02-2FCV-711 - Room J6.14 - Reheater Valve Control Actual SP | J460-02-2FCV-711_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2144 | J270-06-1PNL-001 | J460-02-2FCV-711 | Setting | J460-02-2FCV-711 - Room J6.14 - Reheater Valve Control SP | J460-02-2FCV-711_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2145 | J270-06-1PNL-001 | J460-02-2FCV-711 | Alarm | J460-02-2FCV-711 - Room J6.14 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-711_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2146 | J270-06-1PNL-001 | J460-02-2FCV-711 | Alarm | J460-02-2FCV-711 - Room J6.14 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-711_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2147 | J270-06-1PNL-001 | J460-02-2FCV-711 | Measurement | J460-02-2FCV-711 - Room J6.14 - Reheater Valve Control Error Code | J460-02-2FCV-711_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2594 | J270-06-1PNL-001 | J460-02-2FCV-711 | Measurement | J460-02-2FCV-711 - Room J6.14 - Reheater Valve Control Speed | J460-02-2FCV-711_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2139 | J270-06-1PNL-001 | J460-02-2FCV-712 | Alarm | J460-02-2FCV-712 - Room J6.14 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-712_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2140 | J270-06-1PNL-001 | J460-02-2FCV-712 | Measurement | J460-02-2FCV-712 - Room J6.14 - Reheater Valve Control Forced Position | J460-02-2FCV-712_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2141 | J270-06-1PNL-001 | J460-02-2FCV-712 | Setting | J460-02-2FCV-712 - Room J6.14 - Reheater Valve Control Forced Calibration | J460-02-2FCV-712_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2142 | J270-06-1PNL-001 | J460-02-2FCV-712 | Measurement | J460-02-2FCV-712 - Room J6.14 - Reheater Valve Control Status | J460-02-2FCV-712_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2143 | J270-06-1PNL-001 | J460-02-2FCV-712 | Measurement | J460-02-2FCV-712 - Room J6.14 - Reheater Valve Control Actual SP | J460-02-2FCV-712_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2144 | J270-06-1PNL-001 | J460-02-2FCV-712 | Setting | J460-02-2FCV-712 - Room J6.14 - Reheater Valve Control SP | J460-02-2FCV-712_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2145 | J270-06-1PNL-001 | J460-02-2FCV-712 | Alarm | J460-02-2FCV-712 - Room J6.14 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-712_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2146 | J270-06-1PNL-001 | J460-02-2FCV-712 | Alarm | J460-02-2FCV-712 - Room J6.14 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-712_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2147 | J270-06-1PNL-001 | J460-02-2FCV-712 | Measurement | J460-02-2FCV-712 - Room J6.14 - Reheater Valve Control Error Code | J460-02-2FCV-712_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2594 | J270-06-1PNL-001 | J460-02-2FCV-712 | Measurement | J460-02-2FCV-712 - Room J6.14 - Reheater Valve Control Speed | J460-02-2FCV-712_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1632 | J270-06-1PNL-001 | J460-02-1VAV-716 | Alarm | J460-02-1VAV-716 - Room J6.23 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-716_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1633 | J270-06-1PNL-001 | J460-02-1VAV-716 | Setting | J460-02-1VAV-716 - Room J6.23 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-716_Mode |  | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1634 | J270-06-1PNL-001 | J460-02-1VAV-716 | Setting | J460-02-1VAV-716 - Room J6.23 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-716_FlwSPShift |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1635 | J270-06-1PNL-001 | J460-02-1VAV-716 | Measurement | J460-02-1VAV-716 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-716_LocAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1636 | J270-06-1PNL-001 | J460-02-1VAV-716 | Alarm | J460-02-1VAV-716 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-716_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1637 | J270-06-1PNL-001 | J460-02-1VAV-716 | Measurement | J460-02-1VAV-716 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-716_SumAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1638 | J270-06-1PNL-001 | J460-02-1VAV-716 | Alarm | J460-02-1VAV-716 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-716_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 1639 | J270-06-1PNL-001 | J460-02-1VAV-716 | Measurement | J460-02-1VAV-608 - Room J6.23 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-608_RmEaFlwTot |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1640 | J270-06-1PNL-001 | J460-02-1VAV-716 | Measurement | J460-02-1VAV-716 - Room J6.23 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-716_RmSaFlw |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2220 | J270-06-1PNL-001 | J460-02-2FCV-714 | Alarm | J460-02-2FCV-714 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control - Communication Failure Alarm | J460-02-2FCV-714_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2221 | J270-06-1PNL-001 | J460-02-2FCV-714 | Measurement | J460-02-2FCV-714 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Position | J460-02-2FCV-714_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2222 | J270-06-1PNL-001 | J460-02-2FCV-714 | Setting | J460-02-2FCV-714 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Calibration | J460-02-2FCV-714_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2223 | J270-06-1PNL-001 | J460-02-2FCV-714 | Measurement | J460-02-2FCV-714 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Status | J460-02-2FCV-714_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2224 | J270-06-1PNL-001 | J460-02-2FCV-714 | Measurement | J460-02-2FCV-714 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Actual SP | J460-02-2FCV-714_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2225 | J270-06-1PNL-001 | J460-02-2FCV-714 | Setting | J460-02-2FCV-714 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control SP | J460-02-2FCV-714_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2226 | J270-06-1PNL-001 | J460-02-2FCV-714 | Alarm | J460-02-2FCV-714 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Open Alarm | J460-02-2FCV-714_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2227 | J270-06-1PNL-001 | J460-02-2FCV-714 | Alarm | J460-02-2FCV-714 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Close Alarm | J460-02-2FCV-714_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2228 | J270-06-1PNL-001 | J460-02-2FCV-714 | Measurement | J460-02-2FCV-714 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Error Code | J460-02-2FCV-714_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2599 | J270-06-1PNL-001 | J460-02-2FCV-714 | Measurement | J460-02-2FCV-714 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Speed | J460-02-2FCV-714_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2184 | J270-06-1PNL-001 | J460-02-2FCV-715 | Alarm | J460-02-2FCV-715 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control - Communication Failure Alarm | J460-02-2FCV-715_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2185 | J270-06-1PNL-001 | J460-02-2FCV-715 | Measurement | J460-02-2FCV-715 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Position | J460-02-2FCV-715_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2186 | J270-06-1PNL-001 | J460-02-2FCV-715 | Setting | J460-02-2FCV-715 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Calibration | J460-02-2FCV-715_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2187 | J270-06-1PNL-001 | J460-02-2FCV-715 | Measurement | J460-02-2FCV-715 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Status | J460-02-2FCV-715_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2188 | J270-06-1PNL-001 | J460-02-2FCV-715 | Measurement | J460-02-2FCV-715 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Actual SP | J460-02-2FCV-715_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2189 | J270-06-1PNL-001 | J460-02-2FCV-715 | Setting | J460-02-2FCV-715 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control SP | J460-02-2FCV-715_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2190 | J270-06-1PNL-001 | J460-02-2FCV-715 | Alarm | J460-02-2FCV-715 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Open Alarm | J460-02-2FCV-715_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2191 | J270-06-1PNL-001 | J460-02-2FCV-715 | Alarm | J460-02-2FCV-715 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Close Alarm | J460-02-2FCV-715_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2192 | J270-06-1PNL-001 | J460-02-2FCV-715 | Measurement | J460-02-2FCV-715 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Error Code | J460-02-2FCV-715_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2595 | J270-06-1PNL-001 | J460-02-2FCV-715 | Measurement | J460-02-2FCV-715 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Speed | J460-02-2FCV-715_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2220 | J270-06-1PNL-001 | J460-02-2FCV-716 | Alarm | J460-02-2FCV-716 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control - Communication Failure Alarm | J460-02-2FCV-716_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2221 | J270-06-1PNL-001 | J460-02-2FCV-716 | Measurement | J460-02-2FCV-716 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Position | J460-02-2FCV-716_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2222 | J270-06-1PNL-001 | J460-02-2FCV-716 | Setting | J460-02-2FCV-716 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Calibration | J460-02-2FCV-716_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2223 | J270-06-1PNL-001 | J460-02-2FCV-716 | Measurement | J460-02-2FCV-716 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Status | J460-02-2FCV-716_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2224 | J270-06-1PNL-001 | J460-02-2FCV-716 | Measurement | J460-02-2FCV-716 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Actual SP | J460-02-2FCV-716_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2225 | J270-06-1PNL-001 | J460-02-2FCV-716 | Setting | J460-02-2FCV-716 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control SP | J460-02-2FCV-716_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2226 | J270-06-1PNL-001 | J460-02-2FCV-716 | Alarm | J460-02-2FCV-716 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Open Alarm | J460-02-2FCV-716_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2227 | J270-06-1PNL-001 | J460-02-2FCV-716 | Alarm | J460-02-2FCV-716 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Close Alarm | J460-02-2FCV-716_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2228 | J270-06-1PNL-001 | J460-02-2FCV-716 | Measurement | J460-02-2FCV-716 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Error Code | J460-02-2FCV-716_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2599 | J270-06-1PNL-001 | J460-02-2FCV-716 | Measurement | J460-02-2FCV-716 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Speed | J460-02-2FCV-716_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2184 | J270-06-1PNL-001 | J460-02-2FCV-717 | Alarm | J460-02-2FCV-717 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control - Communication Failure Alarm | J460-02-2FCV-717_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2185 | J270-06-1PNL-001 | J460-02-2FCV-717 | Measurement | J460-02-2FCV-717 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Position | J460-02-2FCV-717_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2186 | J270-06-1PNL-001 | J460-02-2FCV-717 | Setting | J460-02-2FCV-717 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Forced Calibration | J460-02-2FCV-717_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2187 | J270-06-1PNL-001 | J460-02-2FCV-717 | Measurement | J460-02-2FCV-717 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Status | J460-02-2FCV-717_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2188 | J270-06-1PNL-001 | J460-02-2FCV-717 | Measurement | J460-02-2FCV-717 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Actual SP | J460-02-2FCV-717_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2189 | J270-06-1PNL-001 | J460-02-2FCV-717 | Setting | J460-02-2FCV-717 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control SP | J460-02-2FCV-717_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2190 | J270-06-1PNL-001 | J460-02-2FCV-717 | Alarm | J460-02-2FCV-717 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Open Alarm | J460-02-2FCV-717_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2191 | J270-06-1PNL-001 | J460-02-2FCV-717 | Alarm | J460-02-2FCV-717 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Fail to Close Alarm | J460-02-2FCV-717_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2192 | J270-06-1PNL-001 | J460-02-2FCV-717 | Measurement | J460-02-2FCV-717 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Error Code | J460-02-2FCV-717_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2595 | J270-06-1PNL-001 | J460-02-2FCV-717 | Measurement | J460-02-2FCV-717 - Room J0.07 - J460-01-1ACU-001 Heating Valve Control Speed | J460-02-2FCV-717_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1632 | J270-06-1PNL-001 | J460-02-1VAV-723 | Alarm | J460-02-1VAV-723 - Room J6.23 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-723_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1633 | J270-06-1PNL-001 | J460-02-1VAV-723 | Setting | J460-02-1VAV-723 - Room J6.23 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-723_Mode |  | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1634 | J270-06-1PNL-001 | J460-02-1VAV-723 | Setting | J460-02-1VAV-723 - Room J6.23 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-723_FlwSPShift |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1635 | J270-06-1PNL-001 | J460-02-1VAV-723 | Measurement | J460-02-1VAV-723 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-723_LocAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1636 | J270-06-1PNL-001 | J460-02-1VAV-723 | Alarm | J460-02-1VAV-723 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-723_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1637 | J270-06-1PNL-001 | J460-02-1VAV-723 | Measurement | J460-02-1VAV-723 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-723_SumAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1638 | J270-06-1PNL-001 | J460-02-1VAV-723 | Alarm | J460-02-1VAV-723 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-723_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 1639 | J270-06-1PNL-001 | J460-02-1VAV-723 | Measurement | J460-02-1VAV-608 - Room J6.23 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-608_RmEaFlwTot |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1640 | J270-06-1PNL-001 | J460-02-1VAV-723 | Measurement | J460-02-1VAV-723 - Room J6.23 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-723_RmSaFlw |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2139 | J270-06-1PNL-001 | J460-02-2FCV-718 | Alarm | J460-02-2FCV-718 - Room J6.14 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-718_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2140 | J270-06-1PNL-001 | J460-02-2FCV-718 | Measurement | J460-02-2FCV-718 - Room J6.14 - Reheater Valve Control Forced Position | J460-02-2FCV-718_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2141 | J270-06-1PNL-001 | J460-02-2FCV-718 | Setting | J460-02-2FCV-718 - Room J6.14 - Reheater Valve Control Forced Calibration | J460-02-2FCV-718_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2142 | J270-06-1PNL-001 | J460-02-2FCV-718 | Measurement | J460-02-2FCV-718 - Room J6.14 - Reheater Valve Control Status | J460-02-2FCV-718_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2143 | J270-06-1PNL-001 | J460-02-2FCV-718 | Measurement | J460-02-2FCV-718 - Room J6.14 - Reheater Valve Control Actual SP | J460-02-2FCV-718_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2144 | J270-06-1PNL-001 | J460-02-2FCV-718 | Setting | J460-02-2FCV-718 - Room J6.14 - Reheater Valve Control SP | J460-02-2FCV-718_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2145 | J270-06-1PNL-001 | J460-02-2FCV-718 | Alarm | J460-02-2FCV-718 - Room J6.14 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-718_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2146 | J270-06-1PNL-001 | J460-02-2FCV-718 | Alarm | J460-02-2FCV-718 - Room J6.14 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-718_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2147 | J270-06-1PNL-001 | J460-02-2FCV-718 | Measurement | J460-02-2FCV-718 - Room J6.14 - Reheater Valve Control Error Code | J460-02-2FCV-718_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2594 | J270-06-1PNL-001 | J460-02-2FCV-718 | Measurement | J460-02-2FCV-718 - Room J6.14 - Reheater Valve Control Speed | J460-02-2FCV-718_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1598 | J270-06-1PNL-001 | J460-02-1VAV-724 | Alarm | J460-02-2XU-606 - Room J6.22 - Fume hood - Communication Failure Alarm | J460-02-2XU-606_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1599 | J270-06-1PNL-001 | J460-02-1VAV-724 | Measurement | J460-02-2XU-606 - Room J6.22 - Fume hood Actual Volume Flow | J460-02-2XU-606_ActFlow |  | 0 | 800 | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.1 | 1600 | J270-06-1PNL-001 | J460-02-1VAV-724 | Measurement | J460-02-2XU-606 - Room J6.22 - Fume hood SP Volume Flow Display | J460-02-2XU-606_FlowSP |  | 800 | - | [11 empty] | - | - | - | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1601 | J270-06-1PNL-001 | J460-02-1VAV-724 | Measurement | J460-02-2XU-606 - Room J6.22 - Fume hood Actual Actuator Position | J460-02-2XU-606_RelPos |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1602 | J270-06-1PNL-001 | J460-02-1VAV-724 | Measurement | J460-02-2XU-606 - Room J6.22 - Fume hood Fault | J460-02-2XU-606_LocAlm |  | NOFAULT | FAULT | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1603 | J270-06-1PNL-001 | J460-02-1VAV-724 | Alarm | J460-02-2XU-606 - Room J6.22 - Fume hood Fault Alarm | J460-02-2XU-606_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1604 | J270-06-1PNL-001 | J460-02-1VAV-724 | Measurement | J460-02-2XU-606 - Room J6.22 - Fume hood Operating Mode Feedback | J460-02-2XU-606_Mode |  | - | OFF | NORMAL | REDUCED | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2139 | J270-06-1PNL-001 | J460-02-2FCV-719 | Alarm | J460-02-2FCV-719 - Room J6.14 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-719_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2140 | J270-06-1PNL-001 | J460-02-2FCV-719 | Measurement | J460-02-2FCV-719 - Room J6.14 - Reheater Valve Control Forced Position | J460-02-2FCV-719_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2141 | J270-06-1PNL-001 | J460-02-2FCV-719 | Setting | J460-02-2FCV-719 - Room J6.14 - Reheater Valve Control Forced Calibration | J460-02-2FCV-719_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2142 | J270-06-1PNL-001 | J460-02-2FCV-719 | Measurement | J460-02-2FCV-719 - Room J6.14 - Reheater Valve Control Status | J460-02-2FCV-719_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2143 | J270-06-1PNL-001 | J460-02-2FCV-719 | Measurement | J460-02-2FCV-719 - Room J6.14 - Reheater Valve Control Actual SP | J460-02-2FCV-719_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2144 | J270-06-1PNL-001 | J460-02-2FCV-719 | Setting | J460-02-2FCV-719 - Room J6.14 - Reheater Valve Control SP | J460-02-2FCV-719_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2145 | J270-06-1PNL-001 | J460-02-2FCV-719 | Alarm | J460-02-2FCV-719 - Room J6.14 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-719_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2146 | J270-06-1PNL-001 | J460-02-2FCV-719 | Alarm | J460-02-2FCV-719 - Room J6.14 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-719_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2147 | J270-06-1PNL-001 | J460-02-2FCV-719 | Measurement | J460-02-2FCV-719 - Room J6.14 - Reheater Valve Control Error Code | J460-02-2FCV-719_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2594 | J270-06-1PNL-001 | J460-02-2FCV-719 | Measurement | J460-02-2FCV-719 - Room J6.14 - Reheater Valve Control Speed | J460-02-2FCV-719_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2220 | J270-06-1PNL-001 | J460-02-2FCV-720 | Alarm | J460-02-2FCV-720 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control - Communication Failure Alarm | J460-02-2FCV-720_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2221 | J270-06-1PNL-001 | J460-02-2FCV-720 | Measurement | J460-02-2FCV-720 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Position | J460-02-2FCV-720_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2222 | J270-06-1PNL-001 | J460-02-2FCV-720 | Setting | J460-02-2FCV-720 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Calibration | J460-02-2FCV-720_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2223 | J270-06-1PNL-001 | J460-02-2FCV-720 | Measurement | J460-02-2FCV-720 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Status | J460-02-2FCV-720_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2224 | J270-06-1PNL-001 | J460-02-2FCV-720 | Measurement | J460-02-2FCV-720 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Actual SP | J460-02-2FCV-720_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2225 | J270-06-1PNL-001 | J460-02-2FCV-720 | Setting | J460-02-2FCV-720 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control SP | J460-02-2FCV-720_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2226 | J270-06-1PNL-001 | J460-02-2FCV-720 | Alarm | J460-02-2FCV-720 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Open Alarm | J460-02-2FCV-720_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2227 | J270-06-1PNL-001 | J460-02-2FCV-720 | Alarm | J460-02-2FCV-720 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Close Alarm | J460-02-2FCV-720_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2228 | J270-06-1PNL-001 | J460-02-2FCV-720 | Measurement | J460-02-2FCV-720 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Error Code | J460-02-2FCV-720_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2599 | J270-06-1PNL-001 | J460-02-2FCV-720 | Measurement | J460-02-2FCV-720 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Speed | J460-02-2FCV-720_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1632 | J270-06-1PNL-001 | J460-02-1VAV-729 | Alarm | J460-02-1VAV-729 - Room J6.23 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-729_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1633 | J270-06-1PNL-001 | J460-02-1VAV-729 | Setting | J460-02-1VAV-729 - Room J6.23 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-729_Mode |  | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1634 | J270-06-1PNL-001 | J460-02-1VAV-729 | Setting | J460-02-1VAV-729 - Room J6.23 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-729_FlwSPShift |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1635 | J270-06-1PNL-001 | J460-02-1VAV-729 | Measurement | J460-02-1VAV-729 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-729_LocAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1636 | J270-06-1PNL-001 | J460-02-1VAV-729 | Alarm | J460-02-1VAV-729 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-729_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1637 | J270-06-1PNL-001 | J460-02-1VAV-729 | Measurement | J460-02-1VAV-729 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-729_SumAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1638 | J270-06-1PNL-001 | J460-02-1VAV-729 | Alarm | J460-02-1VAV-729 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-729_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 1639 | J270-06-1PNL-001 | J460-02-1VAV-729 | Measurement | J460-02-1VAV-608 - Room J6.23 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-608_RmEaFlwTot |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1640 | J270-06-1PNL-001 | J460-02-1VAV-729 | Measurement | J460-02-1VAV-729 - Room J6.23 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-729_RmSaFlw |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2139 | J270-06-1PNL-001 | J460-02-2FCV-721 | Alarm | J460-02-2FCV-721 - Room J6.14 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-721_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2140 | J270-06-1PNL-001 | J460-02-2FCV-721 | Measurement | J460-02-2FCV-721 - Room J6.14 - Reheater Valve Control Forced Position | J460-02-2FCV-721_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2141 | J270-06-1PNL-001 | J460-02-2FCV-721 | Setting | J460-02-2FCV-721 - Room J6.14 - Reheater Valve Control Forced Calibration | J460-02-2FCV-721_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2142 | J270-06-1PNL-001 | J460-02-2FCV-721 | Measurement | J460-02-2FCV-721 - Room J6.14 - Reheater Valve Control Status | J460-02-2FCV-721_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2143 | J270-06-1PNL-001 | J460-02-2FCV-721 | Measurement | J460-02-2FCV-721 - Room J6.14 - Reheater Valve Control Actual SP | J460-02-2FCV-721_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2144 | J270-06-1PNL-001 | J460-02-2FCV-721 | Setting | J460-02-2FCV-721 - Room J6.14 - Reheater Valve Control SP | J460-02-2FCV-721_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2145 | J270-06-1PNL-001 | J460-02-2FCV-721 | Alarm | J460-02-2FCV-721 - Room J6.14 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-721_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2146 | J270-06-1PNL-001 | J460-02-2FCV-721 | Alarm | J460-02-2FCV-721 - Room J6.14 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-721_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2147 | J270-06-1PNL-001 | J460-02-2FCV-721 | Measurement | J460-02-2FCV-721 - Room J6.14 - Reheater Valve Control Error Code | J460-02-2FCV-721_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2594 | J270-06-1PNL-001 | J460-02-2FCV-721 | Measurement | J460-02-2FCV-721 - Room J6.14 - Reheater Valve Control Speed | J460-02-2FCV-721_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2220 | J270-06-1PNL-001 | J460-02-2FCV-722 | Alarm | J460-02-2FCV-722 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control - Communication Failure Alarm | J460-02-2FCV-722_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2221 | J270-06-1PNL-001 | J460-02-2FCV-722 | Measurement | J460-02-2FCV-722 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Position | J460-02-2FCV-722_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2222 | J270-06-1PNL-001 | J460-02-2FCV-722 | Setting | J460-02-2FCV-722 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Forced Calibration | J460-02-2FCV-722_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2223 | J270-06-1PNL-001 | J460-02-2FCV-722 | Measurement | J460-02-2FCV-722 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Status | J460-02-2FCV-722_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2224 | J270-06-1PNL-001 | J460-02-2FCV-722 | Measurement | J460-02-2FCV-722 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Actual SP | J460-02-2FCV-722_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2225 | J270-06-1PNL-001 | J460-02-2FCV-722 | Setting | J460-02-2FCV-722 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control SP | J460-02-2FCV-722_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2226 | J270-06-1PNL-001 | J460-02-2FCV-722 | Alarm | J460-02-2FCV-722 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Open Alarm | J460-02-2FCV-722_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2227 | J270-06-1PNL-001 | J460-02-2FCV-722 | Alarm | J460-02-2FCV-722 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Fail to Close Alarm | J460-02-2FCV-722_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2228 | J270-06-1PNL-001 | J460-02-2FCV-722 | Measurement | J460-02-2FCV-722 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Error Code | J460-02-2FCV-722_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2599 | J270-06-1PNL-001 | J460-02-2FCV-722 | Measurement | J460-02-2FCV-722 - Room J0.07 - J460-01-1ACU-001 Cooling Valve Control Speed | J460-02-2FCV-722_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1632 | J270-06-1PNL-001 | J460-02-1VAV-730 | Alarm | J460-02-1VAV-730 - Room J6.23 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-730_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1633 | J270-06-1PNL-001 | J460-02-1VAV-730 | Setting | J460-02-1VAV-730 - Room J6.23 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-730_Mode |  | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1634 | J270-06-1PNL-001 | J460-02-1VAV-730 | Setting | J460-02-1VAV-730 - Room J6.23 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-730_FlwSPShift |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1635 | J270-06-1PNL-001 | J460-02-1VAV-730 | Measurement | J460-02-1VAV-730 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-730_LocAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1636 | J270-06-1PNL-001 | J460-02-1VAV-730 | Alarm | J460-02-1VAV-730 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-730_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1637 | J270-06-1PNL-001 | J460-02-1VAV-730 | Measurement | J460-02-1VAV-730 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-730_SumAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1638 | J270-06-1PNL-001 | J460-02-1VAV-730 | Alarm | J460-02-1VAV-730 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-730_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 1639 | J270-06-1PNL-001 | J460-02-1VAV-730 | Measurement | J460-02-1VAV-608 - Room J6.23 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-608_RmEaFlwTot |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1640 | J270-06-1PNL-001 | J460-02-1VAV-730 | Measurement | J460-02-1VAV-730 - Room J6.23 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-730_RmSaFlw |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2139 | J270-06-1PNL-001 | J460-02-2FCV-723 | Alarm | J460-02-2FCV-723 - Room J6.14 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-723_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2140 | J270-06-1PNL-001 | J460-02-2FCV-723 | Measurement | J460-02-2FCV-723 - Room J6.14 - Reheater Valve Control Forced Position | J460-02-2FCV-723_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2141 | J270-06-1PNL-001 | J460-02-2FCV-723 | Setting | J460-02-2FCV-723 - Room J6.14 - Reheater Valve Control Forced Calibration | J460-02-2FCV-723_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2142 | J270-06-1PNL-001 | J460-02-2FCV-723 | Measurement | J460-02-2FCV-723 - Room J6.14 - Reheater Valve Control Status | J460-02-2FCV-723_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2143 | J270-06-1PNL-001 | J460-02-2FCV-723 | Measurement | J460-02-2FCV-723 - Room J6.14 - Reheater Valve Control Actual SP | J460-02-2FCV-723_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2144 | J270-06-1PNL-001 | J460-02-2FCV-723 | Setting | J460-02-2FCV-723 - Room J6.14 - Reheater Valve Control SP | J460-02-2FCV-723_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2145 | J270-06-1PNL-001 | J460-02-2FCV-723 | Alarm | J460-02-2FCV-723 - Room J6.14 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-723_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2146 | J270-06-1PNL-001 | J460-02-2FCV-723 | Alarm | J460-02-2FCV-723 - Room J6.14 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-723_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2147 | J270-06-1PNL-001 | J460-02-2FCV-723 | Measurement | J460-02-2FCV-723 - Room J6.14 - Reheater Valve Control Error Code | J460-02-2FCV-723_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2594 | J270-06-1PNL-001 | J460-02-2FCV-723 | Measurement | J460-02-2FCV-723 - Room J6.14 - Reheater Valve Control Speed | J460-02-2FCV-723_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1632 | J270-06-1PNL-001 | J460-02-1VAV-735 | Alarm | J460-02-1VAV-735 - Room J6.23 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-735_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1633 | J270-06-1PNL-001 | J460-02-1VAV-735 | Setting | J460-02-1VAV-735 - Room J6.23 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-735_Mode |  | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1634 | J270-06-1PNL-001 | J460-02-1VAV-735 | Setting | J460-02-1VAV-735 - Room J6.23 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-735_FlwSPShift |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1635 | J270-06-1PNL-001 | J460-02-1VAV-735 | Measurement | J460-02-1VAV-735 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-735_LocAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1636 | J270-06-1PNL-001 | J460-02-1VAV-735 | Alarm | J460-02-1VAV-735 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-735_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1637 | J270-06-1PNL-001 | J460-02-1VAV-735 | Measurement | J460-02-1VAV-735 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-735_SumAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1638 | J270-06-1PNL-001 | J460-02-1VAV-735 | Alarm | J460-02-1VAV-735 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-735_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 1639 | J270-06-1PNL-001 | J460-02-1VAV-735 | Measurement | J460-02-1VAV-608 - Room J6.23 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-608_RmEaFlwTot |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1640 | J270-06-1PNL-001 | J460-02-1VAV-735 | Measurement | J460-02-1VAV-735 - Room J6.23 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-735_RmSaFlw |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2139 | J270-06-1PNL-001 | J460-02-2FCV-724 | Alarm | J460-02-2FCV-724 - Room J6.14 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-724_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2140 | J270-06-1PNL-001 | J460-02-2FCV-724 | Measurement | J460-02-2FCV-724 - Room J6.14 - Reheater Valve Control Forced Position | J460-02-2FCV-724_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2141 | J270-06-1PNL-001 | J460-02-2FCV-724 | Setting | J460-02-2FCV-724 - Room J6.14 - Reheater Valve Control Forced Calibration | J460-02-2FCV-724_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2142 | J270-06-1PNL-001 | J460-02-2FCV-724 | Measurement | J460-02-2FCV-724 - Room J6.14 - Reheater Valve Control Status | J460-02-2FCV-724_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2143 | J270-06-1PNL-001 | J460-02-2FCV-724 | Measurement | J460-02-2FCV-724 - Room J6.14 - Reheater Valve Control Actual SP | J460-02-2FCV-724_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2144 | J270-06-1PNL-001 | J460-02-2FCV-724 | Setting | J460-02-2FCV-724 - Room J6.14 - Reheater Valve Control SP | J460-02-2FCV-724_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2145 | J270-06-1PNL-001 | J460-02-2FCV-724 | Alarm | J460-02-2FCV-724 - Room J6.14 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-724_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2146 | J270-06-1PNL-001 | J460-02-2FCV-724 | Alarm | J460-02-2FCV-724 - Room J6.14 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-724_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2147 | J270-06-1PNL-001 | J460-02-2FCV-724 | Measurement | J460-02-2FCV-724 - Room J6.14 - Reheater Valve Control Error Code | J460-02-2FCV-724_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2594 | J270-06-1PNL-001 | J460-02-2FCV-724 | Measurement | J460-02-2FCV-724 - Room J6.14 - Reheater Valve Control Speed | J460-02-2FCV-724_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1632 | J270-06-1PNL-001 | J460-02-1VAV-738 | Alarm | J460-02-1VAV-738 - Room J6.23 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-738_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1633 | J270-06-1PNL-001 | J460-02-1VAV-738 | Setting | J460-02-1VAV-738 - Room J6.23 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-738_Mode |  | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1634 | J270-06-1PNL-001 | J460-02-1VAV-738 | Setting | J460-02-1VAV-738 - Room J6.23 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-738_FlwSPShift |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1635 | J270-06-1PNL-001 | J460-02-1VAV-738 | Measurement | J460-02-1VAV-738 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-738_LocAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1636 | J270-06-1PNL-001 | J460-02-1VAV-738 | Alarm | J460-02-1VAV-738 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-738_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1637 | J270-06-1PNL-001 | J460-02-1VAV-738 | Measurement | J460-02-1VAV-738 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-738_SumAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1638 | J270-06-1PNL-001 | J460-02-1VAV-738 | Alarm | J460-02-1VAV-738 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-738_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 1639 | J270-06-1PNL-001 | J460-02-1VAV-738 | Measurement | J460-02-1VAV-608 - Room J6.23 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-608_RmEaFlwTot |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1640 | J270-06-1PNL-001 | J460-02-1VAV-738 | Measurement | J460-02-1VAV-738 - Room J6.23 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-738_RmSaFlw |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2139 | J270-06-1PNL-001 | J460-02-2FCV-725 | Alarm | J460-02-2FCV-725 - Room J6.14 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-725_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2140 | J270-06-1PNL-001 | J460-02-2FCV-725 | Measurement | J460-02-2FCV-725 - Room J6.14 - Reheater Valve Control Forced Position | J460-02-2FCV-725_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2141 | J270-06-1PNL-001 | J460-02-2FCV-725 | Setting | J460-02-2FCV-725 - Room J6.14 - Reheater Valve Control Forced Calibration | J460-02-2FCV-725_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2142 | J270-06-1PNL-001 | J460-02-2FCV-725 | Measurement | J460-02-2FCV-725 - Room J6.14 - Reheater Valve Control Status | J460-02-2FCV-725_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2143 | J270-06-1PNL-001 | J460-02-2FCV-725 | Measurement | J460-02-2FCV-725 - Room J6.14 - Reheater Valve Control Actual SP | J460-02-2FCV-725_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2144 | J270-06-1PNL-001 | J460-02-2FCV-725 | Setting | J460-02-2FCV-725 - Room J6.14 - Reheater Valve Control SP | J460-02-2FCV-725_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2145 | J270-06-1PNL-001 | J460-02-2FCV-725 | Alarm | J460-02-2FCV-725 - Room J6.14 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-725_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2146 | J270-06-1PNL-001 | J460-02-2FCV-725 | Alarm | J460-02-2FCV-725 - Room J6.14 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-725_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2147 | J270-06-1PNL-001 | J460-02-2FCV-725 | Measurement | J460-02-2FCV-725 - Room J6.14 - Reheater Valve Control Error Code | J460-02-2FCV-725_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2594 | J270-06-1PNL-001 | J460-02-2FCV-725 | Measurement | J460-02-2FCV-725 - Room J6.14 - Reheater Valve Control Speed | J460-02-2FCV-725_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1632 | J270-06-1PNL-001 | J460-02-1VAV-741 | Alarm | J460-02-1VAV-741 - Room J6.23 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-741_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1633 | J270-06-1PNL-001 | J460-02-1VAV-741 | Setting | J460-02-1VAV-741 - Room J6.23 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-741_Mode |  | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1634 | J270-06-1PNL-001 | J460-02-1VAV-741 | Setting | J460-02-1VAV-741 - Room J6.23 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-741_FlwSPShift |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1635 | J270-06-1PNL-001 | J460-02-1VAV-741 | Measurement | J460-02-1VAV-741 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-741_LocAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1636 | J270-06-1PNL-001 | J460-02-1VAV-741 | Alarm | J460-02-1VAV-741 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-741_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1637 | J270-06-1PNL-001 | J460-02-1VAV-741 | Measurement | J460-02-1VAV-741 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-741_SumAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1638 | J270-06-1PNL-001 | J460-02-1VAV-741 | Alarm | J460-02-1VAV-741 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-741_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 1639 | J270-06-1PNL-001 | J460-02-1VAV-741 | Measurement | J460-02-1VAV-608 - Room J6.23 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-608_RmEaFlwTot |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1640 | J270-06-1PNL-001 | J460-02-1VAV-741 | Measurement | J460-02-1VAV-741 - Room J6.23 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-741_RmSaFlw |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2139 | J270-06-1PNL-001 | J460-02-2FCV-726 | Alarm | J460-02-2FCV-726 - Room J6.14 - Reheater Valve Control - Communication Failure Alarm | J460-02-2FCV-726_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
1.0 | 2140 | J270-06-1PNL-001 | J460-02-2FCV-726 | Measurement | J460-02-2FCV-726 - Room J6.14 - Reheater Valve Control Forced Position | J460-02-2FCV-726_ForcePos |  | NO | YES | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2141 | J270-06-1PNL-001 | J460-02-2FCV-726 | Setting | J460-02-2FCV-726 - Room J6.14 - Reheater Valve Control Forced Calibration | J460-02-2FCV-726_ForceCal |  | OFF | ON | [11 empty] | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2142 | J270-06-1PNL-001 | J460-02-2FCV-726 | Measurement | J460-02-2FCV-726 - Room J6.14 - Reheater Valve Control Status | J460-02-2FCV-726_MotState |  | - | STOP | RETRACT | EXTEND | CALIB | MANOVRD | CLOGGING | ERROR | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1.0 | 2143 | J270-06-1PNL-001 | J460-02-2FCV-726 | Measurement | J460-02-2FCV-726 - Room J6.14 - Reheater Valve Control Actual SP | J460-02-2FCV-726_ActSP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2144 | J270-06-1PNL-001 | J460-02-2FCV-726 | Setting | J460-02-2FCV-726 - Room J6.14 - Reheater Valve Control SP | J460-02-2FCV-726_SP |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2145 | J270-06-1PNL-001 | J460-02-2FCV-726 | Alarm | J460-02-2FCV-726 - Room J6.14 - Reheater Valve Control Fail to Open Alarm | J460-02-2FCV-726_FTOAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2146 | J270-06-1PNL-001 | J460-02-2FCV-726 | Alarm | J460-02-2FCV-726 - Room J6.14 - Reheater Valve Control Fail to Close Alarm | J460-02-2FCV-726_FTCAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | M | - | bar: State 2 to State 64
1.0 | 2147 | J270-06-1PNL-001 | J460-02-2FCV-726 | Measurement | J460-02-2FCV-726 - Room J6.14 - Reheater Valve Control Error Code | J460-02-2FCV-726_Err |  | 0 | 127 | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
1.0 | 2594 | J270-06-1PNL-001 | J460-02-2FCV-726 | Measurement | J460-02-2FCV-726 - Room J6.14 - Reheater Valve Control Speed | J460-02-2FCV-726_Spd |  | - | 4 s/mm | 100 s/inch | 6 s/mm | 150 s/inch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1632 | J270-06-1PNL-001 | J460-02-1VAV-743 | Alarm | J460-02-1VAV-743 - Room J6.23 - Supply Air Flow Control - Communication Failure Alarm | J460-02-1VAV-743_CommFailAlm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1633 | J270-06-1PNL-001 | J460-02-1VAV-743 | Setting | J460-02-1VAV-743 - Room J6.23 - Supply Air Flow Control Operating Mode Entire Room | J460-02-1VAV-743_Mode |  | - | NOTPRSNT | DAYMODE | NGTMODE | EMGMODE | SHUTOFF | OPEN | - | - | - | - | - | - | - | - | - | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2.0 | 1634 | J270-06-1PNL-001 | J460-02-1VAV-743 | Setting | J460-02-1VAV-743 - Room J6.23 - Supply Air Flow Control Volume Flow SP Shift | J460-02-1VAV-743_FlwSPShift |  | 0 | 100 | [11 empty] | - | - | - | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1635 | J270-06-1PNL-001 | J460-02-1VAV-743 | Measurement | J460-02-1VAV-743 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-743_LocAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1636 | J270-06-1PNL-001 | J460-02-1VAV-743 | Alarm | J460-02-1VAV-743 - Room J6.23 - Supply Air Flow Control Local Alarm | J460-02-1VAV-743_LocAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 2 | Y | - | bar: State 2 to State 64
2.0 | 1637 | J270-06-1PNL-001 | J460-02-1VAV-743 | Measurement | J460-02-1VAV-743 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-743_SumAlm |  | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1638 | J270-06-1PNL-001 | J460-02-1VAV-743 | Alarm | J460-02-1VAV-743 - Room J6.23 - Supply Air Flow Control Summary Alarm | J460-02-1VAV-743_SumAlm_Alm | - | NORMAL | ALARM | [11 empty] | - | - | - | - | - | - | 100 | - | - | HMI/Station |  | 1 | Y | - | bar: State 2 to State 64
2.0 | 1639 | J270-06-1PNL-001 | J460-02-1VAV-743 | Measurement | J460-02-1VAV-608 - Room J6.23 - Return Air Flow Control Extract Air Volume | J460-02-1VAV-608_RmEaFlwTot |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64
2.0 | 1640 | J270-06-1PNL-001 | J460-02-1VAV-743 | Measurement | J460-02-1VAV-743 - Room J6.23 - Supply Air Flow Control Supply Air Volume | J460-02-1VAV-743_RmSaFlw |  | - | - | [11 empty] | - | - | - | - | - | - | 200 | - | l/s | HMI/Station | - | 4 | - | - | bar: State 2 to State 64